## Sheet 1
Site | Month | Equipment.Name | Type | Capacity.loss.(kWp) | From.Date | From.Time | To.Date | To.Time | Duration | Reason | Loss.of.POA | PR.of.the.day.(%) | Generation_loss | Action.Taken
Bhadla | April | Inverter 11 | Island protection fault | 3379.2 | 44652 | 0.35556 | 44652 | 0.37292 | 0.41667 | Inverter Tripped in Island Protection Fault | 0.18302 | 0.72294 | 447.1166 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Island protection fault | 3379.2 | 44652 | 0.37847 | 44652 | 0.39444 | 0.38333 | Again Inverter Tripped in Island Protection Fault | 0.22284 | 0.72294 | 544.3864 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Island protection fault | 844.8 | 44652 | 0.39514 | 44652 | 0.55625 | 3.8667 | Unit-1 Tripped in Island Protection Fault | 3.5759 | 0.72294 | 2183.9506 | Discussed with SG Team As per Instructions of SG Team to interchange Master and Slave between Unit-1 & Unit-2. and Unit-1 Q1 Kept Off.
Bhadla | April | Inverter 11 | Island protection fault | 3379.2 | 44652 | 0.55694 | 44652 | 0.57569 | 0.45 | Inverter Tripped in Island protection fault & Temp Control Cabinet Fault | 0.48036 | 0.72294 | 1173.4864 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Island protection fault | 844.8 | 44652 | 0.57569 | 44652 | 0.62639 | 1.2167 | Unit-01 Tripped in Island protection fault & Temp Control Cabinet Fault | 1.1347 | 0.72294 | 693.0319 | Fault Resume
Bhadla | April | Inverter 11 | Island protection fault | 3379.2 | 44652 | 0.62708 | 44652 | 0.67639 | 1.1833 | Again Inverter Tripped in AC SPD Fault & Island Protection fault. | 0.8924 | 0.72294 | 2180.0766 | Discussed with SG Team As per Instructions of SG Team to interchange Master and Slave between Unit-1 & Unit-2. and Unit-1 Q1 Kept Off. After then Unit-02 to Unit-3 change to Master and Slave then start the Inv.
Bhadla | April | Inverter 11 | Island protection fault | 844.8 | 44652 | 0.67639 | 44652 | 0.79167 | 2.7667 | Unit-01 Tripped in AC SPD Fault & Island Protection fault. | 0.73587 | 0.72294 | 449.419 | After Generation hours SG team Replaced AC MCCB in Unit-01
Bhadla | April | Inverter 11 | Island protection fault | 857.6 | 44652 | 0.67639 | 44652 | 0.79167 | 2.7667 | Unit-02 Tripped in AC SPD Fault & Island Protection fault. | 0.73587 | 0.72294 | 456.2284 | After Generation hours SG team Replaced AC MCCB in Unit-02
Bhadla | April | Inverter 19 | Contactor fault | 3520 | 44653 | 0.27222 | 44653 | 0.35208 | 1.9167 | Inverter Tripped in Contactor Fault | 0.27119 | 0.71734 | 684.7652 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 19 | Contactor fault | 883.2 | 44653 | 0.35208 | 44653 | 0.79097 | 10.5333 | Unit-01 Tripped in Contactor Fault | 7.6003 | 0.71734 | 4815.2 | Discussed with SG Team As per Instructions of SG Team to interchange Master and Slave between Unit-1 & Unit-2. and Unit-1 Q1 Kept Off.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44654 | 0.55347 | 44654 | 0.57708 | 0.56667 | Inverter Tripped in L Over Temp fault | 0.5896 | 0.72632 | 1485.9338 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 19 | Contactor fault | 843.2 | 44655 | 0.27153 | 44655 | 0.33333 | 1.4833 | Unit-03 Tripped in Contactor Fault | 0.10348 | 0.73158 | 138 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44657 | 0.55 | 44657 | 0.57222 | 0.53333 | Inverter Tripped in L-Over Temp. | 0.54917 | 0.73173 | 1394.3722 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 15 | Contactor fault | 3475.2 | 44657 | 0.27014 | 44657 | 0.29375 | 0.56667 | Inverter Tripped in Contactor Fault | 0.012483 | 0.73173 | 31.7428 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | SCB.19.08 | String fault | 192 | 44657 | 0.49653 | 44657 | 0.50556 | 0.21667 | DC Breaker Tripped | 0.2218 | 0.73173 | 31.1608 | DC Floating Checked floating found ok then start the Inv.
Bhadla | April | Inverter 28 | Island protection fault | 844.8 | 44657 | 0.54097 | 44657 | 0.55833 | 0.41667 | Unit-2 Tripped in Island Protection Fault | 0.31163 | 0.73173 | 535 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 28 | Island protection fault | 844.8 | 44657 | 0.57569 | 44657 | 0.59028 | 0.35 | Again Unit-2 Tripped in Island Protection Fault | 0.23341 | 0.73173 | 367 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 28 | Island protection fault | 844.8 | 44657 | 0.625 | 44657 | 0.79236 | 4.0167 | Again Unit-2 Tripped in Island Protection Fault | 1.6884 | 0.73173 | 1043.7357 | After Generation Hour SG Team replaced New AC Breaker in Unit-02.
Bhadla | April | SCB.01.07 | String fault | 166.4 | 44658 | 0.54097 | 44658 | 0.54653 | 0.13333 | DC Breaker Tripped | 0.13966 | 0.73091 | 16.9864 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44658 | 0.56667 | 44658 | 0.58958 | 0.55 | Inverter Tripped in L-Over Temp. | 0.55552 | 0.73091 | 1408.9188 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | SCB.15.08 | String fault | 166.4 | 44658 | 0.49722 | 44658 | 0.50417 | 0.16667 | DC Breaker Tripped | 0.17019 | 0.73091 | 20.6995 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | April | Inverter 15 | Contactor fault | 3475.2 | 44658 | 0.26875 | 44658 | 0.30417 | 0.85 | Inverter Tripped in Contactor Fault | 0.028003 | 0.73091 | 71.1288 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Contactor fault | 857.6 | 44659 | 0.26875 | 44659 | 0.3125 | 1.05 | Unit-02 Tripped in Contactor Fault | 0.054338 | 0.73675 | 34.3328 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 08 | Contactor fault | 870.4 | 44659 | 0.3 | 44660 | 0.79306 | 24.4 | Unit-04 Tripped in Contactor Fault | 0.20943 | 0.73675 | 9610 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | SCB.15.02 | String fault | 166.4 | 44659 | 0.49514 | 44659 | 0.51042 | 0.36667 | DC Breaker Tripped | 0.35685 | 0.73675 | 43.7474 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | April | Inverter 15 | Contactor fault | 3475.2 | 44659 | 0.51875 | 44659 | 0.52361 | 0.11667 | Inverter Tripped in Contactor Contact Fault | 0.11659 | 0.73675 | 298.5089 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Contactor fault | 3379.2 | 44659 | 0.66736 | 44659 | 0.68403 | 0.4 | Inverter Tripped in Contactor Fault, Mism-ac, Paraller I-high | 0.23076 | 0.73675 | 574.5127 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | PT 01 | PT 01 off due to Buccholz tripped | 48167.3 | 44660 | 0.26944 | 44660 | 0.41667 | 13.4 | Power Trfo-01 Tripped in Buccholz Trip | 0.066079 | 0.7261 | 22638 | As Discussed in the Presence of our HT Expert we did Oil Filteration and BDV value checked found Ok, then Oil Top up to the Power trfo-01 then charged the Trafo.
Bhadla | April | Inverter 13 | MCCB tripped | 3411.2 | 44660 | 0.31667 | 44660 | 0.33472 | 2.12 | Inverter DC/AC MCCB Tripped | 0.083975 | 0.7261 | 1094 | Checked DC, AC Floating then Restart the Inv.
Bhadla | April | SCB.17.13 | String fault | 166.4 | 44660 | 0.52083 | 44660 | 0.53333 | 0.3 | DC Breaker Tripped | 0.30263 | 0.7261 | 36.5649 | DC Floating checked nothing found ok then start the SCB
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44660 | 0.55694 | 44660 | 0.57986 | 0.55 | Inverter Tripped in L-Over Temp. | 0.54882 | 0.7261 | 1382.7493 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 11 | Mism Iac fault | 3379.2 | 44660 | 0.66111 | 44660 | 0.675 | 0.33333 | Inverter Tripped in Mism-Iac Fault. | 0.21033 | 0.7261 | 516.0784 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 22 | Comm. fault | 3468.8 | 44661 | 0.26528 | 44661 | 0.57014 | 7.3167 | Inverter Tripped in Com Fault. | 5.5396 | 0.71843 | 13805.1934 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 1715.2 | 44661 | 0.54514 | 44661 | 0.55903 | 0.33333 | Unit-03 & Unit-04 Tripped in V-ac High | 0.34443 | 0.71843 | 424.4319 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44661 | 0.61389 | 44661 | 0.62569 | 0.28333 | Again Inverter Tripped in V-ac High | 0.2538 | 0.71843 | 629.2071 | SG Team Checked the Inverter, then Reset the Inverter.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44661 | 0.66736 | 44661 | 0.67431 | 0.16667 | Again Inverter Tripped in V-ac High | 0.10766 | 0.71843 | 266.9003 | Discussed with SG Team and gave them all parameters Pic & as per their instructions then Restart the Inv.
Bhadla | April | Inverter 14 | RISO fault | 3430.4 | 44661 | 0.28889 | 44661 | 0.30694 | 0.43333 | Inverter Tripped in Riso Fault | 0.016141 | 0.71843 | 39.7797 | DC Floating Checked floating found ok then start the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 844.8 | 44661 | 0.72014 | 44661 | 0.72917 | 0.21667 | Again Unit-04 Tripped in V-ac High | 0.028838 | 0.71843 | 121 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44662 | 0.56389 | 44662 | 0.58542 | 0.51667 | Inverter Tripped in L-Over Temp. | 0.50846 | 0.7292 | 1286.5193 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | SCB.06.07 | String fault | 179.2 | 44662 | 0.45347 | 44662 | 0.4875 | 0.81667 | DC Breaker Tripped | 0.76079 | 0.7292 | 99.4142 | DC Floating Checked nothing found abnormal then Restart the Breaker.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44662 | 0.54097 | 44662 | 0.55486 | 0.33333 | Inverter Tripped in V-ac High | 0.3389 | 0.7292 | 852.7551 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44662 | 0.61597 | 44662 | 0.63889 | 0.55 | Again Inverter Tripped in V-ac High | 0.42943 | 0.7292 | 1080.5414 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44662 | 0.64931 | 44662 | 0.71528 | 1.5833 | Again Inverter Tripped in V-ac High | 0.68004 | 0.7292 | 1711.1423 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 1760 | 44662 | 0.71528 | 44662 | 0.79236 | 1.85 | Again Inverter Tripped in V-ac High | 0.20242 | 0.7292 | 259.7841 | Again Discussed with SG Team as per their instructions Interchange between Unit-01 & Unit-02 Master & Slave & Unit-03 Keeping OFF then Restart the Inv.
Bhadla | April | Inverter 07 | F fault | 3495.8 | 44662 | 0.77986 | 44662 | 0.79236 | 0.3 | Inverter Tripped in F Fault | 0.002715 | 0.7292 | 6.9209 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 18 | RISO fault | 3481.6 | 44662 | 0.76528 | 44662 | 0.77986 | 0.35 | Inverter Tripped in Riso Fault | 0.011579 | 0.7292 | 29.396 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44662 | 0.53264 | 44662 | 0.55 | 0.41667 | Unit-03 Tripped in Island Protection Fault | 0.23595 | 0.7292 | 616 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44662 | 0.58333 | 44662 | 0.60069 | 0.41667 | Again Unit-03 Tripped in Island Protection Fault | 0.17641 | 0.7292 | 613 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | PDP pro fault | 896 | 44662 | 0.60069 | 44662 | 0.79236 | 4.6 | Unit-01 Tripped in PDP Pro Fault | 1.8217 | 0.7292 | 1190.2365 | When we restart the Inv in Unit-01 Showing Fault PDP Pro as per Sungrow Person Instruction Interchange between Unit-01 & Unit-02 Unit-01 Q1 OFF then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44662 | 0.61319 | 44662 | 0.79236 | 4.3 | Unit-03 Tripped in Island Protection Fault | 1.5555 | 0.7292 | 929.1637
Bhadla | April | Inverter 03 | Ground fault | 3450.4 | 44663 | 0.65139 | 44663 | 0.66181 | 0.25 | Inverter Tripped in Gnd Fault | 0.17135 | 0.73599 | 435.1396 | DC Floating Checked SCB 1D3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | April | SCB.03.08 | String fault | 185.6 | 44663 | 0.6625 | 44663 | 0.69306 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.44509 | 0.73599 | 60.7996 | Again Checked found Ok.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.46042 | 44663 | 0.4625 | 0.05 | Inverter Tripped in V-ac High | 0.047769 | 0.73599 | 121.32 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 2560 | 44663 | 0.50069 | 44663 | 0.50556 | 0.11667 | Unit-2,3,&4 Tripped in V-ac High | 0.11776 | 0.73599 | 221.8793 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 2560 | 44663 | 0.50903 | 44663 | 0.51181 | 0.066667 | Again Unit-2,3,&4 Tripped in V-ac High | 0.068448 | 0.73599 | 128.9654 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.52083 | 44663 | 0.52639 | 0.13333 | Again Inverter Tripped in V-ac High | 0.13699 | 0.73599 | 347.9109 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.53056 | 44663 | 0.53333 | 0.066667 | Again Inverter Tripped in V-ac High | 0.068051 | 0.73599 | 172.8293 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.5375 | 44663 | 0.56944 | 0.76667 | Again Inverter Tripped in V-ac High | 0.7825 | 0.73599 | 1987.305 | Auto-Restarted
Bhadla | April | Inverter 06 | Vac high fault | 2560 | 44663 | 0.58333 | 44663 | 0.60556 | 0.53333 | Again Unit-2,3,&4 Tripped in V-ac High | 0.51321 | 0.73599 | 966.9592 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.61528 | 44663 | 0.62986 | 0.35 | Again Inverter Tripped in V-ac High | 0.30134 | 0.73599 | 765.3122 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 844.8 | 44663 | 0.62986 | 44663 | 0.6375 | 0.18333 | Again Unit-04 Tripped in V-ac High | 0.15106 | 0.73599 | 93.9235 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.63958 | 44663 | 0.66528 | 0.61667 | Again Inverter Tripped in V-ac High | 0.43975 | 0.73599 | 1116.8273 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 844.8 | 44663 | 0.66528 | 44663 | 0.67569 | 0.25 | Again Unit-04 Tripped in V-ac High | 0.15565 | 0.73599 | 96.7813 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 3450.7 | 44663 | 0.67639 | 44663 | 0.70833 | 0.76667 | Again Inverter Tripped in V-ac High | 0.3789 | 0.73599 | 962.2813 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 06 | Vac high fault | 844.8 | 44663 | 0.70833 | 44663 | 0.79444 | 2.0667 | Again Unit-04 Tripped in V-ac High | 0.33673 | 0.73599 | 209.3705 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44663 | 0.46875 | 44663 | 0.51944 | 1.2167 | Unit-03 Tripped in Island Fault | 0.98521 | 0.73599 | 1207 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44663 | 0.54444 | 44663 | 0.79444 | 6 | Unit-03 Tripped in Island Fault | 3.4823 | 0.73599 | 2099.594 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 15 | PDP pro fault | 3475.2 | 44663 | 0.48889 | 44663 | 0.49306 | 0.1 | Inverter Tripped PDP Pro Fault | 0.10105 | 0.73599 | 258.4568 | Auto-Restarted
Bhadla | April | All Inverters | Grid voltage issue | 27710 | 44664 | 0.69861 | 44664 | 0.70764 | 0.21667 | Inv-03,05,06,07,11,12,19,21 derated due to sudden grid jerk in line. | 0.044614 | 0.74741 | 923.9915 | Checked DC, AC Floating then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44664 | 0.475 | 44664 | 0.56042 | 2.05 | Unit-03 Tripped in Island Fault | 0.16518 | 0.74741 | 4377 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 819.2 | 44664 | 0.58403 | 44664 | 0.79514 | 5.0667 | Unit-03 Tripped in Island Fault | 2.1957 | 0.74741 | 1344.3894 | Manually Stopped and start the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 896 | 44664 | 0.56111 | 44664 | 0.79514 | 5.6167 | Unit-01 Tripped in Island Fault | 2.7122 | 0.74741 | 1816.2951 | Manually Stopped and start the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 3468.8 | 44665 | 0.37708 | 44665 | 0.40347 | 0.63333 | Inverter Tripped in Island Protection Fault | 0.23164 | 0.74403 | 597.8285 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Island protection fault | 3468.8 | 44665 | 0.42083 | 44665 | 0.42292 | 0.05 | Again Inverter Tripped in Island Protection Fault | 0.023419 | 0.74403 | 60.4427 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 25 | Parallel I high fault | 896 | 44665 | 0.42292 | 44665 | 0.79375 | 8.9 | Unit-01 Tripped in Parallel I High Fault | 3.7305 | 0.74403 | 2486.9687 | Again Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44666 | 0.52847 | 44666 | 0.55764 | 0.7 | Inverter Tripped in L-Over Temp. | 0.73419 | 0.72337 | 1842.8249 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 3411.2 | 44666 | 0.32569 | 44666 | 0.32986 | 0.1 | Inverter Tripped in Island Protection Fault. | 0.021703 | 0.72337 | 53.5527 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 3411.2 | 44666 | 0.34097 | 44666 | 0.37639 | 0.85 | Again Inverter Tripped in Island Protection Fault. | 0.3442 | 0.72337 | 849.3176 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 896 | 44666 | 0.37708 | 44666 | 0.79583 | 10.05 | Unit-01 Tripped in Island Protection fault | 7.0269 | 0.72337 | 4554.3993 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | SCB.25.17 | String fault | 166.4 | 44666 | 0.46944 | 44666 | 0.48472 | 0.36667 | DC Breaker Tripped | 0.35803 | 0.72337 | 43.0948 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | April | SCB.25.06 | String fault | 192 | 44666 | 0.52986 | 44666 | 0.53681 | 0.16667 | DC Breaker Tripped | 0.1744 | 0.72337 | 24.2223 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44667 | 0.54861 | 44667 | 0.57153 | 0.55 | Inverter Tripped in L-Over Temp. | 0.55741 | 0.72856 | 1409.1392 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 3411.2 | 44667 | 0.28681 | 44667 | 0.31806 | 0.75 | Inverter Tripped in Island Protection Fault. | 0.082203 | 0.72856 | 204.2964 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 896 | 44667 | 0.31875 | 44667 | 0.61181 | 7.0333 | Unit-01 Tripped in Island Protection fault | 5.4888 | 0.72856 | 3583.0453 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 3411.2 | 44667 | 0.6125 | 44667 | 0.63889 | 0.63333 | Again Inverter Tripped in Island Protection Fault. | 0.54028 | 0.72856 | 1342.744 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 896 | 44667 | 0.63889 | 44667 | 0.79653 | 3.7833 | Unit-01 Tripped in Island Protection fault | 1.3128 | 0.72856 | 856.983 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Island protection fault | 3411.2 | 44668 | 0.2625 | 44668 | 0.29444 | 0.76667 | Inverter Tripped in Island Protection Fault | 0.023643 | 0.74646 | 60.2029 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | Mism Iac fault | 896 | 44668 | 0.29444 | 44668 | 0.79653 | 12 | Unit-01 Tripped in Mism ac fault | 2.4157 | 0.74646 | 5694 | Again Discussed with SG Team as per their instructions Interchange between Unit-01 & Unit-02 Master Slave and Unit-01 Q1 Off Keeping OFF then Restart the Inv.
Bhadla | April | Inverter 19 | Contactor fault | 844.8 | 44670 | 0.26111 | 44670 | 0.32708 | 1.5833 | Unit-03 Tripped in Contactor Fault | 0.12688 | 0.75313 | 80.726 | Auto-Restarted
Bhadla | April | SCB.13.15 | String fault | 12.8 | 44670 | 0.26111 | 44670 | 0.42917 | 4.0333 | String found faulty during suspected SCB check. | 1.2997 | 0.75313 | 12.529 | 1 set of MC4 Connector used.
Bhadla | April | Inverter 11 | Contactor fault | 857.6 | 44671 | 0.29306 | 44671 | 0.30486 | 0.28333 | Unit-02 Tripped in Contactor Fault | 0.027275 | 0.76194 | 17.8225 | Discussed with SG Team to Restart the Inv.
Bhadla | April | Inverter 15 | String fault | 844.8 | 44671 | 0.29028 | 44671 | 0.3125 | 0.53333 | String found faulty during suspected SCB check. | 0.056601 | 0.76194 | 36.433 | 3 set of MC4 Connector used.
Bhadla | April | Inverter 12 | Ground fault | 3443.2 | 44671 | 0.34861 | 44671 | 0.36875 | 0.48333 | Inverter Tripped in Gnd Fault | 0.18358 | 0.76194 | 481.6134 | DC Floating checked Fault found in 2C2 & 2D2 keeping those SCB OFF then start the Inv.
Bhadla | April | SCB.12.12 | String fault | 179.2 | 44671 | 0.36875 | 44671 | 0.41875 | 1.2 | Inverter Tripped in Gnd Fault | 0.68837 | 0.76194 | 93.9899 | ST-6 & 11 Isolated then Start the SCB
Bhadla | April | SCB.12.17 | String fault | 166.4 | 44671 | 0.36875 | 44671 | 0.40486 | 0.86667 | Inverter Tripped in Gnd Fault | 0.469 | 0.76194 | 59.4627 | ST-2 Isolated then Start the SCB
Bhadla | April | SCB.12.12 | String fault | 12.8 | 44671 | 0.41875 | 44671 | 0.4375 | 0.45 | ST-6 found Abnormal Floating | 0.33127 | 0.76194 | 3.2308 | Again Checked found Ok.
Bhadla | April | SCB.12.12 | String fault | 12.8 | 44671 | 0.41875 | 44671 | 0.44792 | 0.7 | ST-11 found Abnormal Floating | 0.51981 | 0.76194 | 5.0696 | Found (-Ve) Cable Faulty 25 Mtr cable & 2 set MC4 Connector Used.
Bhadla | April | SCB.12.17 | String fault | 12.8 | 44671 | 0.40486 | 44671 | 0.44097 | 0.86667 | ST-2 found Abnormal Floating | 0.61632 | 0.76194 | 6.0108 | Again Checked found Ok.
Bhadla | April | Inverter 22 | Island protection fault | 3468.8 | 44673 | 0.52847 | 44673 | 0.54167 | 0.31667 | Inverter Tripped in Island Protection Fault | 0.31773 | 0.74042 | 816.0529 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 13 | RISO fault | 3411.2 | 44673 | 0.25833 | 44673 | 0.27153 | 0.31667 | Inverter Tripped in Riso Fault | 0.0034383 | 0.74042 | 8.6843 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | April | Inverter 17 | Contactor fault | 857.6 | 44674 | 0.28958 | 44674 | 0.30347 | 0.33333 | Unit-02 Tripped in Contactor Fault | 0.03416 | 0.74025 | 21.6864 | Discussed with SG Team to Restart the Inv.
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44674 | 0.41667 | 44674 | 0.43056 | 0.33333 | Unit-03 Reactor Over Fauit | 0.229 | 0.74025 | 145.3763 | Auto-Restarted
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44674 | 0.75625 | 44674 | 0.77083 | 0.35 | Again Unit-03 Reactor Over Fauit | 0.032594 | 0.74025 | 20.6919 | Auto-Restarted
Bhadla | April | Inverter 27 | RISO fault | 3404.8 | 44675 | 0.37708 | 44675 | 0.39028 | 0.31667 | Inverter Tripped in Riso Fault | 0.16861 | 0.74217 | 426.0767 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44675 | 0.43472 | 44675 | 0.44444 | 0.23333 | Unit-03 Reactor Over Fauit | 0.18675 | 0.74217 | 118.8657 | Auto-Restarted
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44675 | 0.4625 | 44675 | 0.47431 | 0.28333 | Again Unit-03 Reactor Over Fauit | 0.24447 | 0.74217 | 155.6035 | Auto-Restarted
Bhadla | April | Inverter 20 | RISO fault | 3507.4 | 44676 | 0.25694 | 44676 | 0.27014 | 0.31667 | Inverter Tripped in Riso Fault | 0.003741 | 0.75365 | 9.8888 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | April | SCB.13.12 | String fault | 12.8 | 44677 | 0.25486 | 44677 | 0.52083 | 6.3833 | St-3 Found Faulty during Suspected SCB Check. | 3.493 | 0.73784 | 32.9892 | 1 set of MC4 Connector used.
Bhadla | April | SCB.15.19 | String fault | 12.8 | 44677 | 0.25486 | 44677 | 0.61458 | 8.6333 | St-5 Found Faulty during Suspected SCB Check. | 5.5572 | 0.73784 | 52.4838 | 15Amp Fuse replaced
Bhadla | April | SCB.14.01 | String fault | 12.8 | 44677 | 0.25486 | 44677 | 0.5625 | 7.3833 | St-8 Found Faulty during Suspected SCB Check. | 4.4427 | 0.73784 | 41.9583 | (-VE) Y-Connector Replaced with new One.
Bhadla | April | SCB.27.19 | String fault | 12.8 | 44677 | 0.25486 | 44677 | 0.59375 | 8.1333 | St-11 Found Faulty during Suspected SCB Check. | 5.1167 | 0.73784 | 48.3236 | (-VE) Y-Connector Replaced with new One.
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44678 | 0.53819 | 44678 | 0.5625 | 0.58333 | Inverter Tripped in L-Over Temp. | 0.59112 | 0.73032 | 1497.9877 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | Inverter 15 | Contactor fault | 876.8 | 44678 | 0.25486 | 44678 | 0.30417 | 1.1833 | Unit-02 Tripped in Contactor Fault | 0.070667 | 0.73032 | 45.2512 | Discussed with SG Team to Restart the Inv.
Bhadla | April | Inverter 15 | PDP pro fault | 3475.2 | 44678 | 0.53889 | 44678 | 0.54375 | 0.11667 | Inverter Tripped PDP Pro Fault | 0.13266 | 0.73032 | 336.6869 | Auto-Restarted
Bhadla | April | Inverter 02 | L over temp fault | 3469.9 | 44679 | 0.52222 | 44679 | 0.54375 | 0.51667 | Inverter Tripped in L-Over Temp. | 0.51188 | 0.74025 | 1314.8086 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | SCB.01.12 | String fault | 166.4 | 44679 | 0.50347 | 44679 | 0.50833 | 0.11667 | DC Breaker Tripped | 0.11563 | 0.74025 | 14.2436 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | April | SCB.13.10 | String fault | 12.8 | 44679 | 0.25417 | 44679 | 0.53125 | 6.65 | St-5 Found Faulty during Suspected SCB Check. | 3.846 | 0.74025 | 36.4412 | 1 set of MC4 Connector used.
Bhadla | April | SCB.22.13 | String fault | 12.8 | 44679 | 0.25417 | 44679 | 0.61806 | 8.7333 | St-11 Found Faulty during Suspected SCB Check. | 5.8148 | 0.74025 | 55.0969 | 1 set of MC4 Connector used.
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44680 | 0.67986 | 44680 | 0.68542 | 0.13333 | Unit-03 Tripped in Reactor Over Temp | 0.077299 | 0.72326 | 47.9462 | Auto-Restarted
Bhadla | April | Inverter 17 | Contactor fault | 870.4 | 44680 | 0.30139 | 44680 | 0.3125 | 0.26667 | Unit-03 Tripped in Contactor Fault | 0.045686 | 0.72326 | 28.7606 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | April | SCB.17.12 | String fault | 192 | 44681 | 0.68681 | 44681 | 0.69306 | 0.15 | DC Breaker Tripped | 0.079869 | 0.72648 | 11.1404 | DC Floating checked nothimg found abnormal then start the SCB
Bhadla | April | Inverter 27 | Reactor over temp fault | 857.6 | 44681 | 0.43472 | 44681 | 0.48333 | 1.1667 | Unit-03 Tripped in Reactor Over Temp Fault | 0.6442 | 0.72648 | 1303 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44682 | 0.40694 | 44682 | 0.41597 | 0.21667 | Unit-03 Tripped in Reactor Over Temp | 0.16 | 0.72581 | 99.5931 | Auto-Restarted
Bhadla | May | Inverter 25 | Grid voltage issue | 3468.8 | 44683 | 0.46319 | 44683 | 0.47153 | 0.2 | Only Inverter-25 Tripped due to due to Under voltage in Line | 0.17739 | 0.77631 | 477.6938 | Manually Reastarted after Grid Voltage Resume (due to sudden jerk in line)
Bhadla | May | Inverter-1,2,3,4,5,6,9,10,11,12,13,14,15,16,17,18,19,20,21,23,24,25,26, 28 | Grid voltage issue | 82746.5 | 44683 | 0.51944 | 44683 | 0.53125 | 0.28333 | Inverter-1,2,3,4,5,6,9,10,11,12,13,14,15,16,17,18,19,20,21,23,24,25,26, 28 Tripped due to Sudden Unbalance in Grid Voltage | 0.2319 | 0.77631 | 14896.5742 | Manually Reastarted after Grid Voltage Resume (due to sudden jerk in line)
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44683 | 0.43333 | 44683 | 0.43472 | 0.033333 | Unit-03 Tripped in Reactor Over Temp | 0.025186 | 0.77631 | 16.7681 | Auto-Restarted
Bhadla | May | SCB.14.12 | String fault | 6.4 | 44683 | 0.25208 | 44683 | 0.61458 | 8.7 | String-5 found faulty during suspected SCB check. | 5.018 | 0.77631 | 24.9313 | one 15Amp fuse used in Y-Connector.
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44684 | 0.45903 | 44684 | 0.46111 | 0.05 | Unit-03 Tripped in Reactor Over Temp Fault | 0.03987 | 0.77673 | 26.5581 | Auto-Restarted
Bhadla | May | SCB.14.14 | String fault | 6.4 | 44684 | 0.25139 | 44684 | 0.59375 | 8.2167 | St-14 Found Faulty during Suspected SCB Check. | 4.7506 | 0.77673 | 23.6154 | one 15Amp fuse used in Y-Connector.
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44685 | 0.47153 | 44685 | 0.47292 | 0.033333 | Unit-03 Tripped in Reactor Over Temp Fault | 0.026678 | 0.73148 | 16.7354 | Auto-Restarted
Bhadla | May | Inverter 12 | Ground fault | 3443.2 | 44685 | 0.52153 | 44685 | 0.54028 | 0.45 | Inverter Tripped in Gnd Fault | 0.41513 | 0.73148 | 1045.5526 | Found 10Amp GFD Fuse faulty same replaced & Dc Floating Checked fault found in 2B1 keeping that SCB off then start the Inv.
Bhadla | May | SCB.12.06 | String fault | 12.8 | 44685 | 0.54028 | 44685 | 0.56181 | 0.51667 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.47538 | 0.73148 | 4.451 | Again Checked found Ok.
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44686 | 0.43472 | 44686 | 0.43889 | 0.1 | Unit-03 Tripped in Reactor Over Temp Fault | 0.070899 | 0.73524 | 44.7047 | Auto-Restarted
Bhadla | May | Block 13 | Block 13 IDT tripped due to exceeded high temp. | 6963.2 | 44687 | 0.48472 | 44687 | 0.50833 | 0.56667 | Block-13 IDT WTI LV-01 Tripped due to Exceeded in High Temp. | 0.50748 | 0.73597 | 2600.708 | Checked the Meter then Reset the Meter after that visually checked found Ok then Charged the Transformer.
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44687 | 0.44236 | 44687 | 0.44514 | 0.066667 | Unit-03 Tripped in Reactor Over Temp Fault | 0.051035 | 0.73597 | 32.2116 | Auto-Restarted
Bhadla | May | Inverter 27 | Reactor over temp fault | 857.6 | 44689 | 0.42083 | 44689 | 0.42222 | 0.033333 | Unit-03 Tripped in Reactor Over Temp Fault | 0.037804 | 0.72455 | 23.4904 | Auto-Restarted
Bhadla | May | Inverter 23 | Ground fault | 3456 | 44689 | 0.43472 | 44689 | 0.44444 | 0.23333 | Inverter Tripped in Gnd Fault | 0.20155 | 0.72455 | 504.6907 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | May | Inverter 28 | Contactor fault | 870.4 | 44692 | 0.31736 | 44692 | 0.33194 | 0.35 | Unit-04 Tripped in Contactor Fault | 0.092566 | 0.72915 | 58.7471 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | May | Inverter 28 | Contactor fault | 870.4 | 44693 | 0.31458 | 44693 | 0.32639 | 0.28333 | Unit-04 Tripped in Contactor Fault | 0.070262 | 0.72304 | 44.2182 | Discussed with SG Team to Restart the Inv.
Bhadla | May | Inverter 23 | Ground fault | 3456 | 44693 | 0.44028 | 44693 | 0.45069 | 0.25 | Inverter Tripped in Gnd Fault | 0.21396 | 0.72304 | 534.6566 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | May | Inverter 10 | Ground fault | 3404.8 | 44693 | 0.48681 | 44693 | 0.49792 | 0.26667 | Inverter Tripped in Gnd Fault | 0.25878 | 0.72304 | 637.0706 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | May | Inverter 10 | RISO fault | 3404.8 | 44695 | 0.24514 | 44695 | 0.25833 | 0.31667 | Inverter Tripped in Riso Low Fault | 0.0023182 | 0.7268 | 5.7365 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | May | Inverter 28 | Contactor fault | 870.4 | 44695 | 0.30903 | 44695 | 0.31875 | 0.23333 | Unit-04 Tripped in Contactor Fault | 0.059349 | 0.7268 | 37.5447 | Discussed with SG Team to Restart the Inv.
Bhadla | May | Inverter 16 | Ground fault | 3411.2 | 44698 | 0.33681 | 44698 | 0.35625 | 0.46667 | Inverter Tripped in Gnd Fault | 0.17059 | 0.73902 | 430.0581 | DC Floating Checked SCB 2C5 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | May | SCB.16.15 | String fault | 166.4 | 44698 | 0.35625 | 44698 | 0.37847 | 0.53333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.24905 | 0.73902 | 30.6266 | ST-13 Isolated then Start the SCB
Bhadla | May | SCB.16.15 | String fault | 12.8 | 44698 | 0.37847 | 44698 | 0.40625 | 0.66667 | ST-13 found Abnormal Floating | 0.39926 | 0.73902 | 3.7768 | Found (-ve) String Cable 60Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | May | Inverter 21 | Ground fault | 3494.4 | 44699 | 0.24444 | 44699 | 0.26319 | 0.45 | Inverter Tripped in Gnd Fault | 0.0052363 | 0.72345 | 13.2375 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 22 | Ground fault | 3468.8 | 44699 | 0.28403 | 44699 | 0.32569 | 1 | Inverter Tripped in Gnd Fault | 0.093239 | 0.72345 | 233.9827 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 22 | Leakage current fault | 3468.8 | 44701 | 0.36667 | 44701 | 0.38264 | 0.38333 | Inverter Tripped in Leakage Current Fault | 0.20532 | 0.75812 | 539.945 | DC Floating Checked SCB 2A3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | May | SCB.22.03 | String fault | 192 | 44701 | 0.38264 | 44701 | 0.39792 | 0.36667 | Manually Stopped as found Abnormal Floating During INV Leakage Current Fault attend | 0.2242 | 0.75812 | 32.6338 | ST-2 Isolated then Start the SCB
Bhadla | May | SCB.22.03 | String fault | 12.8 | 44701 | 0.39792 | 44701 | 0.41667 | 0.45 | ST-02 found Abnormal Floating | 0.3068 | 0.75812 | 2.9771 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | May | Inverter-1, 10, 12, 18, 20, 21, 23 & 25 | Grid voltage issue | 27707.7 | 44701 | 0.52222 | 44701 | 0.53264 | 0.25 | Inverter-1, 10, 12, 18, 20, 21, 23 & 25 Tripped due to Under Voltage in Line. | 0.2256 | 0.75812 | 4738.9152 | Manually Reastarted after Grid Voltage Resume (due to sudden jerk in line)
Bhadla | May | Inverter 25 | Ground fault | 3468.8 | 44703 | 0.51458 | 44703 | 0.52014 | 0.13333 | Inverter Tripped in Gnd Fault | 0.13076 | 0.72601 | 329.2927 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 08 | Ground fault | 3444.2 | 44704 | 0.32708 | 44704 | 0.35694 | 0.71667 | Inverter Tripped in Gnd Fault | 0.11738 | 0.72051 | 291.2856 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 16 | Ground fault | 3411.2 | 44704 | 0.32639 | 44704 | 0.34167 | 0.36667 | Inverter Tripped in Gnd Fault | 0.026012 | 0.72051 | 63.9316 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 21 | Ground fault | 3494.4 | 44704 | 0.325 | 44704 | 0.34028 | 0.36667 | Inverter Tripped in Gnd Fault | 0.029331 | 0.72051 | 73.8485 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 25 | Ground fault | 3468.8 | 44704 | 0.32569 | 44704 | 0.35347 | 0.66667 | Inverter Tripped in Gnd Fault | 0.096861 | 0.72051 | 242.0845 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | May | Inverter 23 | Voc high fault | 3456 | 44704 | 0.77708 | 44704 | 0.78403 | 0.16667 | Inverter Tripped in Voc High Fault | 0.007547 | 0.72051 | 18.7925 | Discussed with SG Team to Restart the Inv.
Bhadla | May | SCB.08.07 | String fault | 12.8 | 44711 | 0.53125 | 44711 | 0.55556 | 0.58333 | Block-4 Inv-08 SCB 2B2 St-15 Found fuse faulty | 0.56184 | 0.72966 | 5.2473 | New fuse Replaced
Bhadla | May | Inverter 28 | Contactor fault | 869.8 | 44712 | 0.31597 | 44712 | 0.325 | 0.21667 | Unit-04 Tripped in Contactor Fault | 0.05317 | 0.73563 | 34.0207 | Auto-Restarted
Bhadla | June | Inverter 12 | Leakage current fault | 3443.2 | 44714 | 0.36389 | 44714 | 0.37708 | 0.31667 | Inverter Tripped in Leakage Current Fault | 0.15836 | 0.72064 | 392.9506 | DC Floating Checked SCB 2C1,2B3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB.12.11 | String fault | 179.2 | 44714 | 0.37708 | 44714 | 0.4 | 0.55 | Inverter Tripped in Leakage Current Fault | 0.30976 | 0.72064 | 40.0016 | Agin Check Found Ok
Bhadla | June | SCB.12.08 | String fault | 166.4 | 44714 | 0.37708 | 44714 | 0.4 | 0.55 | Inverter Tripped in Leakage Current Fault | 0.30976 | 0.72064 | 37.1443 | Agin Check Found Ok
Bhadla | June | Inverter 16 | Ground fault | 3411.2 | 44716 | 0.25694 | 44716 | 0.28472 | 0.66667 | Inverter Tripped in Gnd Fault | 0.041025 | 0.74171 | 103.7975 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 22 | RISO fault | 3468.8 | 44716 | 0.75556 | 44716 | 0.76806 | 0.3 | Inverter Tripped in Riso Fault | 0.046137 | 0.74171 | 118.7029 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 11 | Island protection fault | 3379.2 | 44717 | 0.26389 | 44717 | 0.27361 | 0.23333 | Inverter Tripped in Island Protection Fault | 0.012717 | 0.73524 | 31.5954 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 27 | RISO fault | 3404.8 | 44720 | 0.23958 | 44720 | 0.25833 | 0.45 | Inverter Tripped in Riso Fault | 0.005505 | 0.73012 | 13.685 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 12 | Ground fault | 3443.2 | 44720 | 0.42153 | 44720 | 0.43542 | 0.33333 | Inverter Tripped in Gnd Fault | 0.25813 | 0.73012 | 648.9396 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 12 | Ground fault | 3443.2 | 44721 | 0.30208 | 44721 | 0.32222 | 0.48333 | Inverter Tripped in Gnd Fault | 0.10828 | 0.72833 | 271.556 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 12 | Ground fault | 3443.2 | 44721 | 0.34097 | 44721 | 0.34792 | 0.16667 | Inverter Tripped in Gnd Fault | 0.067928 | 0.72833 | 170.3492 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 24 | RISO fault | 3392 | 44722 | 0.23958 | 44722 | 0.25903 | 0.46667 | Inverter Tripped in Riso Fault | 0.0055348 | 0.72701 | 13.649 | DC Floating Checked nothing found Abnormal then Start the Inv.
Bhadla | June | Inverter 07 | Grid voltage issue | 3495.8 | 44722 | 0.70069 | 44722 | 0.71528 | 0.35 | Inverter Tripped due to Sudden Unbalance in Grid Voltage. | 0.14912 | 0.72701 | 378.9963 | Inverter Resumed after Grid voltage normalized.
Bhadla | June | Inverter 21 | Grid voltage issue | 3494.4 | 44722 | 0.70069 | 44722 | 0.71528 | 0.35 | Inverter Tripped due to Sudden Unbalance in Grid Voltage. | 0.14912 | 0.72701 | 378.8446 | Inverter Resumed after Grid voltage normalized.
Bhadla | June | Inverter 27 | Ground fault | 3404.8 | 44724 | 0.26597 | 44724 | 0.3 | 0.81667 | Inverter Tripped in Gnd Fault | 0.084051 | 0.72357 | 207.0671 | DC Floating Checked SCB 1A3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB.14.03 | String fault | 166.4 | 44724 | 0.3 | 44724 | 0.31736 | 0.41667 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.090477 | 0.72357 | 10.8935 | Agin Checkd Found Ok
Bhadla | June | Inverter 14 | RISO fault | 3430.4 | 44725 | 0.23958 | 44725 | 0.2625 | 0.55 | Inverter Tripped in Riso Low Fault | 0.0082485 | 0.71744 | 20.3005 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44725 | 0.56597 | 44725 | 0.57847 | 0.3 | Inverter Tripped in Island Protection Fault | 0.22561 | 0.71744 | 567.7164 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 27 | Ground fault | 3404.8 | 44726 | 0.37778 | 44726 | 0.40694 | 0.7 | Inverter Tripped in Gnd Fault | 0.41338 | 0.70559 | 993.1117 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44726 | 0.56319 | 44726 | 0.57222 | 0.21667 | Inverter Tripped in Island Protection Fault | 0.23007 | 0.70559 | 569.3896 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44726 | 0.65556 | 44726 | 0.66875 | 0.31667 | Agin Inverter Tripped in Island Protection Fault | 0.24922 | 0.70559 | 616.7639 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44726 | 0.67431 | 44726 | 0.68333 | 0.21667 | Agin Inverter Tripped in Island Protection Fault | 0.14857 | 0.70559 | 367.6697 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 832 | 44726 | 0.68333 | 44726 | 0.81736 | 3.2167 | Inverter Tripped in Island Protection Fault Unit-01 | 0.82924 | 0.70559 | 486.8107 | Again Discussed with SG Team as per their instructions Interchange between Unit-01 & Unit-02 Master Slave and Unit-01 Q1 Off Keeping OFF then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44727 | 0.39097 | 44727 | 0.39861 | 0.18333 | Inverter Tripped in Island Protection Fault | 0.12295 | 0.73252 | 315.8999 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 832 | 44727 | 0.39861 | 44727 | 0.81667 | 10.0333 | Inverter Tripped in Island Protection Fault Unit-01 | 6.5019 | 0.73252 | 3962.6345 | Again Discussed with SG Team as per their instructions Interchange between Unit-01 & Unit-02 Master Slave and Unit-01 Q1 Off Keeping OFF then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 3507.4 | 44728 | 0.36875 | 44728 | 0.39306 | 0.58333 | Inverter Tripped in Island Protection Fault | 0.33391 | 0.7217 | 845.2308 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 20 | Island protection fault | 832 | 44728 | 0.39306 | 44728 | 0.81597 | 10.15 | Inverter Tripped in Island Protection Fault Unit-01 | 5.9589 | 0.7217 | 3578.0102 | Again Discussed with SG Team as per their instructions Interchange between Unit-01 & Unit-02 Master Slave and Unit-01 Q1 Off Keeping OFF then Restart the Inv.
Bhadla | June | Inverter 16 | Leakage current fault | 3411.2 | 44729 | 0.26181 | 44729 | 0.26944 | 0.18333 | Inverter Tripped in Leakage Current Fault | 0.0090067 | 0.72794 | 22.365 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 13 | RISO fault | 3411.2 | 44731 | 0.22847 | 44731 | 0.25486 | 0.63333 | Inverter Tripped in Riso Low Fault | 0.0026687 | 0.79779 | 7.2626 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 27 | RISO fault | 3404.8 | 44731 | 0.24306 | 44731 | 0.26944 | 0.63333 | Inverter Tripped in Riso Low Fault | 0.01281 | 0.79779 | 34.7965 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 21 | RISO fault | 3494.4 | 44731 | 0.24306 | 44731 | 0.26944 | 0.63333 | Inverter Tripped in Riso Low Fault | 0.01281 | 0.79779 | 35.7122 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 23 | RISO fault | 3456 | 44731 | 0.24306 | 44731 | 0.26875 | 0.61667 | Inverter Tripped in Riso Low Fault | 0.012086 | 0.79779 | 33.3231 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 10 | RISO fault | 3404.8 | 44731 | 0.24306 | 44731 | 0.28125 | 0.91667 | Inverter Tripped in Riso Low Fault | 0.02969 | 0.79779 | 80.6471 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 26 | RISO fault | 3494.4 | 44731 | 0.24306 | 44731 | 0.28958 | 1.1167 | Inverter Tripped in Riso Low Fault | 0.048878 | 0.79779 | 136.2626 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 06 | RISO fault | 3450.7 | 44731 | 0.24306 | 44731 | 0.27222 | 0.7 | Inverter Tripped in Riso Low Fault | 0.015998 | 0.79779 | 44.0406 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 12 | RISO fault | 3443.2 | 44731 | 0.45208 | 44731 | 0.47222 | 0.48333 | Inverter Tripped in Riso Low Fault | 0.19121 | 0.79779 | 525.2571 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 19 | RISO fault | 3520 | 44731 | 0.45 | 44731 | 0.4875 | 0.9 | Inverter Tripped in Riso Low Fault | 0.40405 | 0.79779 | 1134.6559 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 25 | RISO fault | 3468.8 | 44731 | 0.45486 | 44731 | 0.49097 | 0.86667 | Inverter Tripped in Riso Low Fault | 0.41906 | 0.79779 | 1159.6846 | DC Floating Checked SCB 1B1 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB.25.06 | String fault | 192 | 44731 | 0.49097 | 44731 | 0.57222 | 1.95 | Inverter Tripped in Riso Low Fault | 1.4743 | 0.79779 | 225.8286 | Again Checked found Ok.
Bhadla | June | Inverter 27 | RISO fault | 3404.8 | 44731 | 0.45833 | 44731 | 0.5 | 1 | Inverter Tripped in Riso Low Fault | 0.48981 | 0.79779 | 1330.4697 | DC Floating Checked SCB 1A2,1B3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB 14.02 | String fault | 166 | 44731 | 0.5 | 44731 | 0.53472 | 0.83333 | Inverter Tripped in Riso Low Fault | 0.55617 | 0.79779 | 73.6549 | Again Checked found Ok.
Bhadla | June | SCB 14.13 | String fault | 192 | 44731 | 0.5 | 44731 | 0.53542 | 0.85 | Inverter Tripped in Riso Low Fault | 0.56859 | 0.79779 | 87.095 | Again Checked found Ok.
Bhadla | June | Inverter 21 | RISO fault | 3404.8 | 44731 | 0.45347 | 44731 | 0.47986 | 0.63333 | Inverter Tripped in Riso Low Fault | 0.28031 | 0.79779 | 761.4238 | DC Floating Checked SCB 1A2,1A4,1A5 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB 11.02 | String fault | 179 | 44731 | 0.47986 | 44731 | 0.53125 | 1.2333 | Inverter Tripped in Riso Low Fault | 0.71553 | 0.79779 | 102.1811 | Again Checked found Ok.
Bhadla | June | SCB 11.04 | String fault | 166 | 44731 | 0.47986 | 44731 | 0.53125 | 1.2333 | Inverter Tripped in Riso Low Fault | 0.71553 | 0.79779 | 94.7601 | Again Checked found Ok.
Bhadla | June | SCB 11.05 | String fault | 140 | 44731 | 0.47986 | 44731 | 0.53125 | 1.2333 | Inverter Tripped in Riso Low Fault | 0.71553 | 0.79779 | 79.9182 | Again Checked found Ok.
Bhadla | June | Inverter 24 | RISO fault | 3392 | 44731 | 0.46181 | 44731 | 0.50069 | 0.93333 | Inverter Tripped in Riso Low Fault | 0.47318 | 0.79779 | 1280.4797 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter -01,6,7,9,11,12,19,21 | Grid voltage issue | 27658.8 | 44731 | 0.49097 | 44731 | 0.50625 | 0.36667 | Inverter-1,6,7,9,11,12,19,21 Tripped due to Sudden Unbalance in Grid Voltage | 0.14617 | 0.79779 | 3225.4496 | Inverter Resumed after Grid voltage normalized.
Bhadla | June | Inverter 09 | RISO fault | 3424 | 44732 | 0.24583 | 44732 | 0.28681 | 0.98333 | Inverter Tripped in Riso Low Fault | 0.011157 | 0.77234 | 29.5046 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 10 | RISO fault | 3404.8 | 44732 | 0.24583 | 44732 | 0.28681 | 0.98333 | Inverter Tripped in Riso Low Fault | 0.011157 | 0.77234 | 29.3391 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 24 | RISO fault | 3392 | 44732 | 0.24583 | 44732 | 0.27569 | 0.71667 | Inverter Tripped in Riso Low Fault | 0.0075393 | 0.77234 | 19.7514 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 24 | Leakage current fault | 3392 | 44732 | 0.38125 | 44732 | 0.42292 | 1 | Inverter Tripped in Leakage Current Fault | 0.57694 | 0.77234 | 1511.4411 | DC Floating Checked SCB 2B2,2B3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB 12.12 | String fault | 166.4 | 44732 | 0.42292 | 44732 | 0.45278 | 0.71667 | Inverter Tripped in Leakage Current Fault | 0.44971 | 0.77234 | 57.7958 | ST-10 Isolated then Start the SCB
Bhadla | June | SCB 12.10 | String fault | 12.8 | 44732 | 0.45278 | 44732 | 0.5625 | 2.6333 | Inverter Tripped in Leakage Current Fault | 2.0285 | 0.77234 | 20.0535 | y connector replaced
Bhadla | June | SCB 12.13 | String fault | 166.4 | 44732 | 0.45278 | 44732 | 0.47569 | 0.55 | Inverter Tripped in Leakage Current Fault | 0.41703 | 0.77234 | 53.5959 | ST-13 Isolated then Start the SCB
Bhadla | June | SCB 12.13 | String fault | 12.8 | 44732 | 0.47569 | 44732 | 0.575 | 2.3833 | Inverter Tripped in Leakage Current Fault | 1.8243 | 0.77234 | 18.0348 | Found (-ve) String Cable 42Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | June | Inverter 27 | Ground fault | 3404.8 | 44732 | 0.53333 | 44732 | 0.54514 | 0.28333 | Inverter Tripped in Gnd Fault | 0.25403 | 0.77234 | 668.0029 | DC Floating Checked SCB 1A2 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB27.02 | String fault | 166.4 | 44732 | 0.54514 | 44732 | 0.55625 | 0.26667 | Inverter Tripped in Gnd Fault | 0.22601 | 0.77234 | 29.0462 | ST-06 Isolated then Start the SCB
Bhadla | June | SCB27.02 | String fault | 12.8 | 44732 | 0.55625 | 44732 | 0.64236 | 2.0667 | Inverter Tripped in Gnd Fault | 1.5206 | 0.77234 | 15.0326 | y connector replaced
Bhadla | June | Inverter 07 | Ground fault | 3495.8 | 44733 | 0.56944 | 44733 | 0.59444 | 0.6 | Inverter Tripped in Gnd Fault | 0.26 | 0.78134 | 710.1669 | DC Floating Checked SCB 1A1,1C5,1D4 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB4.1 | String fault | 192 | 44733 | 0.59444 | 44733 | 0.71806 | 2.9667 | Inverter Tripped in Gnd Fault | 1.48 | 0.78134 | 222.0258 | Again Checked found Ok.
Bhadla | June | SCB4.15 | String fault | 192 | 44733 | 0.59444 | 44733 | 0.71667 | 2.9333 | Inverter Tripped in Gnd Fault | 1.48 | 0.78134 | 222.0258 | Again Checked found Ok.
Bhadla | June | SCB4. 19 | String fault | 192 | 44733 | 0.59444 | 44733 | 0.71667 | 2.9333 | Inverter Tripped in Gnd Fault | 1.48 | 0.78134 | 222.0258 | Again Checked found Ok.
Bhadla | June | Inverter 28 | Ground fault | 3379.2 | 44733 | 0.52083 | 44733 | 0.54306 | 0.53333 | Inverter Tripped in Gnd Fault | 0.02 | 0.78134 | 52.8061 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 28 | Ground fault | 3379.2 | 44733 | 0.57917 | 44733 | 0.61042 | 0.75 | Inverter Tripped in Gnd Fault | 0.56 | 0.78134 | 1478.5718 | DC Floating Checked SCB 2D1found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB14.16 | String fault | 179.2 | 44733 | 0.61042 | 44733 | 0.68681 | 1.8333 | Inverter Tripped in Gnd Fault | 0.93 | 0.78134 | 130.2151 | Again Checked found Ok.
Bhadla | June | Inverter 19 | Ground fault | 3520 | 44733 | 0.51458 | 44733 | 0.60417 | 2.15 | Inverter Tripped in Gnd Fault | 0.65 | 0.78134 | 1787.7077 | DC Floating Checked SCB 1D1found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB10.16 | String fault | 166.4 | 44733 | 0.60417 | 44733 | 0.69653 | 2.2167 | Inverter Tripped in Gnd Fault | 1.25 | 0.78134 | 162.5189 | Again Checked found Ok.
Bhadla | June | Inverter 24 | Ground fault | 3392 | 44733 | 0.51319 | 44733 | 0.59722 | 2.0167 | Inverter Tripped in Gnd Fault | 0.45 | 0.78134 | 1192.6386 | DC Floating Checked SCB 2c3found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB12.13 | String fault | 192 | 44733 | 0.59722 | 44733 | 0.71806 | 2.9 | Inverter Tripped in Gnd Fault | 1.39 | 0.78134 | 208.5242 | Again Checked found Ok.
Bhadla | June | Inverter 10 | Ground fault | 3404.8 | 44733 | 0.50764 | 44733 | 0.55556 | 1.15 | Inverter Tripped in Gnd Fault | 0.08 | 0.78134 | 212.8247 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 10 | Ground fault | 3404.8 | 44733 | 0.57014 | 44733 | 0.60069 | 0.73333 | Inverter Tripped in Gnd Fault | 0.42 | 0.78134 | 1117.3298 | DC Floating Checked SCB 2B2,2B3,2C1,2C4,2C5,2D3,2D4 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB5.7 | String fault | 179.2 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 119.0138 | Again Checked found Ok.
Bhadla | June | SCB5.8 | String fault | 166.4 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 110.5128 | Again Checked found Ok.
Bhadla | June | SCB5.11 | String fault | 179.2 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 119.0138 | Again Checked found Ok.
Bhadla | June | SCB5.14 | String fault | 166.4 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 110.5128 | Again Checked found Ok.
Bhadla | June | SCB5.15 | String fault | 166.4 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 110.5128 | Again Checked found Ok.
Bhadla | June | SCB5.18 | String fault | 179.2 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 119.0138 | Again Checked found Ok.
Bhadla | June | SCB5.19 | String fault | 153.6 | 44733 | 0.60069 | 44733 | 0.66181 | 1.4667 | Inverter Tripped in Gnd Fault | 0.85 | 0.78134 | 102.0119 | Again Checked found Ok.
Bhadla | June | Inverter 26 | Ground fault | 3494.4 | 44733 | 0.53889 | 44733 | 0.57014 | 0.75 | Inverter Tripped in Gnd Fault | 0.09 | 0.78134 | 245.7285 | DC Floating Checked SCB 2A2,2B5,2C3,2C4 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB13.2 | String fault | 166.4 | 44733 | 0.57014 | 44733 | 0.66181 | 2.2 | Inverter Tripped in Gnd Fault | 1.26 | 0.78134 | 163.819 | Again Checked found Ok.
Bhadla | June | SCB13.10 | String fault | 166.4 | 44733 | 0.57014 | 44733 | 0.66181 | 2.2 | Inverter Tripped in Gnd Fault | 1.26 | 0.78134 | 163.819 | Again Checked found Ok.
Bhadla | June | SCB13.13 | String fault | 166.4 | 44733 | 0.57014 | 44733 | 0.66181 | 2.2 | Inverter Tripped in Gnd Fault | 1.26 | 0.78134 | 163.819 | Again Checked found Ok.
Bhadla | June | SCB13.14 | String fault | 166.4 | 44733 | 0.57014 | 44733 | 0.66181 | 2.2 | Inverter Tripped in Gnd Fault | 1.26 | 0.78134 | 163.819 | Again Checked found Ok.
Bhadla | June | Inverter 25 | Ground fault | 3468.8 | 44733 | 0.54861 | 44733 | 0.56806 | 0.46667 | Inverter Tripped in Gnd Fault | 0.07 | 0.78134 | 189.722 | DC Floating Checked SCB 1A3,1B3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB13.16 | String fault | 192 | 44733 | 0.56806 | 44733 | 0.65972 | 2.2 | Inverter Tripped in Gnd Fault | 1.24 | 0.78134 | 186.0216 | Again Checked found Ok.
Bhadla | June | SCB13.17 | String fault | 166.4 | 44733 | 0.56806 | 44733 | 0.65972 | 2.2 | Inverter Tripped in Gnd Fault | 1.24 | 0.78134 | 161.2187 | Again Checked found Ok.
Bhadla | June | Inverter 21 | Ground fault | 3494.4 | 44733 | 0.51667 | 44733 | 0.61806 | 2.4333 | Inverter Tripped in Gnd Fault | 0.83 | 0.78134 | 2266.1633 | DC Floating Checked SCB 1D3 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB11.18 | String fault | 179.2 | 44733 | 0.61806 | 44733 | 0.71111 | 2.2333 | Inverter Tripped in Gnd Fault | 0.96 | 0.78134 | 134.4156 | Again Checked found Ok.
Bhadla | June | Inverter 01 | Ground fault | 3451.5 | 44734 | 0.24514 | 44734 | 0.27569 | 0.73333 | Inverter Tripped in Gnd Fault | 0.014855 | 0.78256 | 40.1241 | DC Floating Checked SCB 1C4 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB1.14 | String fault | 153.6 | 44734 | 0.27569 | 44734 | 0.35486 | 1.9 | Inverter Tripped in Gnd Fault | 0.32406 | 0.78256 | 38.9526 | ST-4&6 Isolated then Start the SCB
Bhadla | June | SCB1.14.4 | String fault | 12.8 | 44734 | 0.35486 | 44734 | 0.49306 | 3.3167 | Inverter Tripped in Gnd Fault | 2.13 | 0.78256 | 21.3362 | 1per mc4 connector and 20 mtr cable changed
Bhadla | June | SCB1.14.6 | String fault | 12.8 | 44734 | 0.35486 | 44734 | 0.52083 | 3.9833 | Inverter Tripped in Gnd Fault | 2.7125 | 0.78256 | 27.1709 | 1per mc4 connector and 20 mtr cable changed
Bhadla | June | Inverter 08 | RISO fault | 3444.2 | 44734 | 0.24514 | 44734 | 0.28472 | 0.95 | Inverter Tripped in Riso Low Fault | 0.026402 | 0.78256 | 71.1628 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 10 | RISO fault | 3404.8 | 44734 | 0.24514 | 44734 | 0.28472 | 0.95 | Inverter Tripped in Riso Low Fault | 0.026402 | 0.78256 | 70.3487 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 14 | RISO fault | 3430.4 | 44734 | 0.24514 | 44734 | 0.27083 | 0.61667 | Inverter Tripped in Riso Low Fault | 0.010624 | 0.78256 | 28.5202 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 27 | RISO fault | 3404.8 | 44734 | 0.24514 | 44734 | 0.29444 | 1.1833 | Inverter Tripped in Riso Low Fault | 0.041998 | 0.78256 | 111.9016 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 21 | Leakage current fault | 3494.4 | 44734 | 0.52153 | 44734 | 0.54722 | 0.61667 | Inverter Tripped in Leakage current Fault | 0.56394 | 0.78256 | 1542.1531 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | SCB11.15 | String fault | 166.4 | 44734 | 0.54722 | 44734 | 0.55278 | 0.13333 | Inverter Tripped in Leakage current Fault | 0.13178 | 0.78256 | 17.1606 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | SCB14.16.1 | String fault | 12.8 | 44734 | 0.38194 | 44734 | 0.60417 | 5.3333 | String Cable Faulty | 4.2009 | 0.78256 | 42.0794 | 40 m tr cable Replaced
Bhadla | June | SCB14.16.5 | String fault | 12.8 | 44734 | 0.38194 | 44734 | 0.51389 | 3.1667 | String Cable Faulty | 2.3049 | 0.78256 | 23.0882 | 48 m tr cable Replaced
Bhadla | June | SCB10.16.10 | String fault | 12.8 | 44734 | 0.41389 | 44734 | 0.53125 | 2.8167 | Y connector burnt | 2.2503 | 0.78256 | 22.541 | y connector replaced
Bhadla | June | SCB5.16.2 | String fault | 12.8 | 44734 | 0.4375 | 44734 | 0.55 | 2.7 | Y connector burnt | 2.2703 | 0.78256 | 22.7416 | y connector replaced
Bhadla | June | SCB5.19.12 | String fault | 12.8 | 44734 | 0.46181 | 44734 | 0.66667 | 4.9167 | Y connector burnt | 4.0227 | 0.78256 | 40.2941 | y connector replaced
Bhadla | June | SCB5.14.6 | String fault | 12.8 | 44734 | 0.46528 | 44734 | 0.65972 | 4.6667 | String Cable Faulty | 3.8588 | 0.78256 | 38.6528 | 34m tr cable Replaced
Bhadla | June | SCB5.15.1 | String fault | 12.8 | 44734 | 0.47917 | 44734 | 0.57639 | 2.3333 | Y connector burnt | 2.0519 | 0.78256 | 20.5539 | y connector replaced
Bhadla | June | Inverter 01 | RISO fault | 3451.5 | 44735 | 0.24167 | 44735 | 0.25486 | 0.31667 | Inverter Tripped in Riso Low Fault | 0.0021062 | 0.78048 | 5.6737 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 06 | RISO fault | 3450.7 | 44735 | 0.24167 | 44735 | 0.25486 | 0.31667 | Inverter Tripped in Riso Low Fault | 0.0021062 | 0.78048 | 5.6723 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 08 | RISO fault | 3444.2 | 44735 | 0.24167 | 44735 | 0.26736 | 0.61667 | Inverter Tripped in Riso Low Fault | 0.0096228 | 0.78048 | 25.8674 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | SCB8.4.10. | String fault | 12.8 | 44735 | 0.38542 | 44735 | 0.53264 | 3.5333 | Y connector burnt | 2.6669 | 0.78048 | 26.6426 | y connector replaced
Bhadla | June | SCB8.14.16.3 | String fault | 12.8 | 44735 | 0.40972 | 44735 | 0.49861 | 2.1333 | Fuse Faulty | 1.6294 | 0.78048 | 16.278 | New fuse Replaced
Bhadla | June | SCB8.13.9.6 | String fault | 12.8 | 44735 | 0.42708 | 44735 | 0.56528 | 3.3167 | Fuse Faulty | 2.8003 | 0.78048 | 27.9756 | New fuse Replaced
Bhadla | June | SCB8.11.15.9 | String fault | 12.8 | 44735 | 0.4375 | 44735 | 0.54097 | 2.4833 | Y connector burnt | 2.1065 | 0.78048 | 21.0446 | y connector replaced
Bhadla | June | SCB8.10.16.9 | String fault | 12.8 | 44735 | 0.46181 | 44735 | 0.5625 | 2.4167 | Fuse Faulty | 2.1285 | 0.78048 | 21.2643 | New fuse Replaced
Bhadla | June | Inverter 01 | Ground fault | 3451.5 | 44736 | 0.24236 | 44736 | 0.26875 | 0.63333 | Inverter Tripped in Gnd Fault | 0.013176 | 0.75674 | 34.4144 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 04 | Ground fault | 3470.2 | 44736 | 0.24236 | 44736 | 0.27361 | 0.75 | Inverter Tripped in Gnd Fault | 0.01942 | 0.75674 | 50.9965 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 05 | Ground fault | 3476 | 44736 | 0.24583 | 44736 | 0.27917 | 0.8 | Inverter Tripped in Gnd Fault | 0.028329 | 0.75674 | 74.5169 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 06 | Ground fault | 3450.7 | 44736 | 0.24236 | 44736 | 0.26806 | 0.61667 | Inverter Tripped in Gnd Fault | 0.012401 | 0.75674 | 32.3827 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 05 | Ground fault | 3476 | 44736 | 0.3 | 44736 | 0.32986 | 0.71667 | Inverter Tripped in Gnd Fault | 0.15857 | 0.75674 | 417.1161 | DC Floating Checked SCB 1A4 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB3.4 | String fault | 179.2 | 44736 | 0.3 | 44736 | 0.32986 | 0.71667 | Inverter Tripped in Gnd Fault | 0.15857 | 0.75674 | 21.5038 | ST-2 Isolated then Start the SCB
Bhadla | June | SCB3.4.2 | String fault | 12.8 | 44736 | 0.32986 | 44736 | 0.66458 | 8.0333 | Inverter Tripped in Gnd Fault | 6.0867 | 0.75674 | 58.9571 | 35 mtr Cable Faulty , string cable replaced
Bhadla | June | Inverter 10 | Ground fault | 3404.8 | 44736 | 0.24236 | 44736 | 0.29097 | 1.1667 | Inverter Tripped in Gnd Fault | 0.05589 | 0.75674 | 144.0028 | DC Floating Checked SCB 2C1 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | June | SCB5.11. | String fault | 179.2 | 44736 | 0.29097 | 44736 | 0.37222 | 1.95 | Inverter Tripped in Gnd Fault | 0.58512 | 0.75674 | 79.346 | ST-10 Isolated then Start the SCB
Bhadla | June | SCB5.11.10 | String fault | 12.8 | 44736 | 0.37222 | 44736 | 0.53125 | 3.8167 | Inverter Tripped in Gnd Fault | 3.0284 | 0.75674 | 29.3339 | 10 mtr Cable Faulty , string cable replaced
Bhadla | June | Inverter 14 | Ground fault | 3430.4 | 44736 | 0.24236 | 44736 | 0.26875 | 0.63333 | Inverter Tripped in Gnd Fault | 0.013176 | 0.75674 | 34.2041 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 15 | Ground fault | 3475.2 | 44736 | 0.24236 | 44736 | 0.29653 | 1.3 | Inverter Tripped in Gnd Fault | 0.072908 | 0.75674 | 191.7334 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 27 | Ground fault | 3404.8 | 44736 | 0.24236 | 44736 | 0.28264 | 0.96667 | Inverter Tripped in Gnd Fault | 0.035452 | 0.75674 | 91.3432 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 07 | Ground fault | 3495.8 | 44736 | 0.24236 | 44736 | 0.28611 | 1.05 | Inverter Tripped in Gnd Fault | 0.043258 | 0.75674 | 114.4353 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | June | Inverter 11 | Island protection fault | 3379.2 | 44737 | 0.26389 | 44737 | 0.28056 | 0.4 | Inverter Tripped in Island Protection Fault | 0.023591 | 0.75098 | 59.8683 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 11 | Mism Iac fault | 3379.2 | 44737 | 0.57431 | 44737 | 0.58542 | 0.26667 | Inverter Tripped in Mism-Iac Fault | 0.26285 | 0.75098 | 667.0294 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | SCB.10.10.09 | String fault | 12.8 | 44738 | 0.46528 | 44738 | 0.57639 | 2.6667 | Y connector burnt | 2.6148 | 0.7534 | 25.2158 | y connector replaced
Bhadla | June | SCB.12.11.12 | String fault | 12.8 | 44738 | 0.46875 | 44738 | 0.63889 | 4.0833 | Y connector burnt | 3.892 | 0.7534 | 37.533 | y connector replaced
Bhadla | June | SCB.12.20.14 | String fault | 12.8 | 44738 | 0.48611 | 44738 | 0.57986 | 2.25 | fuse Faulty | 2.2294 | 0.7534 | 21.499 | New fuse Replaced
Bhadla | June | SCB.13.20.02 | String fault | 12.8 | 44738 | 0.50347 | 44738 | 0.60417 | 2.4167 | Y connector burnt | 2.3738 | 0.7534 | 22.8918 | y connector replaced
Bhadla | June | SCB.14.14.14 | String fault | 12.8 | 44738 | 0.50694 | 44738 | 0.63542 | 3.0833 | Y connector burnt | 2.9454 | 0.7534 | 28.4037 | y connector replaced
Bhadla | June | Inverter 11 | Island protection fault | 3379.2 | 44738 | 0.26319 | 44738 | 0.27847 | 0.36667 | Inverter Tripped in Island Protection Fault | 0.021643 | 0.7534 | 55.1016 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | June | Inverter 18 | Ground fault | 3481.6 | 44742 | 0.24514 | 44742 | 0.26389 | 0.45 | Inverter Tripped in Gnd Fault | 0.008921 | 0.79236 | 24.6101 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44744 | 0.44931 | 44744 | 0.49028 | 0.98333 | Inverter Tripped in Riso Fault | 0.037408 | 0.83341 | 108.941 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44744 | 0.48819 | 44744 | 0.49792 | 0.23333 | Inverter Tripped in Gnd Fault | 0.013344 | 0.83341 | 38.8605 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44744 | 0.58611 | 44744 | 0.59861 | 0.3 | Inverter Tripped in Gnd Fault | 0.073499 | 0.83341 | 214.0505 | DC Floating Checked SCB 2A3,2C5 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.26.3 | String fault | 166.4 | 44744 | 0.59861 | 44744 | 0.64375 | 1.0833 | Inverter Tripped in Gnd Fault | 0.32067 | 0.83341 | 44.4703 | Again Checked found Ok.
Bhadla | July | SCB.26.15 | String fault | 179.2 | 44744 | 0.59861 | 44744 | 0.64375 | 1.0833 | Inverter Tripped in Gnd Fault | 0.32067 | 0.83341 | 47.8911 | Again Checked found Ok.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44744 | 0.50486 | 44744 | 0.55069 | 1.1 | Inverter Tripped in Gnd Fault | 0.15801 | 0.83341 | 456.7883 | DC Floating Checked SCB 1A5,1C3,1B5 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.25.10 | String fault | 166.4 | 44744 | 0.55069 | 44744 | 0.58264 | 0.76667 | Inverter Tripped in Gnd Fault | 0.69932 | 0.83341 | 96.9823 | Again Checked found Ok.
Bhadla | July | SCB.25.5 | String fault | 166.4 | 44744 | 0.55069 | 44744 | 0.58264 | 0.76667 | Inverter Tripped in Gnd Fault | 0.69932 | 0.83341 | 96.9823 | Again Checked found Ok.
Bhadla | July | SCB.25.18 | String fault | 153.6 | 44744 | 0.55069 | 44744 | 0.58264 | 0.76667 | Inverter Tripped in Gnd Fault | 0.69932 | 0.83341 | 89.5221 | Again Checked found Ok.
Bhadla | July | Inverter 28 | Ground fault | 3379.2 | 44744 | 0.55903 | 44744 | 0.57778 | 0.45 | Inverter Tripped in Gnd Fault | 0.083581 | 0.83341 | 235.3866 | DC Floating Checked SCB 2C2 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.28.12 | String fault | 166.4 | 44744 | 0.57778 | 44744 | 0.69444 | 2.8 | Inverter Tripped in Gnd Fault | 0.77964 | 0.83341 | 108.1205 | Again Checked found Ok.
Bhadla | July | Inverter 05 | RISO fault | 3476 | 44745 | 0.25069 | 44745 | 0.27292 | 0.53333 | Inverter Tripped in Riso Fault | 0.0049815 | 0.81722 | 14.1508 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44745 | 0.25069 | 44745 | 0.27639 | 0.61667 | Inverter Tripped in Gnd Fault | 0.0067862 | 0.81722 | 19.1369 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 08 | RISO fault | 3444.2 | 44745 | 0.25208 | 44745 | 0.28611 | 0.81667 | Inverter Tripped in Riso Fault | 0.013641 | 0.81722 | 38.3955 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44745 | 0.25069 | 44745 | 0.29792 | 1.1333 | Inverter Tripped in Riso Fault | 0.023019 | 0.81722 | 65.7359 | DC Floating Checked SCB 1A5,1C1 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.21.05 | String fault | 140.8 | 44745 | 0.29792 | 44745 | 0.32361 | 0.61667 | Inverter Tripped in Riso Fault | 0.049083 | 0.81722 | 5.6478 | ST-06 Isolated then Start the SCB
Bhadla | July | SCB.21.05.06 | String fault | 12.8 | 44745 | 0.32361 | 44745 | 0.4375 | 2.7333 | Y connector burnt | 0.67334 | 0.81722 | 7.0434 | Replaced y connector
Bhadla | July | SCB.21.11 | String fault | 192 | 44745 | 0.29792 | 44745 | 0.32361 | 0.61667 | Inverter Tripped in Riso Fault | 0.049083 | 0.81722 | 7.7015 | ST-10 Isolated then Start the SCB
Bhadla | July | SCB.21.11.10 | String fault | 12.8 | 44745 | 0.32361 | 44745 | 0.52778 | 4.9 | Y connector burnt | 2.028 | 0.81722 | 21.2143 | Replaced y connector
Bhadla | July | SCB.28.12.05 | String fault | 12.8 | 44745 | 0.39722 | 44745 | 0.48611 | 2.1333 | Mc4 connector burnt | 0.94204 | 0.81722 | 9.8541 | Replaced Mc4 connector
Bhadla | July | SCB.28.12.13 | String fault | 12.8 | 44745 | 0.39722 | 44745 | 0.55208 | 3.7167 | String Cable Faulty | 2.1112 | 0.81722 | 22.0844 | 12Mtr String Cable Replaced
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44745 | 0.62986 | 44745 | 0.68958 | 1.4333 | Inverter Tripped in Gnd Fault | 0.11811 | 0.81722 | 328.6323 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44745 | 0.66528 | 44745 | 0.69444 | 0.7 | Inverter Tripped in Gnd Fault | 0.10201 | 0.81722 | 287.0327 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44745 | 0.63194 | 44745 | 0.67708 | 1.0833 | Inverter Tripped in Gnd Fault | 0.072771 | 0.81722 | 206.2895 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44745 | 0.67708 | 44745 | 0.68472 | 0.18333 | Inverter Tripped in Riso Fault | 0.028179 | 0.81722 | 80.4704 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 05 | Ground fault | 3476 | 44746 | 0.27222 | 44746 | 0.28333 | 0.26667 | Inverter Tripped in Gnd Fault | 0.018837 | 0.76039 | 49.7885 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44746 | 0.24583 | 44746 | 0.27431 | 0.68333 | Inverter Tripped in Gnd Fault | 0.020566 | 0.76039 | 53.9628 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 08 | Ground fault | 3444.2 | 44746 | 0.25139 | 44746 | 0.25972 | 0.2 | Inverter Tripped in Gnd Fault | 0.0035362 | 0.76039 | 9.261 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 09 | Ground fault | 3424 | 44746 | 0.24583 | 44746 | 0.29097 | 1.0833 | Inverter Tripped in Gnd Fault | 0.050462 | 0.76039 | 131.3824 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44746 | 0.24583 | 44746 | 0.27361 | 0.66667 | Inverter Tripped in Gnd Fault | 0.019488 | 0.76039 | 50.4528 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44746 | 0.24583 | 44746 | 0.27292 | 0.65 | Inverter Tripped in Gnd Fault | 0.018433 | 0.76039 | 48.2596 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 28 | Ground fault | 3379.2 | 44746 | 0.24583 | 44746 | 0.25972 | 0.33333 | Inverter Tripped in Gnd Fault | 0.004091 | 0.76039 | 10.5119 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44746 | 0.62986 | 44746 | 0.64792 | 0.43333 | Inverter Tripped in Gnd Fault | 0.022919 | 0.76039 | 59.336 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 07 | Ground fault | 3495.8 | 44746 | 0.62361 | 44746 | 0.67986 | 1.35 | Inverter Tripped in Gnd Fault | 0.13621 | 0.76039 | 362.0608 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44746 | 0.63333 | 44746 | 0.68542 | 1.25 | Inverter Tripped in Gnd Fault | 0.16109 | 0.76039 | 413.9188 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44746 | 0.66597 | 44746 | 0.71736 | 1.2333 | Inverter Tripped in Gnd Fault | 0.22514 | 0.76039 | 589.4566 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 14 | Ground fault | 3430.4 | 44746 | 0.66111 | 44746 | 0.69028 | 0.7 | Inverter Tripped in Gnd Fault | 0.1289 | 0.76039 | 336.2286 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44746 | 0.62431 | 44746 | 0.69028 | 1.5833 | Inverter Tripped in Gnd Fault | 0.21797 | 0.76039 | 574.9286 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 28 | Ground fault | 3379.2 | 44746 | 0.69375 | 44746 | 0.7125 | 0.45 | Inverter Tripped in Gnd Fault | 0.077614 | 0.76039 | 199.4313 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44746 | 0.72083 | 44746 | 0.73611 | 0.36667 | Inverter Tripped in Gnd Fault | 0.11601 | 0.76039 | 299.2205 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44746 | 0.73264 | 44746 | 0.74583 | 0.31667 | Inverter Tripped in Gnd Fault | 0.087498 | 0.76039 | 230.7894 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44746 | 0.74236 | 44746 | 0.76389 | 0.51667 | Inverter Tripped in Gnd Fault | 0.13093 | 0.76039 | 342.806 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44746 | 0.68958 | 44746 | 0.71736 | 0.66667 | Inverter Tripped in Gnd Fault | 0.11743 | 0.76039 | 304.0122 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 26 | Island protection fault | 3494.4 | 44746 | 0.25417 | 44746 | 0.31667 | 1.5 | Inverter Tripped in Island Protection Fault | 0.11854 | 0.76039 | 314.9801 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | July | Inverter 26 | Island protection fault | 3494.4 | 44746 | 0.66736 | 44746 | 0.78542 | 2.8333 | Inverter Tripped in Island Protection Fault | 0.54485 | 0.76039 | 1447.7361 | Discussed with SG Team as per their instructions then Restart the Inv.
Bhadla | July | Inverter 26 | Island protection fault | 857.6 | 44746 | 0.31667 | 44746 | 0.8125 | 11.9 | Unit-04 Tripped in Island Protection Fault | 4.5399 | 0.76039 | 2960.4947 | Again Discussed with SG Team as per their instructions Unit-04 Q1 Off Keeping OFF then Restart the Inv.
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44746 | 0.24583 | 44746 | 0.27431 | 0.68333 | Inverter Tripped in Gnd Fault | 0.020566 | 0.76039 | 54.6462 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 05 | Ground fault | 3476 | 44747 | 0.25139 | 44747 | 0.27639 | 0.6 | Inverter Tripped in Gnd Fault | 0.01797 | 0.77526 | 48.4261 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44747 | 0.24583 | 44747 | 0.27014 | 0.58333 | Inverter Tripped in Gnd Fault | 0.011111 | 0.77526 | 29.7231 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 14 | Ground fault | 3430.4 | 44747 | 0.24583 | 44747 | 0.28681 | 0.98333 | Inverter Tripped in Gnd Fault | 0.039796 | 0.77526 | 105.8369 | DC Floating Checked SCB 2D1,2B2 found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.14.16. | String fault | 166.4 | 44747 | 0.28681 | 44747 | 0.35208 | 1.5667 | Inverter Tripped in Gnd Fault | 0.38952 | 0.77526 | 50.2488 | ST-10 Isolated then Start the SCB
Bhadla | July | SCB.14.16.10 | String fault | 12.8 | 44747 | 0.35208 | 44747 | 0.48958 | 3.3 | Y connector burnt | 2.277 | 0.77526 | 22.5958 | y connector replaced
Bhadla | July | SCB.14.07 | String fault | 166.4 | 44747 | 0.28681 | 44747 | 0.35208 | 1.5667 | Inverter Tripped in Gnd Fault | 0.38952 | 0.77526 | 50.2488 | ST-05 Isolated then Start the SCB
Bhadla | July | SCB.14.07.05 | String fault | 12.8 | 44747 | 0.35208 | 44747 | 0.59028 | 5.7167 | Y connector burnt | 4.1755 | 0.77526 | 41.4348 | y connector replaced
Bhadla | July | Inverter 28 | Leakage current fault | 3379.2 | 44747 | 0.36736 | 44747 | 0.37847 | 0.26667 | Inverter Tripped in Leakage Current Fault | 0.13312 | 0.77526 | 348.7427 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 28 | Leakage current fault | 3379.2 | 44747 | 0.46736 | 44747 | 0.48056 | 0.31667 | Inverter Tripped in Leakage Current Fault | 0.25776 | 0.77526 | 675.2625 | DC Floating Checked SCB 2D2found Abnormal , keeping SCB off then Start the Inv.
Bhadla | July | SCB.28.17 | String fault | 179.2 | 44747 | 0.48056 | 44747 | 0.50833 | 0.66667 | Inverter Tripped in Leakage Current Fault | 0.54505 | 0.77526 | 75.7214 | ST-10 Isolated then Start the SCB
Bhadla | July | SCB.28.17.10 | String fault | 12.8 | 44747 | 0.50833 | 44747 | 0.58056 | 1.7333 | Y connector burnt | 1.3594 | 0.77526 | 13.4897 | y connector replaced
Bhadla | July | SCB.14.08.04 | String fault | 12.8 | 44747 | 0.38542 | 44747 | 0.65625 | 6.5 | Y connector burnt | 5.0051 | 0.77526 | 49.6668 | y connector replaced
Bhadla | July | Inverter 16 | Ground fault | 3411.2 | 44747 | 0.24583 | 44747 | 0.26042 | 0.35 | Inverter Tripped in Gnd Fault | 0.0045253 | 0.77526 | 11.9675 | Dc Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | Inverter 02 | Ground fault | 3469.9 | 44748 | 0.24653 | 44748 | 0.27708 | 0.73333 | Inverter Tripped in Gnd Fault | 0.018395 | 0.77256 | 49.3119 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2B1 & 2C3 keeping those SCB off then start the Inv.
Bhadla | July | SCB.02.06 | String fault | 185.6 | 44748 | 0.27708 | 44748 | 0.38333 | 2.55 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.70901 | 0.77256 | 101.6621 | St-6 Isolated then Start the SCB
Bhadla | July | SCB.02.06 | String fault | 12.8 | 44748 | 0.38333 | 44748 | 0.51875 | 3.25 | ST-6 found Abnormal Floating | 2.6034 | 0.77256 | 25.7443 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | July | SCB.02.13 | String fault | 166.4 | 44748 | 0.27708 | 44748 | 0.35139 | 1.7833 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.35613 | 0.77256 | 45.7814 | Again checked found Ok.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44748 | 0.24653 | 44748 | 0.28264 | 0.86667 | Inverter Tripped in Gnd Fault | 0.026499 | 0.77256 | 70.6437 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2B1 & 2D4 keeping those SCB off then start the Inv.
Bhadla | July | SCB.06.06 | String fault | 166.4 | 44748 | 0.28264 | 44748 | 0.34792 | 1.5667 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.31839 | 0.77256 | 40.9304 | Again checked found Ok.
Bhadla | July | SCB.06.19 | String fault | 166.4 | 44748 | 0.28264 | 44748 | 0.34792 | 1.5667 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.31839 | 0.77256 | 40.9304 | Again checked found Ok.
Bhadla | July | Inverter 08 | Ground fault | 3444.2 | 44748 | 0.24653 | 44748 | 0.28958 | 1.0333 | Inverter Tripped in Gnd Fault | 0.042214 | 0.77256 | 112.3249 | 10Amp fuse found faulty same replacement done & DC Floating nothing found abnormal, Then start the Inv.
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44748 | 0.24653 | 44748 | 0.29583 | 1.1833 | Inverter Tripped in Gnd Fault | 0.059394 | 0.77256 | 156.2303 | 10Amp fuse found faulty same replacement done &DC Floating Checked fault found in 2A5, 2B2, 2B3, 2D3 & 2D5 keeping those SCB off then start the Inv.
Bhadla | July | SCB.10.05 | String fault | 179.2 | 44748 | 0.29583 | 44748 | 0.38889 | 2.2333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.74294 | 0.77256 | 102.8539 | St-11 Isolated then Start the SCB.
Bhadla | July | SCB.10.05 | String fault | 12.8 | 44748 | 0.38889 | 44748 | 0.53819 | 3.5833 | ST-11 found Abnormal Floating | 2.97 | 0.77256 | 29.3699 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | July | SCB.10.07 | String fault | 179.2 | 44748 | 0.29583 | 44748 | 0.39722 | 2.4333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.86352 | 0.77256 | 119.548 | Again checked found Ok.
Bhadla | July | SCB.10.08 | String fault | 166.4 | 44748 | 0.29583 | 44748 | 0.39722 | 2.4333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.86352 | 0.77256 | 111.0089 | St-6 Isolated then Start the SCB.
Bhadla | July | SCB.10.08 | String fault | 12.8 | 44748 | 0.39722 | 44748 | 0.63889 | 5.8 | ST-6 found Abnormal Floating | 4.924 | 0.77256 | 48.6924 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | July | SCB.10.18 | String fault | 179.2 | 44748 | 0.29583 | 44748 | 0.34583 | 1.2 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.26866 | 0.77256 | 37.1945 | Again checked found Ok.
Bhadla | July | SCB.10.20 | String fault | 166.4 | 44748 | 0.29583 | 44748 | 0.38889 | 2.2333 | Manually Stopped as found Abnormal Floating During INV Gnd Fault attend | 0.745 | 0.77256 | 95.7724 | Again checked found Ok.
Bhadla | July | Inverter 11 | Mism Iac fault | 3379.2 | 44748 | 0.24653 | 44748 | 0.35208 | 2.5333 | Inverter Tripped in Mism-Iac Fault. | 0.38004 | 0.77256 | 992.1384 | Discussed with SG Team to restart the Inverter after DC floating checked thenFault found in 1A1 & 1B3 Keeping those SCB off Then Start the Inv.
Bhadla | July | SCB.11.01 | String fault | 166.4 | 44748 | 0.35208 | 44748 | 0.40208 | 1.2 | Manually Stopped as found Abnormal Floating During INV Mism I-ac fault attend | 0.61273 | 0.77256 | 78.7683 | Again checked found Ok.
Bhadla | July | SCB.11.08 | String fault | 179.2 | 44748 | 0.35208 | 44748 | 0.40208 | 1.2 | Manually Stopped as found Abnormal Floating During INV Mism I-ac fault attend | 0.61273 | 0.77256 | 84.8274 | Again checked found Ok.
Bhadla | July | Inverter 11 | Mism Iac fault | 3379.2 | 44748 | 0.42014 | 44748 | 0.43819 | 0.43333 | Again Inverter Tripped in Mism-Iac Fault. | 0.33458 | 0.77256 | 873.4519 | Again Discussed with SG Team to restart the Inverter after DC floating checked thenFault found in 1B3 Keeping that SCB off Then Start the Inv.
Bhadla | July | SCB.11.08 | String fault | 12.8 | 44748 | 0.40208 | 44748 | 0.64583 | 5.85 | ST-5 found Abnormal Floating | 4.9852 | 0.77256 | 49.2974 | Found (-ve) String Cable 16Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | SCB.11.08 | String fault | 12.8 | 44748 | 0.40208 | 44748 | 0.60417 | 4.85 | ST-7 found Abnormal Floating | 4.1871 | 0.77256 | 41.4052 | Found (-ve) String Cable 24Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44748 | 0.24653 | 44748 | 0.30139 | 1.3167 | Inverter Tripped in Gnd Fault. | 0.077404 | 0.77256 | 205.9007 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2B3, 2D1 & 2D2 keeping those SCB off then start the Inv.
Bhadla | July | SCB.12.08 | String fault | 166.4 | 44748 | 0.30139 | 44748 | 0.40069 | 2.3833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.89469 | 0.77256 | 115.0158 | Again Checked found ok.
Bhadla | July | SCB.12.16 | String fault | 166.4 | 44748 | 0.30139 | 44748 | 0.40069 | 2.3833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.89469 | 0.77256 | 115.0158 | Again Checked found ok.
Bhadla | July | SCB.12.17 | String fault | 166.4 | 44748 | 0.30139 | 44748 | 0.40069 | 2.3833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.89469 | 0.77256 | 115.0158 | Again Checked found ok.
Bhadla | July | Inverter 13 | Ground fault | 3411.2 | 44748 | 0.24653 | 44748 | 0.31111 | 1.55 | Inverter Tripped in Gnd Fault | 0.11417 | 0.77256 | 300.8674 | Dc Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44748 | 0.24653 | 44748 | 0.32569 | 1.9 | Inverter Tripped in Gnd Fault | 0.18692 | 0.77256 | 489.8249 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2B1 & 2D3 keeping those SCB off then start the Inv.
Bhadla | July | SCB.24.06 | String fault | 166.4 | 44748 | 0.32569 | 44748 | 0.37292 | 1.1333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.41444 | 0.77256 | 53.2774 | Again checked found Ok.
Bhadla | July | SCB.24.18 | String fault | 166.4 | 44748 | 0.32569 | 44748 | 0.37292 | 1.1333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.41444 | 0.77256 | 53.2774 | Again checked found Ok.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44748 | 0.45764 | 44748 | 0.47153 | 0.33333 | Inverter Tripped in Gnd Fault. | 0.30059 | 0.77256 | 805.5355 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 1B4 & 1C2 keeping those SCB off then start the Inv.
Bhadla | July | SCB.25.09 | String fault | 166.4 | 44748 | 0.47153 | 44748 | 0.48889 | 0.41667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38873 | 0.77256 | 49.9729 | ST-9 Isolated then Start the SCB
Bhadla | July | SCB.25.09 | String fault | 12.8 | 44748 | 0.48889 | 44748 | 0.67014 | 4.35 | ST-9 found Abnormal Floating | 3.7316 | 0.77256 | 36.9008 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | July | SCB.25.12 | String fault | 166.4 | 44748 | 0.47153 | 44748 | 0.48889 | 0.41667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38873 | 0.77256 | 49.9729 | ST-3 Isolated then start the SCB
Bhadla | July | SCB.25.12 | String fault | 12.8 | 44748 | 0.48889 | 44748 | 0.65972 | 4.1 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 3.55 | 0.77256 | 35.1046 | Found (-ve) Y connector burnt, Replaced New Y connector
Bhadla | July | Inverter 26 | Island protection fault | 3494.4 | 44748 | 0.525 | 44748 | 0.53889 | 0.33333 | Inverter Tripped in Island Protection fault. | 0.33885 | 0.77256 | 914.7763 | Discussed with SG Service Person as per their instructions to restart the Inv.
Bhadla | July | Inverter 27 | Ground fault | 3404.8 | 44748 | 0.24653 | 44748 | 0.31806 | 1.7167 | Inverter Tripped in Gnd Fault. | 0.14638 | 0.77256 | 385.0265 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 1A3 & 1B1 keeping those SCB off then start the Inv.
Bhadla | July | SCB.27.03 | String fault | 166.4 | 44748 | 0.31806 | 44748 | 0.37639 | 1.4 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.49647 | 0.77256 | 63.8228 | Again checked found Ok.
Bhadla | July | SCB.27.06 | String fault | 140.8 | 44748 | 0.31806 | 44748 | 0.37639 | 1.4 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.49647 | 0.77256 | 54.0039 | Again checked found Ok.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44749 | 0.24931 | 44749 | 0.29583 | 1.1167 | Inverter Tripped in Gnd Fault. | 0.031445 | 0.76567 | 83.0808 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2C3 & 2C4 keeping those SCB off then start the Inv.
Bhadla | July | SCB.06.13 | String fault | 192 | 44749 | 0.29583 | 44749 | 0.35278 | 1.3667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.20433 | 0.76567 | 30.0376 | Again Checked found Ok.
Bhadla | July | SCB.06.14 | String fault | 179.2 | 44749 | 0.29583 | 44749 | 0.35278 | 1.3667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.20433 | 0.76567 | 28.0351 | St-6 Isolated then Start the SCB.
Bhadla | July | SCB.06.14 | String fault | 12.8 | 44749 | 0.35278 | 44749 | 0.57639 | 5.3667 | ST-6 found Abnormal Floating | 3.5043 | 0.76567 | 34.3443 | Found (-ve) String Cable 24Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | SCB.06.14 | String fault | 12.8 | 44749 | 0.35278 | 44749 | 0.64583 | 7.0333 | ST-7 found Abnormal Floating | 4.4059 | 0.76567 | 43.18 | Found (-ve) String Cable 36Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | SCB.06.14 | String fault | 12.8 | 44749 | 0.35278 | 44749 | 0.68056 | 7.8667 | ST-12 found Abnormal Floating | 4.836 | 0.76567 | 47.3951 | Found (+ve) Y connector burnt, Replaced New Y connector
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44749 | 0.24931 | 44749 | 0.28958 | 0.96667 | Inverter Tripped in Gnd Fault. | 0.022467 | 0.76567 | 58.5706 | 10Amp fuse found faulty same replacement done & DC Floating nothing found abnormal, Then start the Inv.
Bhadla | July | Inverter 11 | Mism Iac fault | 3379.2 | 44749 | 0.28264 | 44749 | 0.34236 | 1.4333 | Inverter Tripped in Mism I-Ac Fault. | 0.16517 | 0.76567 | 427.36 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 1A1 keeping those SCB off then start the Inv.
Bhadla | July | SCB.11.01 | String fault | 166.4 | 44749 | 0.34236 | 44749 | 0.425 | 1.9833 | Manually Stopped as found Abnormal Floating During Mism Iac fault attend | 0.86253 | 0.76567 | 109.8922 | Again Checked found Ok.
Bhadla | July | Inverter 11 | Mism Iac fault | 843.2 | 44749 | 0.44792 | 44749 | 0.81597 | 8.8333 | Unit-01 Tripped in Mism ac Fault | 4.1638 | 0.76567 | 2688.1981 | Discussed with SG team as per their instructions to interchange Master & Slave between Unit-01 & Unit-02 & Keeping Unit-01 Q-1 Off. After generation SG Team replaced 2 nos of IGBT in that Unit.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44749 | 0.24931 | 44749 | 0.81597 | 13.6 | Inverter Tripped in Gnd Fault | 3.5041 | 0.76567 | 10492 | Dc Floating Checked and found that some burning smell and some smoke inside in Unit-1.thats why we kept whole Inverter Off. After generation hour SG Team checked whole inverter but nothing found any abnormal.
Bhadla | July | Inverter 25 | RISO fault | 3468.8 | 44749 | 0.24931 | 44749 | 0.26181 | 0.3 | Inverter Tripped in Riso Fault | 0.0025068 | 0.76567 | 6.658 | Auto-Restarted
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44749 | 0.30625 | 44749 | 0.32153 | 0.36667 | Inverter Tripped in Riso Fault | 0.044636 | 0.76567 | 119.4252 | Dc floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 03 | Ground fault | 3450.4 | 44750 | 0.24583 | 44750 | 0.27014 | 0.58333 | Inverter Tripped in Gnd Fault | 0.010889 | 0.7598 | 28.5459 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 1B2 & 1B5 keeping those SCB off then start the Inv.
Bhadla | July | SCB.03.07 | String fault | 166.4 | 44750 | 0.27014 | 44750 | 0.44514 | 4.2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.8141 | 0.7598 | 229.3615 | Again Checked found Ok
Bhadla | July | SCB.03.10 | String fault | 166.4 | 44750 | 0.27014 | 44750 | 0.44514 | 4.2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.8141 | 0.7598 | 229.3615 | Again Checked found Ok
Bhadla | July | Inverter 05 | Ground fault | 3476 | 44750 | 0.24583 | 44750 | 0.37014 | 2.9833 | Inverter Tripped in Gnd Fault | 0.61372 | 0.7598 | 1620.8866 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found keeping those SCB off then start the Inv.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44750 | 0.27153 | 44750 | 0.29792 | 0.63333 | Inverter Tripped in Gnd Fault | 0.056377 | 0.7598 | 147.8124 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found in 2C4 & 2D2 keeping those SCB off then start the Inv.
Bhadla | July | SCB.06.14 | String fault | 179.2 | 44750 | 0.29792 | 44750 | 0.44722 | 3.5833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.8005 | 0.7598 | 245.1499 | Again checked found ok
Bhadla | July | SCB.06.17 | String fault | 166.4 | 44750 | 0.29792 | 44750 | 0.45764 | 3.8333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 2.0108 | 0.7598 | 254.2282 | ST-5 Isolated then Start the SCB
Bhadla | July | SCB.06.17 | String fault | 12.8 | 44750 | 0.45764 | 44750 | 0.60417 | 3.5167 | St-5 found abnormal Floating | 3.2181 | 0.7598 | 31.2975 | Found (-ve) String Cable 36Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | Inverter 08 | Ground fault | 3444.2 | 44750 | 0.34167 | 44750 | 0.42222 | 1.9333 | Inverter Tripped in Gnd Fault | 1.079 | 0.7598 | 2823.7242 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found keeping those SCB off then start the Inv.
Bhadla | July | SCB.08.17 | String fault | 12.8 | 44750 | 0.42222 | 44750 | 0.65278 | 5.5333 | St-9 found abnormal Floating | 4.7875 | 0.7598 | 46.5609 | Found (-ve) String Cable 40Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | SCB.08.05 | String fault | 12.8 | 44750 | 0.42222 | 44750 | 0.68056 | 6.2 | St-2 found abnormal Floating | 4.9913 | 0.7598 | 48.5426 | Found both (+ve) & (-ve) String Cable 80Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44750 | 0.24583 | 44750 | 0.28333 | 0.9 | Inverter Tripped in Gnd Fault | 0.030143 | 0.7598 | 77.9789 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found keeping mentioned SCB off then start the Inv.
Bhadla | July | SCB.10.04 | String fault | 166.4 | 44750 | 0.28333 | 44750 | 0.32014 | 0.88333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.13922 | 0.7598 | 17.6018 | Again checked found ok
Bhadla | July | SCB.10.05 | String fault | 179.2 | 44750 | 0.28333 | 44750 | 0.32014 | 0.88333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.13922 | 0.7598 | 18.9558 | Again checked found ok
Bhadla | July | SCB.10.08 | String fault | 166.4 | 44750 | 0.28333 | 44750 | 0.43472 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5963 | 0.7598 | 201.8253 | St-1 isolated then Start the SCB
Bhadla | July | SCB.10.08 | String fault | 12.8 | 44750 | 0.43472 | 44750 | 0.65625 | 5.3167 | St-1 found abnormal floating | 4.6101 | 0.7598 | 44.835 | Found +ve Y-connector & MC4 Connector Damage same replaced with new one.
Bhadla | July | SCB.10.09 | String fault | 166.4 | 44750 | 0.28333 | 44750 | 0.42431 | 3.3833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.4055 | 0.7598 | 177.6959 | Again checked found ok
Bhadla | July | SCB.10.17 | String fault | 166.4 | 44750 | 0.28333 | 44750 | 0.43472 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5963 | 0.7598 | 201.8253 | Again checked found ok
Bhadla | July | SCB.10.18 | String fault | 179.2 | 44750 | 0.28333 | 44750 | 0.43472 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5963 | 0.7598 | 217.3503 | Again checked found ok
Bhadla | July | SCB.10.19 | String fault | 153.6 | 44750 | 0.28333 | 44750 | 0.43472 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5963 | 0.7598 | 186.3002 | Again checked found ok
Bhadla | July | SCB.10.20 | String fault | 166.4 | 44750 | 0.28333 | 44750 | 0.43472 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5963 | 0.7598 | 201.8253 | St-4 Isolated then Start the SCB
Bhadla | July | SCB.10.20 | String fault | 12.8 | 44750 | 0.43472 | 44750 | 0.64583 | 5.0667 | ST-4 found Abnormal Floating | 4.4757 | 0.7598 | 43.5282 | Found (-ve) String Cable 16Mtr Faulty And 2set Mc4 connector Replaced
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44750 | 0.29792 | 44750 | 0.31736 | 0.46667 | Inverter Tripped in Gnd Fault | 0.086723 | 0.7598 | 222.6639 | Dc Floating Checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 13 | Ground fault | 3411.2 | 44750 | 0.24583 | 44750 | 0.28958 | 1.05 | Inverter Tripped in Gnd Fault | 0.044229 | 0.7598 | 114.6336 | Dc Floating Checked fault found in 1D2 off the SCB then start the Inv.
Bhadla | July | SCB.13.17 | String fault | 166.4 | 44750 | 0.28958 | 44750 | 0.45556 | 3.9833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.9898 | 0.7598 | 251.5748 | Again checked found ok
Bhadla | July | SCB.24.01 | String fault | 179.2 | 44750 | 0.24583 | 44750 | 0.34792 | 2.45 | DC Breaker Manually Stopped | 0.3774 | 0.7598 | 51.385 | will start after Floating checked.
Bhadla | July | SCB.24.02 | String fault | 166.4 | 44750 | 0.24583 | 44750 | 0.34792 | 2.45 | DC Breaker Manually Stopped | 0.3774 | 0.7598 | 47.7146 | will start after Floating checked.
Bhadla | July | SCB.24.03 | String fault | 166.4 | 44750 | 0.24583 | 44750 | 0.34792 | 2.45 | DC Breaker Manually Stopped | 0.3774 | 0.7598 | 47.7146 | will start after Floating checked.
Bhadla | July | SCB.24.04 | String fault | 166.4 | 44750 | 0.24583 | 44750 | 0.34792 | 2.45 | DC Breaker Manually Stopped | 0.3774 | 0.7598 | 47.7146 | will start after Floating checked.
Bhadla | July | SCB.24.05 | String fault | 166.4 | 44750 | 0.24583 | 44750 | 0.34792 | 2.45 | DC Breaker Manually Stopped | 0.3774 | 0.7598 | 47.7146 | will start after Floating checked.
Bhadla | July | SCB.24.01 | String fault | 179.2 | 44750 | 0.34861 | 44750 | 0.81458 | 11.1833 | DC Breaker Manually Stopped | 6.4424 | 0.7598 | 877.1728 | when we went to start those SCB's found some burning ashes in that Unit. So for safety purpose we manually Off 2A1 SCB. After Generation hour SG Team replaced one DC MCCB in 1A1
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44750 | 0.31597 | 44750 | 0.33194 | 0.38333 | Inverter Tripped in Gnd Fault | 0.10493 | 0.7598 | 278.5907 | 10Amp fuse found faulty same replacement done & DC Floating Checked fault found keeping mentioned SCB off then start the Inv.
Bhadla | July | SCB.26.08 | String fault | 166.4 | 44750 | 0.33194 | 44750 | 0.45139 | 2.8667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.7083 | 0.7598 | 215.9839 | Again checked found ok
Bhadla | July | SCB.26.09 | String fault | 166.4 | 44750 | 0.33194 | 44750 | 0.45139 | 2.8667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.7083 | 0.7598 | 215.9839 | Again checked found ok
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44750 | 0.33194 | 44750 | 0.45139 | 2.8667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.7083 | 0.7598 | 215.9839 | Again checked found ok
Bhadla | July | SCB.26.11 | String fault | 204.8 | 44750 | 0.33194 | 44750 | 0.45139 | 2.8667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.7083 | 0.7598 | 265.8263 | Again checked found ok
Bhadla | July | Inverter 01 | Ground fault | 3451.5 | 44751 | 0.24861 | 44751 | 0.27569 | 0.65 | Inverter Tripped in Gnd Fault | 0.018449 | 0.77994 | 49.6649 | Dc Floating Checked fault found in 1C1 off the SCB then start the Inv.
Bhadla | July | SCB.01.11 | String fault | 192 | 44751 | 0.27569 | 44751 | 0.34792 | 1.7333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.35023 | 0.77994 | 52.4469 | Again Checked found Ok.
Bhadla | July | Inverter 04 | Ground fault | 3470.2 | 44751 | 0.24861 | 44751 | 0.26111 | 0.3 | Inverter Tripped in Gnd Fault | 0.0037428 | 0.77994 | 10.1302 | Auto-Restarted
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44751 | 0.24861 | 44751 | 0.28194 | 0.8 | Inverter Tripped in Gnd Fault | 0.029304 | 0.77994 | 77.8179 | DC Floating nothing found abnormal, Then start the Inv.
Bhadla | July | Inverter 17 | Ground fault | 3404.8 | 44751 | 0.24861 | 44751 | 0.28819 | 0.95 | Inverter Tripped in Gnd Fault | 0.042675 | 0.77994 | 113.3251 | Dc Floating Checked fault found in 1A4 & 1D1 off the SCB then start the Inv.
Bhadla | July | SCB.17.04 | String fault | 166.4 | 44751 | 0.28819 | 44751 | 0.39306 | 2.5167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.85181 | 0.77994 | 110.5495 | Again checked found ok.
Bhadla | July | SCB.17.16 | String fault | 166.4 | 44751 | 0.28819 | 44751 | 0.39306 | 2.5167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.85181 | 0.77994 | 110.5495 | St-12 Isolated then Start the SCB
Bhadla | July | SCB.17.16 | String fault | 12.8 | 44751 | 0.39306 | 44751 | 0.52778 | 3.2333 | ST-12 found Abnormal Floating | 2.4438 | 0.77994 | 24.397 | Both (+ve) & (-Ve) Cable found Faulty. Same Replaced with 30 mtr Cable & 2 set MC4 Connector
Bhadla | July | Inverter 27 | Ground fault | 3404.8 | 44751 | 0.24861 | 44751 | 0.29375 | 1.0833 | Inverter Tripped in Gnd Fault | 0.057015 | 0.77994 | 151.4047 | Dc Floating Checked fault found in 1D4 off the SCB then start the Inv.
Bhadla | July | SCB.27.19 | String fault | 179.2 | 44751 | 0.29375 | 44751 | 0.40694 | 2.7167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.0316 | 0.77994 | 144.1835 | St-14 Isolated then Start the SCB
Bhadla | July | SCB.27.19 | String fault | 12.8 | 44751 | 0.40694 | 44751 | 0.60417 | 4.7333 | ST-14 found Abnormal Floating | 3.6887 | 0.77994 | 36.825 | (-Ve) Cable found Faulty. Same Replaced with 40 mtr Cable & 2 set MC4 Connector
Bhadla | July | SCB.24.01 | String fault | 166.4 | 44751 | 0.24861 | 44751 | 0.29792 | 1.1833 | DC Breaker Manually Stopped | 0.069316 | 0.77994 | 8.996 | Last night SG Team replaced DC Breaker & wii start after Floating checked.
Bhadla | July | Inverter 22 | Island protection fault | 857.6 | 44751 | 0.47014 | 44751 | 0.49167 | 0.51667 | Unit-04 Tripped in Island Protection Fault | 0.27669 | 0.77994 | 654 | Discussed with SG Team to restart the Inv.
Bhadla | July | Inverter 22 | Island protection fault | 857.6 | 44751 | 0.58472 | 44751 | 0.59514 | 0.25 | Again Unit-04 Tripped in Island Protection Fault | 0.093947 | 0.77994 | 205 | Again Discussed with SG Team to restart the Inv.
Bhadla | July | Inverter-1,2,3,6,7,9,10,12,14,16,17,20,22,24,25 & 28 | Grid voltage issue | 55052.9 | 44751 | 0.57153 | 44751 | 0.57361 | 0.05 | Inverter-1,2,3,6,7,9,10,12,14,16,17,20,22,24,25 & 28 Tripped due to due to Under voltage in Line. | 0.05068 | 0.77994 | 2176.0741 | Inverters resumes after Grid voltage normalised.
Bhadla | July | Inverter 18 | RISO fault | 3481.6 | 44752 | 0.24931 | 44752 | 0.26181 | 0.3 | Inverter Tripped in Riso Low Fault | 0.003111 | 0.80117 | 8.6777 | DC Floating Checked nothing found abnormal then start the Inverter.
Bhadla | July | Inverter 22 | Island protection fault | 857.6 | 44752 | 0.55278 | 44752 | 0.56806 | 0.36667 | Unit-04 Tripped in Island Protection Fault | 0.29424 | 0.80117 | 404 | Discussed with SG Team to restart the Inv.
Bhadla | July | Inverter 07 | RISO fault | 3495.8 | 44753 | 0.24653 | 44753 | 0.28333 | 0.88333 | Inverter Tripped in Riso Low Fault | 0.040168 | 0.78385 | 110.0682 | Dc Floating Checked fault found in 1B1 & 1C5 off the SCB then start the Inv.
Bhadla | July | SCB.07.06 | String fault | 179.2 | 44753 | 0.28333 | 44753 | 0.32708 | 1.05 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.20093 | 0.78385 | 28.2234 | ST-7 Isolated then start the SCB
Bhadla | July | SCB.07.06 | String fault | 12.8 | 44753 | 0.32708 | 44753 | 0.46875 | 3.4 | ST-7 found Abnormal Floating | 1.9659 | 0.78385 | 19.724 | Found Cut mark on purlin 1 set of MC4 Connector replaced.
Bhadla | July | SCB.07.15 | String fault | 192 | 44753 | 0.28333 | 44753 | 0.32708 | 1.05 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.20093 | 0.78385 | 30.2394 | Again Checked found Ok.
Bhadla | July | Inverter 16 | RISO fault | 3411.2 | 44753 | 0.24653 | 44753 | 0.28889 | 1.0167 | Inverter Tripped in Riso Low Fault | 0.057806 | 0.78385 | 154.5654 | Dc Floating Checked fault found in 2A3 off the SCB then start the Inv.
Bhadla | July | SCB.16.03 | String fault | 166.4 | 44753 | 0.28889 | 44753 | 0.30069 | 0.28333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.046808 | 0.78385 | 6.1053 | Again checked found ok.
Bhadla | July | Inverter 22 | Island protection fault | 857.6 | 44753 | 0.43403 | 44753 | 0.44167 | 0.18333 | Unit-04 Tripped in Island Protection Fault | 0.1052 | 0.78385 | 218 | Discussed with SG Team to restart the Inv.
Bhadla | July | SCB.07.03 | String fault | 12.8 | 44753 | 0.24653 | 44753 | 0.60417 | 8.5833 | St-3 Found Faulty during Suspected SCB Check. | 4.2923 | 0.78385 | 43.0661 | (-Ve) Y-connector Replaced with new One.
Bhadla | July | SCB.08.06 | String fault | 12.8 | 44753 | 0.24653 | 44753 | 0.65972 | 9.9167 | St-3 Found Faulty during Suspected SCB Check. | 4.6218 | 0.78385 | 46.3722 | 30A Fuse found faulty same replaced with new one.
Bhadla | July | Inverter 15 | RISO fault | 3475.2 | 44754 | 0.24792 | 44754 | 0.28194 | 0.81667 | Inverter Tripped in riso fault | 0.025112 | 0.77286 | 67.4483 | DC Floating fault found in 1A5 & 1B2 keeping those SCB Off then start the Inv.
Bhadla | July | SCB.15.05 | String fault | 166.4 | 44754 | 0.28194 | 44754 | 0.3 | 0.43333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.046647 | 0.77286 | 5.999 | St-01 Isolated then start the SCB.
Bhadla | July | SCB.15.05 | String fault | 12.8 | 44754 | 0.3 | 44754 | 0.43056 | 3.1333 | ST-01 found abnormal floating | 1.4234 | 0.77286 | 14.0813 | Again checked found ok.
Bhadla | July | SCB.15.07 | String fault | 192 | 44754 | 0.28194 | 44754 | 0.3 | 0.43333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.046647 | 0.77286 | 6.9219 | St-8 & 10 Isolated then start the SCB.
Bhadla | July | SCB.15.07 | String fault | 12.8 | 44754 | 0.3 | 44754 | 0.48264 | 4.3833 | ST-8 found abnormal floating | 2.4323 | 0.77286 | 24.062 | (-Ve) Cable found Faulty. Same Replaced with 15 mtr Cable & 2 set MC4 Connector
Bhadla | July | SCB.15.07 | String fault | 12.8 | 44754 | 0.3 | 44754 | 0.49375 | 4.65 | ST-10 found abnormal floating | 2.6081 | 0.77286 | 25.801 | (-Ve) Cable found Faulty. Same Replaced with 22 mtr Cable & 2 set MC4 Connector
Bhadla | July | SCB.25.09 | String fault | 12.8 | 44755 | 0.24653 | 44755 | 0.47917 | 5.5833 | St-7 Found Faulty during Suspected SCB Check. | 2.4479 | 0.77267 | 24.2101 | (+VE) Y-Connector Found Faulty. Same Replaced with new One.
Bhadla | July | Inverter-2,3,4,5,7,9,10,11,12,13,15,16,17,18,22,23,24,25,26,27 & 28 | Grid voltage issue | 72261.5 | 44756 | 0.76319 | 44756 | 0.76458 | 0.033333 | Inverter-2,3,4,5,7,9,10,11,12,13,15,16,17,18,22,23,24,25,26,27 & 28 Tripped due to due to Under voltage in Line. | 0.0064657 | 0.78396 | 366.2812 | Inverters resumes after Grid voltage normalised.
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44756 | 0.25556 | 44756 | 0.26944 | 0.33333 | Inverter Tripped in Riso Fault | 0.0058573 | 0.78396 | 15.849 | Auto-Restarted
Bhadla | July | Inverter 05 | Ground fault | 3476 | 44756 | 0.67569 | 44756 | 0.68403 | 0.2 | Inverter Tripped in Gnd Fault | 0.043389 | 0.78396 | 118.2357 | 10Amp fuse found faulty same replaced. Dc floating checked nothing found abnormal then start the SCB.
Bhadla | July | Inverter 06 | RISO fault | 3450.7 | 44756 | 0.25556 | 44756 | 0.26875 | 0.31667 | Inverter Tripped in Riso Fault | 0.043389 | 0.78396 | 117.3752 | Auto-Restarted
Bhadla | July | Inverter 08 | RISO fault | 3444.2 | 44756 | 0.3375 | 44756 | 0.36181 | 0.58333 | Inverter Tripped in Riso Fault | 0.25991 | 0.78396 | 701.7827 | DC floating fault found in 2D4 keeping that SCB Off then start the Inv. & 2D4 St-2,9 & 12 Isolated from SCB.
Bhadla | July | SCB.08.19 | String fault | 12.8 | 44756 | 0.36181 | 44756 | 0.48958 | 3.0667 | St-2 found abnormal Floating | 2.2327 | 0.78396 | 22.4047 | Again checked found ok.
Bhadla | July | SCB.08.19 | String fault | 12.8 | 44756 | 0.36181 | 44756 | 0.48958 | 3.0667 | St-9 found abnormal Floating | 2.2327 | 0.78396 | 22.4047 | Again checked found ok.
Bhadla | July | SCB.08.19 | String fault | 12.8 | 44756 | 0.36181 | 44756 | 0.48958 | 3.0667 | St-12 found abnormal Floating | 2.2327 | 0.78396 | 22.4047 | Again checked found ok.
Bhadla | July | Inverter 10 | RISO fault | 3404.8 | 44756 | 0.25556 | 44756 | 0.29861 | 1.0333 | Inverter tripped in Riso Fault | 0.053757 | 0.78396 | 143.4893 | DC floating fault found in 2B2 keeping that SCB Off then start the Inv
Bhadla | July | SCB.10.07 | String fault | 166.4 | 44756 | 0.29861 | 44756 | 0.37083 | 1.7333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.57916 | 0.78396 | 75.5519 | ST-2 Isolated then Start the SCB
Bhadla | July | SCB.10.07 | String fault | 12.8 | 44756 | 0.37083 | 44756 | 0.49583 | 3 | St-2 found abnormal Floating | 2.2419 | 0.78396 | 22.4965 | (-Ve) Y-connector Replaced with new One.
Bhadla | July | Inverter 11 | Mism Iac fault | 3379.2 | 44756 | 0.25556 | 44756 | 0.33819 | 1.9833 | Inverter Tripped in Mism-Iac Fault. | 0.26381 | 0.78396 | 698.8852 | DC Floating checked fault found in 1A5, 1B1, 1B2 & 1C2 keeping those SCB off then start the inv. & as per SG team instruction we reset the Inv.
Bhadla | July | SCB.11.05 | String fault | 179.2 | 44756 | 0.33819 | 44756 | 0.36806 | 0.71667 | Manually Stopped as found Abnormal Floating During INV mism fault attend | 0.33087 | 0.78396 | 46.483 | Again checked found ok.
Bhadla | July | SCB.11.06 | String fault | 166.4 | 44756 | 0.33819 | 44756 | 0.36806 | 0.71667 | Manually Stopped as found Abnormal Floating During INV mism fault attend | 0.33087 | 0.78396 | 43.1627 | Again checked found ok.
Bhadla | July | SCB.11.07 | String fault | 166.4 | 44756 | 0.33819 | 44756 | 0.39653 | 1.4 | Manually Stopped as found Abnormal Floating During INV mism fault attend | 0.72032 | 0.78396 | 93.967 | Again checked found ok.
Bhadla | July | SCB.11.12 | String fault | 140.8 | 44756 | 0.33819 | 44756 | 0.39653 | 1.4 | Manually Stopped as found Abnormal Floating During INV mism fault attend | 0.72032 | 0.78396 | 79.5105 | Again checked found ok.
Bhadla | July | Inverter 11 | Mism Iac fault | 3379.2 | 44756 | 0.43333 | 44756 | 0.44792 | 0.35 | Again Inverter Tripped in Mism-Iac Fault. | 0.29243 | 0.78396 | 774.694 | as per SG team instruction we reset the Inv.
Bhadla | July | Inverter 12 | RISO fault | 3443.2 | 44756 | 0.25556 | 44756 | 0.29375 | 0.91667 | Inverter Tripped in riso fault | 0.043308 | 0.78396 | 116.9019 | Dc floating checked fault found in 2A2, 2B2, 2B3 2C2 & 2D5 keeping those SCb off then start the Inv.
Bhadla | July | SCB.12.02 | String fault | 166.4 | 44756 | 0.29375 | 44756 | 0.38819 | 2.2667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.82187 | 0.78396 | 107.2139 | Again checked found ok.
Bhadla | July | SCB.12.07 | String fault | 166.4 | 44756 | 0.29375 | 44756 | 0.38819 | 2.2667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.82187 | 0.78396 | 107.2139 | ST-13 Isolated then Start the SCB
Bhadla | July | SCB.12.07 | String fault | 12.8 | 44756 | 0.29375 | 44756 | 0.50347 | 5.0333 | ST-13 found Abnormal Floating | 2.9671 | 0.78396 | 29.7735 | Again checked found ok.
Bhadla | July | SCB.12.08 | String fault | 166.4 | 44756 | 0.29375 | 44756 | 0.36736 | 1.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.5438 | 0.78396 | 70.9399 | Again checked found ok.
Bhadla | July | SCB.12.12 | String fault | 179.2 | 44756 | 0.29375 | 44756 | 0.36736 | 1.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.5438 | 0.78396 | 76.3968 | Again checked found ok.
Bhadla | July | SCB.12.20 | String fault | 192 | 44756 | 0.29375 | 44756 | 0.36736 | 1.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.5438 | 0.78396 | 81.8537 | Again checked found ok.
Bhadla | July | Inverter 16 | RISO fault | 3411.2 | 44756 | 0.28681 | 44756 | 0.31389 | 0.65 | Inverter Tripped in riso fault | 0.092369 | 0.78396 | 247.0167 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44756 | 0.25556 | 44756 | 0.30347 | 1.15 | Inverter Tripped in riso fault | 0.066775 | 0.78396 | 182.9283 | DC Floating Checked Keeping Mentioned SCB Off, then Start the Inv.
Bhadla | July | SCB.26.05 | String fault | 179.2 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 83.4481 | Again checked then Start the SCB.
Bhadla | July | SCB.26.06 | String fault | 166.4 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 77.4875 | Again checked then Start the SCB.
Bhadla | July | SCB.26.09 | String fault | 166.4 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 77.4875 | Again checked then Start the SCB.
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 77.4875 | Again checked then Start the SCB.
Bhadla | July | SCB.26.11 | String fault | 204.8 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 95.3692 | Again checked then Start the SCB.
Bhadla | July | SCB.26.12 | String fault | 179.2 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 83.4481 | Again checked then Start the SCB.
Bhadla | July | SCB.26.14 | String fault | 166.4 | 44756 | 0.30347 | 44756 | 0.37292 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.594 | 0.78396 | 77.4875 | Again checked then Start the SCB.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44757 | 0.24931 | 44757 | 0.27361 | 0.58333 | Inverter tripped in Riso Fault | 0.0095097 | 0.80706 | 26.8192 | DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 01 | Ground fault | 3451.5 | 44759 | 0.25833 | 44759 | 0.28819 | 0.71667 | Inverter tripped in Gnd Fault | 0.0089767 | 0.78385 | 24.2859 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 02 | Ground fault | 3469.9 | 44759 | 0.25833 | 44759 | 0.28056 | 0.53333 | Inverter tripped in Gnd Fault | 0.0063353 | 0.78385 | 17.2313 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 03 | Ground fault | 3450.4 | 44759 | 0.25833 | 44759 | 0.30486 | 1.1167 | Inverter tripped in Gnd Fault | 0.026693 | 0.78385 | 72.194 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 04 | Ground fault | 3470.2 | 44759 | 0.25833 | 44759 | 0.29167 | 0.8 | Inverter tripped in Gnd Fault | 0.010636 | 0.78385 | 28.9302 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 10 | Ground fault | 3404.8 | 44759 | 0.32917 | 44759 | 0.33472 | 0.13333 | Inverter tripped in Gnd Fault | 0.017431 | 0.78385 | 46.522 | Auto-Restarted
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44759 | 0.25833 | 44759 | 0.33264 | 1.7833 | Inverter tripped in Gnd Fault | 0.088497 | 0.78385 | 234.4098 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked and Mentioned SCB off then Start the Inv
Bhadla | July | SCB.11.03 | String fault | 166.4 | 44759 | 0.33264 | 44759 | 0.36319 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.13225 | 0.78385 | 17.2503 | Agan checked found ok.
Bhadla | July | SCB.11.06 | String fault | 166.4 | 44759 | 0.33264 | 44759 | 0.36319 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.13225 | 0.78385 | 17.2503 | Agan checked found ok.
Bhadla | July | SCB.11.12 | String fault | 140.8 | 44759 | 0.33264 | 44759 | 0.36319 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.13225 | 0.78385 | 14.5964 | Agan checked found ok.
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44759 | 0.36389 | 44759 | 0.37778 | 0.33333 | Again Inverter Tripped in Gnd Fault | 0.080622 | 0.78385 | 213.5498 | DC Floating checked nothing mentioned below SCB off then start the Inv.
Bhadla | July | SCB.11.03 | String fault | 166.4 | 44759 | 0.37778 | 44759 | 0.43681 | 1.4167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.89851 | 0.78385 | 117.1948 | Again checked found ok.
Bhadla | July | SCB.11.06 | String fault | 166.4 | 44759 | 0.37778 | 44759 | 0.47153 | 2.25 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.4304 | 0.78385 | 186.5689 | St-4 Isolated then Start the SCB
Bhadla | July | SCB.11.07 | String fault | 166.4 | 44759 | 0.37778 | 44759 | 0.47153 | 2.25 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.4304 | 0.78385 | 186.5689 | Again checked found ok.
Bhadla | July | SCB.11.12 | String fault | 140.8 | 44759 | 0.37778 | 44759 | 0.43681 | 1.4167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.89851 | 0.78385 | 99.1648 | Again checked found ok.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44759 | 0.25833 | 44759 | 0.29583 | 0.9 | Inverter Tripped in Gnd Fault | 0.013796 | 0.78385 | 37.2346 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked and Mentioned below SCB off then Start the Inv
Bhadla | July | SCB.12.01 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.37917 | 2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.295 | 0.78385 | 38.4774 | Again checked found ok
Bhadla | July | SCB.12.02 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.37917 | 2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.295 | 0.78385 | 38.4774 | Again checked found ok
Bhadla | July | SCB.12.08 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.43403 | 3.3167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.1485 | 0.78385 | 149.8043 | Again checked found ok
Bhadla | July | SCB.12.09 | String fault | 192 | 44759 | 0.29583 | 44759 | 0.37917 | 2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.295 | 0.78385 | 44.397 | Again checked found ok
Bhadla | July | SCB.12.15 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.43403 | 3.3167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.1485 | 0.78385 | 149.8043 | Again checked found ok
Bhadla | July | SCB.12.18 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.37917 | 2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.295 | 0.78385 | 38.4774 | Again checked found ok
Bhadla | July | SCB.12.19 | String fault | 166.4 | 44759 | 0.29583 | 44759 | 0.37917 | 2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.295 | 0.78385 | 38.4774 | Again checked found ok
Bhadla | July | SCB.12.20 | String fault | 192 | 44759 | 0.29583 | 44759 | 0.47083 | 4.2 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.7006 | 0.78385 | 255.9373 | St-4 Isolated then Start the SCB
Bhadla | July | Inverter 13 | Ground fault | 3411.2 | 44759 | 0.25833 | 44759 | 0.32708 | 1.65 | Inverter Tripped in Gnd Fault | 0.074128 | 0.78385 | 198.2076 | DC Floating checked and Mentioned below SCB off then Start the Inv
Bhadla | July | SCB.13.05 | String fault | 179.2 | 44759 | 0.32708 | 44759 | 0.38403 | 1.3667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.28134 | 0.78385 | 39.5188 | Again checked found ok
Bhadla | July | SCB.13.06 | String fault | 166.4 | 44759 | 0.32708 | 44759 | 0.38403 | 1.3667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.28134 | 0.78385 | 36.696 | Again checked found ok
Bhadla | July | SCB.13.16 | String fault | 166.4 | 44759 | 0.32708 | 44759 | 0.44097 | 2.7333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.1767 | 0.78385 | 153.4844 | Again checked found ok
Bhadla | July | Inverter 17 | Ground fault | 3404.8 | 44759 | 0.25833 | 44759 | 0.31944 | 1.4667 | Inverter Tripped in Gnd Fault | 0.055885 | 0.78385 | 149.1475 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked and Mentioned SCB off then Start the Inv
Bhadla | July | SCB.17.02 | String fault | 179.2 | 44759 | 0.31944 | 44759 | 0.38889 | 1.6667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38166 | 0.78385 | 53.6106 | Again checked found ok.
Bhadla | July | SCB.17.04 | String fault | 166.4 | 44759 | 0.31944 | 44759 | 0.44306 | 2.9667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.2221 | 0.78385 | 159.3994 | Again checked found ok.
Bhadla | July | SCB.17.05 | String fault | 179.2 | 44759 | 0.31944 | 44759 | 0.46528 | 3.5 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5387 | 0.78385 | 216.133 | St-8 Isolated then Start the SCB
Bhadla | July | Inverter 18 | Ground fault | 3481.6 | 44759 | 0.25833 | 44759 | 0.31389 | 1.3333 | Inverter Tripped in Gnd Fault | 0.043855 | 0.78385 | 119.6827 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked mentioned below SCB off then start the Inv.
Bhadla | July | SCB.18.05 | String fault | 179.2 | 44759 | 0.31389 | 44759 | 0.46528 | 3.6333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.27534 | 0.78385 | 38.6754 | Again checked found ok.
Bhadla | July | SCB.18.11 | String fault | 166.4 | 44759 | 0.31389 | 44759 | 0.38056 | 1.6 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.27534 | 0.78385 | 35.9129 | Again checked found ok.
Bhadla | July | SCB.18.16 | String fault | 192 | 44759 | 0.31389 | 44759 | 0.38056 | 1.6 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.27534 | 0.78385 | 41.4379 | Again checked found ok.
Bhadla | July | SCB.18.17 | String fault | 166.4 | 44759 | 0.31389 | 44759 | 0.38056 | 1.6 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.27534 | 0.78385 | 35.9129 | Again checked found ok.
Bhadla | July | SCB.18.19 | String fault | 153.6 | 44759 | 0.31389 | 44759 | 0.38056 | 1.6 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.27534 | 0.78385 | 33.1503 | Again checked found ok.
Bhadla | July | Inverter 19 | Ground fault | 3520 | 44759 | 0.25833 | 44759 | 0.31181 | 1.2833 | Inverter Tripped in Gnd Fault | 0.039764 | 0.78385 | 109.7132 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 20 | Ground fault | 3507.4 | 44759 | 0.25833 | 44759 | 0.31528 | 1.3667 | Inverter Tripped in Gnd Fault | 0.046661 | 0.78385 | 128.2836 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked fault found in 2A2 keeping scb off then start the SCB.
Bhadla | July | SCB.20.02 | String fault | 166.4 | 44759 | 0.31528 | 44759 | 0.42986 | 2.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.0642 | 0.78385 | 138.8036 | Again checked found ok.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44759 | 0.25833 | 44759 | 0.30833 | 1.2 | Inverter Tripped in Gnd Fault | 0.032975 | 0.78385 | 87.6756 | Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44759 | 0.28264 | 44759 | 0.32361 | 0.98333 | Inverter Tripped in Gnd Fault | 0.059227 | 0.78385 | 162.2269 | Found 10A Gnd Fuse Faulty same replaced.Found 10A Gnd Fuse Faulty same replaced. DC Floating checked nothing found abnormal then start the Inv
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44759 | 0.35833 | 44759 | 0.37639 | 0.43333 | Again Inverter Tripped in Gnd Fault | 0.10488 | 0.78385 | 287.2644 | Found 10A Gnd Fuse Faulty same replaced.DC Floating checked mentioned below SCB off then start the Inv.
Bhadla | July | SCB.26.05 | String fault | 179.2 | 44759 | 0.37639 | 44759 | 0.46875 | 2.2167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3868 | 0.78385 | 194.8028 | Again checked found ok.
Bhadla | July | SCB.26.11 | String fault | 204.8 | 44759 | 0.37639 | 44759 | 0.46875 | 2.2167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3868 | 0.78385 | 222.6318 | Again checked found ok.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44759 | 0.69514 | 44759 | 0.8125 | 2.8167 | Inverter Tripped in Gnd Fault | 0.016703 | 0.78385 | 44.4115 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44759 | 0.71806 | 44759 | 0.8125 | 2.2667 | Inverter Tripped in Gnd Fault | 0.01245 | 0.78385 | 32.9769 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.11.06 | String fault | 12.8 | 44759 | 0.46458 | 44759 | 0.50347 | 0.93333 | ST-4 found Abnormal Floating | 0.54178 | 0.78385 | 5.4359 | Found (-Ve) cable faulty 26 Mtr cable & 2 set MC4 Connector Used.
Bhadla | July | SCB.12.20 | String fault | 12.8 | 44759 | 0.47083 | 44759 | 0.51042 | 0.95 | ST-4 found Abnormal Floating | 0.4253 | 0.78385 | 4.2672 | Found (-Ve) cable faulty 10 Mtr cable & 2 set MC4 Connector Used.
Bhadla | July | SCB.17.05 | String fault | 12.8 | 44759 | 0.46528 | 44759 | 0.52431 | 1.4167 | ST-8 found Abnormal Floating | 0.59264 | 0.78385 | 5.9461 | Found (+ve) Y-connector found faulty same replaced new one.
Bhadla | July | Inverter-1,2,3,4,5,6,9,10,11,12,17,18,19,20,21,22,23,24,25,27 & 28 | Grid voltage issue | 72397.7 | 44759 | 0.66667 | 44759 | 0.66875 | 0.05 | Inverter-1,2,3,4,5,6,9,10,11,12,17,18,19,20,21,22,23,24,25,27 & 28 Tripped due to due to Over voltage in Line. | 0.0010923 | 0.78385 | 61.9886 | Inverters resumes after Grid voltage normalised.
Bhadla | July | Inverter 03 | Ground fault | 3450.4 | 44760 | 0.25278 | 44760 | 0.27708 | 0.58333 | Inverter Tripped in Gnd Fault | 0.013956 | 0.76045 | 36.6189 | DC Floating checked keeping mentioned below SCB's Off, then start the Inv.
Bhadla | July | SCB.03.07 | String fault | 166.4 | 44760 | 0.27708 | 44760 | 0.44792 | 4.1 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5282 | 0.76045 | 193.3811 | Again checked Found Ok.
Bhadla | July | SCB.03.10 | String fault | 166.4 | 44760 | 0.27708 | 44760 | 0.44792 | 4.1 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5282 | 0.76045 | 193.3811 | Again checked Found Ok.
Bhadla | July | SCB.03.15 | String fault | 166.4 | 44760 | 0.27708 | 44760 | 0.50486 | 5.4667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 2.3279 | 0.76045 | 294.5743 | ST-3 Isolated then start the SCB.
Bhadla | July | SCB.03.15 | String fault | 12.8 | 44760 | 0.50486 | 44760 | 0.6875 | 4.3833 | St-3 found abnormal floating | 3.1322 | 0.76045 | 30.4881 | Found (-ve) Side 16mtr cable with 2 set MC4 Connector used.
Bhadla | July | SCB.03.18 | String fault | 166.4 | 44760 | 0.27708 | 44760 | 0.44792 | 4.1 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.5282 | 0.76045 | 193.3811 | Again checked Found Ok.
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44760 | 0.25278 | 44760 | 0.28542 | 0.78333 | Inverter Tripped in Gnd Fault. | 0.028983 | 0.76045 | 74.4778 | DC Floating checked keeping mentioned below SCB's Off, then start the Inv.
Bhadla | July | SCB.11.03 | String fault | 166.4 | 44760 | 0.28542 | 44760 | 0.4 | 2.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.8955 | 0.76045 | 113.315 | Again checked Found Ok.
Bhadla | July | SCB.11.04 | String fault | 166.4 | 44760 | 0.28542 | 44760 | 0.4 | 2.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.8955 | 0.76045 | 113.315 | Again checked Found Ok.
Bhadla | July | SCB.11.06 | String fault | 166.4 | 44760 | 0.28542 | 44760 | 0.44444 | 3.8167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.4872 | 0.76045 | 188.1857 | Again checked Found Ok.
Bhadla | July | SCB.11.12 | String fault | 140.8 | 44760 | 0.28542 | 44760 | 0.44444 | 3.8167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.4872 | 0.76045 | 159.2341 | Again checked Found Ok.
Bhadla | July | SCB.11.16 | String fault | 179.2 | 44760 | 0.28542 | 44760 | 0.4 | 2.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.8955 | 0.76045 | 122.0315 | Again checked Found Ok.
Bhadla | July | SCB.11.18 | String fault | 153.6 | 44760 | 0.28542 | 44760 | 0.4 | 2.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.8955 | 0.76045 | 104.5984 | Again checked Found Ok.
Bhadla | July | Inverter 12 | Ground fault | 3443.2 | 44760 | 0.25278 | 44760 | 0.28819 | 0.85 | Inverter Tripped in Gnd Fault. | 0.0059007 | 0.76045 | 15.4501 | DC Floating checked keeping mentioned below SCB's Off, then start the Inv.
Bhadla | July | SCB.12.08 | String fault | 166.4 | 44760 | 0.28819 | 44760 | 0.39722 | 2.6167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.86196 | 0.76045 | 109.0713 | Again checked Found Ok.
Bhadla | July | SCB.12.12 | String fault | 179.2 | 44760 | 0.28819 | 44760 | 0.65139 | 8.7167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 5.134 | 0.76045 | 699.6208 | ST-15 Isolated then start the SCB.
Bhadla | July | SCB.12.12 | String fault | 12.8 | 44760 | 0.65139 | 44760 | 0.73958 | 2.1167 | St-15 found abnormal floating | 0.72131 | 0.76045 | 7.021 | Found (-ve) Side 35mtr cable with 2 set MC4 Connector used.
Bhadla | July | SCB.12.13 | String fault | 166.4 | 44760 | 0.28819 | 44760 | 0.39722 | 2.6167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.86196 | 0.76045 | 109.0713 | Again checked Found Ok.
Bhadla | July | SCB.12.20 | String fault | 192 | 44760 | 0.28819 | 44760 | 0.39722 | 2.6167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.86196 | 0.76045 | 125.8515 | Again checked Found Ok.
Bhadla | July | Inverter 14 | Ground fault | 3430.4 | 44760 | 0.25278 | 44760 | 0.29792 | 1.0833 | Inverter Tripped in Gnd Fault. | 0.063984 | 0.76045 | 166.9116 | Dc Floating checked fault found in 2A4 keeping SCB off then start the Inv.
Bhadla | July | SCB.14.04 | String fault | 166.4 | 44760 | 0.29792 | 44760 | 0.39514 | 2.3333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.82927 | 0.76045 | 104.935 | Found abnormal Floating.
Bhadla | July | Inverter 14 | Ground fault | 3430.4 | 44760 | 0.39583 | 44760 | 0.40347 | 0.18333 | Again Inverter Tripped in Gnd Fault. | 0.1047 | 0.76045 | 273.1224 | Dc Floating checked fault found in 2A4 keeping SCB off then start the Inv.
Bhadla | July | SCB.14.04 | String fault | 166.4 | 44760 | 0.40417 | 44760 | 0.47986 | 1.8167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.91703 | 0.76045 | 116.04 | ST-3 Isolated then start the SCB.
Bhadla | July | SCB.14.04 | String fault | 12.8 | 44760 | 0.47986 | 44760 | 0.72917 | 5.9833 | St-3 found abnormal floating | 3.9363 | 0.76045 | 38.3149 | Found (+ve) Side Y-Connector burnt same replaced with new one.
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44760 | 0.25278 | 44760 | 0.30556 | 1.2667 | Inverter tripped in Gnd Fault | 0.023678 | 0.76045 | 62.9202 | DC Floating Checked fault found in SCB 1B1 & 1D5 keeping those SCB off then Start the Inv.
Bhadla | July | SCB.21.06 | String fault | 179.2 | 44760 | 0.30556 | 44760 | 0.49931 | 4.65 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 2.1963 | 0.76045 | 299.2942 | Again checked Found Ok.
Bhadla | July | SCB.21.20 | String fault | 153.6 | 44760 | 0.30556 | 44760 | 0.46944 | 3.9333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.62 | 0.76045 | 189.2292 | ST-4 Isolated then start the SCB.
Bhadla | July | SCB.21.20 | String fault | 12.8 | 44760 | 0.46944 | 44760 | 0.70139 | 5.5667 | St-4 found abnormal floating | 3.8834 | 0.76045 | 37.8 | Found (-ve) Side 10mtr cable with 2 set MC4 Connector used.
Bhadla | July | Inverter 24 | Ground fault | 3392 | 44760 | 0.25278 | 44760 | 0.33403 | 1.95 | Inverter Tripped in gnd Fault. | 0.26602 | 0.76045 | 686.1943 | DC Floating keeping mention below SCB's Off then start the Inv.
Bhadla | July | SCB.24.01 | String fault | 179.2 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 29.697 | Again checked Found Ok.
Bhadla | July | SCB.24.02 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 27.5758 | Again checked Found Ok.
Bhadla | July | SCB.24.03 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 27.5758 | Again checked Found Ok.
Bhadla | July | SCB.24.04 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.45417 | 2.8833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3246 | 0.76045 | 167.6132 | Again checked Found Ok.
Bhadla | July | SCB.24.05 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.45417 | 2.8833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3246 | 0.76045 | 167.6132 | Again checked Found Ok.
Bhadla | July | SCB.24.07 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 27.5758 | Again checked Found Ok.
Bhadla | July | SCB.24.09 | String fault | 179.2 | 44760 | 0.33403 | 44760 | 0.45417 | 2.8833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3246 | 0.76045 | 180.5065 | Again checked Found Ok.
Bhadla | July | SCB.24.11 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 27.5758 | Again checked Found Ok.
Bhadla | July | SCB.24.12 | String fault | 192 | 44760 | 0.33403 | 44760 | 0.49653 | 3.9 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.9784 | 0.76045 | 288.8558 | ST-15 Isolated then start the SCB.
Bhadla | July | SCB.24.12 | String fault | 12.8 | 44760 | 0.49653 | 44760 | 0.73472 | 5.7167 | St-15 found abnormal floating | 3.6208 | 0.76045 | 35.2437 | Found (-ve) Side 35mtr cable with 2 set MC4 Connector used.
Bhadla | July | SCB.24.16 | String fault | 179.2 | 44760 | 0.33403 | 44760 | 0.35694 | 0.55 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.21792 | 0.76045 | 29.697 | Again checked Found Ok.
Bhadla | July | SCB.24.18 | String fault | 166.4 | 44760 | 0.33403 | 44760 | 0.45417 | 2.8833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3246 | 0.76045 | 167.6132 | Again checked Found Ok.
Bhadla | July | SCB.24.19 | String fault | 140.8 | 44760 | 0.33403 | 44760 | 0.45417 | 2.8833 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 1.3246 | 0.76045 | 141.8266 | Again checked Found Ok.
Bhadla | July | Inverter 26 | Island protection fault | 3494.4 | 44760 | 0.35486 | 44760 | 0.47014 | 2.7667 | Inverter Tripped in Island protection fault. | 1.2727 | 0.76045 | 3381.9009 | Discussed with SG Team gave them all parameters pic, as per his instructions we reset the Inverter. But again tripped Unit-1. then we interchange Master & Slave between Unit-1 & 2. and also remove control cable in ACDB section. Then Inverter Started.
Bhadla | July | Inverter 26 | Island protection fault | 896 | 44760 | 0.47014 | 44760 | 0.81736 | 8.3333 | Unit-01 Tripped in Island protection Fault | 4.2921 | 0.76045 | 2924.4709 | After the generation period, Sungrow team replaced the faulty AC brekaer, now all unit are in healthy condition
Bhadla | July | SCB.26.11 | String fault | 204.8 | 44760 | 0.47014 | 44760 | 0.50625 | 0.86667 | Found DC Floating abnormal during fault attend | 0.63175 | 0.76045 | 98.388 | Again checked Found Ok.
Bhadla | July | SCB.26.20 | String fault | 179.2 | 44760 | 0.47014 | 44760 | 0.50625 | 0.86667 | Found DC Floating abnormal during fault attend | 0.63175 | 0.76045 | 86.0895 | Again checked Found Ok.
Bhadla | July | Inverter 06 | Ground fault | 3450.7 | 44761 | 0.24931 | 44761 | 0.28542 | 0.86667 | Inverter Tripped in Gnd Fault | 0.030051 | 0.78621 | 81.527 | DC Floating Checked Fault Found in 2B1 keeping that SCB off , then Start the Inv.
Bhadla | July | SCB.06.06 | String fault | 166.4 | 44761 | 0.28542 | 44761 | 0.3875 | 2.45 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.78046 | 0.78621 | 102.1047 | Again checked Found Ok.
Bhadla | July | Inverter 11 | Ground fault | 3379.2 | 44761 | 0.29861 | 44761 | 0.31111 | 0.3 | Inverter Tripped in Gnd Fault | 0.046765 | 0.78621 | 124.2434 | DC Floating checked nothimg found abnormal then start the SCB
Bhadla | July | Inverter 15 | Ground fault | 3475.2 | 44761 | 0.24931 | 44761 | 0.29167 | 1.0167 | Inverter Tripped in Gnd Fault | 0.044321 | 0.78621 | 121.095 | DC Floating Checked Fault Found in 1A5 & 1D4 keeping those SCB off , then Start the Inv.
Bhadla | July | SCB.15.05 | String fault | 166.4 | 44761 | 0.29167 | 44761 | 0.38056 | 2.1333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.67244 | 0.78621 | 87.9719 | Again checked Found Ok.
Bhadla | July | SCB.15.19 | String fault | 166.4 | 44761 | 0.29167 | 44761 | 0.38056 | 2.1333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.67244 | 0.78621 | 87.9719 | Again checked Found Ok.
Bhadla | July | Inverter 19 | Ground fault | 3520 | 44761 | 0.24931 | 44761 | 0.27708 | 0.66667 | Inverter Tripped in Gnd Fault | 0.015986 | 0.78621 | 44.2417 | DC Floating checked nothimg found abnormal then start the SCB
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44761 | 0.24931 | 44761 | 0.29861 | 1.1833 | Inverter Tripped in Gnd Fault | 0.064135 | 0.78621 | 176.1999 | DC Floating Checked Fault Found in 2A4, 2B5, 2C1 & 2D5 keeping those SCB off , then Start the Inv.
Bhadla | July | SCB.26.04 | String fault | 204.8 | 44761 | 0.29861 | 44761 | 0.35972 | 1.4667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.080458 | 0.78621 | 12.955 | ST-10 Isolated then Start the SCB
Bhadla | July | SCB.26.04 | String fault | 12.8 | 44761 | 0.35972 | 44761 | 0.48611 | 3.0333 | ST-10 found abnormal floating | 2.5066 | 0.78621 | 25.2253 | Found (-Ve) side Y-Connector found damage same replaced by new one.
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44761 | 0.29861 | 44761 | 0.35972 | 1.4667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.080458 | 0.78621 | 10.5259 | Again checked Found Ok.
Bhadla | July | SCB.26.10 | String fault | 12.8 | 44761 | 0.35972 | 44761 | 0.49306 | 3.2 | St-3 found abnormal floating | 2.6557 | 0.78621 | 26.7257 | Again checked found ok.
Bhadla | July | SCB.26.11 | String fault | 204.8 | 44761 | 0.29861 | 44761 | 0.35972 | 1.4667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.080458 | 0.78621 | 12.955 | Again checked found ok.
Bhadla | July | SCB.26.20 | String fault | 179.2 | 44761 | 0.29861 | 44761 | 0.34306 | 1.0667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.2521 | 0.78621 | 35.5177 | Again checked found ok.
Bhadla | July | Inverter 26 | Ground fault | 3494.4 | 44761 | 0.36042 | 44761 | 0.37708 | 0.4 | Again Inverter Tripped in Gnd Fault | 0.19911 | 0.78621 | 547.0156 | Again DC Floating Checked nothing found abnormal , then Start the Inv.
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44762 | 0.25139 | 44762 | 0.27778 | 0.63333 | Inverter Tripped in Gnd Fault | 0.015126 | 0.79813 | 42.1872 | DC Floating checked fault found in 1D2 & 1D3 keeping those SCB off then Start the Inv.
Bhadla | July | SCB.21.17 | String fault | 204.8 | 44762 | 0.27778 | 44762 | 0.30903 | 0.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.085178 | 0.79813 | 13.923 | ST-5 & 14 Isolated then Start the SCB
Bhadla | July | SCB.21.17 | String fault | 12.8 | 44762 | 0.30903 | 44762 | 0.48611 | 4.25 | St-5 found abnormal Floating | 2.543 | 0.79813 | 25.9792 | Again checked found ok.
Bhadla | July | SCB.21.17 | String fault | 12.8 | 44762 | 0.30903 | 44762 | 0.49306 | 4.4167 | St-14 found abnormal Floating | 2.6978 | 0.79813 | 27.5606 | Found both (+ve) & (-ve) Side cable faulty and 120mtr cable with 2 set MC4 connector used.
Bhadla | July | SCB.21.18 | String fault | 179.2 | 44762 | 0.27778 | 44762 | 0.30903 | 0.75 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.085178 | 0.79813 | 12.1826 | ST-1 & 4 Isolated then Start the SCB
Bhadla | July | SCB.21.18 | String fault | 12.8 | 44762 | 0.30903 | 44762 | 0.51389 | 4.9167 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 3.1685 | 0.79813 | 32.3696 | Found (+ve) Y-connector found faulty same replaced new one.
Bhadla | July | SCB.21.18 | String fault | 12.8 | 44762 | 0.30903 | 44762 | 0.53125 | 5.3333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 3.5659 | 0.79813 | 36.4292 | Found (+ve) Y-connector found faulty same replaced new one.
Bhadla | July | SCB.17.17 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44762 | 0.25139 | 44762 | 0.81667 | 13.5667 | String Manually Isolated (Low VOC Issue) | 7.3161 | 0.79813 | 74.7416 | Resoration WIP.
Bhadla | July | SCB.17.17 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44763 | 0.25208 | 44763 | 0.81042 | 13.4 | String Manually Isolated (Low VOC Issue) | 5.199 | 0.80971 | 53.8841 | Resoration WIP.
Bhadla | July | Inverter 20 | Ground fault | 3507.4 | 44764 | 0.39097 | 44764 | 0.40278 | 0.28333 | Inverter Tripped in Gnd Fault. | 0.065215 | 0.79473 | 181.7836 | Dc Floating checked fault found in 2C2 keeping that SCB off then start the Inv.
Bhadla | July | SCB.20.12 | String fault | 166.4 | 44764 | 0.40278 | 44764 | 0.43125 | 0.68333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.36594 | 0.79473 | 48.3933 | Again checked ok
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44764 | 0.25417 | 44764 | 0.27708 | 0.55 | Inverter Tripped in Gnd Fault. | 0.008729 | 0.79473 | 24.2414 | Dc Floating checked fault found in 1D4 keeping that SCB off then start the Inv.
Bhadla | July | SCB.21.19 | String fault | 166.4 | 44764 | 0.27708 | 44764 | 0.28889 | 0.28333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.013621 | 0.79473 | 1.8012 | ST-8 & 11 Isolated then start SCB
Bhadla | July | SCB.21.19 | String fault | 12.8 | 44764 | 0.28889 | 44764 | 0.43611 | 3.5333 | ST-8 found Abnormal Floating | 0.87605 | 0.79473 | 8.9116 | Again checked found ok.
Bhadla | July | SCB.21.19 | String fault | 12.8 | 44764 | 0.28889 | 44764 | 0.43611 | 3.5333 | ST-11 found Abnormal Floating | 0.87605 | 0.79473 | 8.9116 | Again checked found ok.
Bhadla | July | SCB.17.17 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44764 | 0.25417 | 44764 | 0.81806 | 13.5333 | String Manually Isolated (Low VOC Issue) | 5.4823 | 0.79473 | 55.7693 | Resoration WIP.
Bhadla | July | Inverter 11 | RISO fault | 3379.2 | 44765 | 0.72153 | 44765 | 0.73611 | 0.35 | Inverter Tripped in Riso Fault. | 0.068774 | 0.76397 | 177.5468 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44765 | 0.25486 | 44765 | 0.27569 | 0.5 | Inverter Tripped in Riso Fault. | 0.0083208 | 0.76397 | 22.2133 | DC Floating checked fault found in SCB 1A3, 1B3 & 1C3 keeping those SCB Off, then start the Inv.
Bhadla | July | SCB.21.05 | String fault | 140.8 | 44765 | 0.27569 | 44765 | 0.29931 | 0.56667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.03177 | 0.76397 | 3.4174 | Again Checked found ok.
Bhadla | July | SCB.21.08 | String fault | 179.2 | 44765 | 0.27569 | 44765 | 0.29931 | 0.56667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.03177 | 0.76397 | 4.3494 | Again Checked found ok.
Bhadla | July | SCB.21.13 | String fault | 192 | 44765 | 0.27569 | 44765 | 0.29931 | 0.56667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.03177 | 0.76397 | 4.6601 | Again Checked found ok.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44765 | 0.65903 | 44765 | 0.67708 | 0.43333 | Inverter Tripped in Riso Fault. | 0.028835 | 0.76397 | 76.977 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44765 | 0.71458 | 44765 | 0.73194 | 0.41667 | Again Inverter Tripped in Riso Fault. | 0.10066 | 0.76397 | 268.726 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | SCB.17.17 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44765 | 0.25486 | 44765 | 0.81111 | 13.35 | String Manually Isolated (Low VOC Issue) | 3.8246 | 0.76397 | 37.3994 | Resoration WIP.
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44766 | 0.33403 | 44766 | 0.34583 | 0.28333 | Inverter Tripped in Riso Fault | 0.11244 | 0.78605 | 305.0464 | DC Floating checked fault found in 1B4, 1B5 1C1 & 1D1 keeping those SCB off then Start the Inv.
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44766 | 0.34583 | 44766 | 0.40556 | 1.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.55379 | 0.78605 | 66.8629 | Again checked found ok.
Bhadla | July | SCB.01.10 | String fault | 185.6 | 44766 | 0.34583 | 44766 | 0.44306 | 2.3333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.1325 | 0.78605 | 165.2183 | Again checked found ok.
Bhadla | July | SCB.01.11 | String fault | 192 | 44766 | 0.34583 | 44766 | 0.42847 | 1.9833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.86853 | 0.78605 | 131.081 | Again checked found ok.
Bhadla | July | SCB.01.16 | String fault | 192 | 44766 | 0.34583 | 44766 | 0.42847 | 1.9833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.86853 | 0.78605 | 131.081 | Again checked found ok.
Bhadla | July | Inverter 11 | RISO fault | 3379.2 | 44766 | 0.30347 | 44766 | 0.34792 | 1.0667 | Inverter Tripped in Riso Fault | 0.25633 | 0.78605 | 680.8628 | DC Floating checked fault found in 1A3 & 1A5 keeping those SCB off then Start the Inv.
Bhadla | July | SCB.11.03 | String fault | 166.4 | 44766 | 0.34792 | 44766 | 0.43472 | 2.0833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.95574 | 0.78605 | 125.0095 | Again checked found ok.
Bhadla | July | SCB.11.05 | String fault | 179.2 | 44766 | 0.34792 | 44766 | 0.43472 | 2.0833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.95574 | 0.78605 | 134.6257 | Again checked found ok.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44766 | 0.2625 | 44766 | 0.30625 | 1.05 | Inverter Tripped in Riso Fault | 0.053793 | 0.78605 | 147.7562 | DC Floating checked fault found in 1A5, 1C2 & 1D4 keeping those SCB off then Start the Inv.
Bhadla | July | SCB.21.05 | String fault | 140.8 | 44766 | 0.30625 | 44766 | 0.43125 | 3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.1405 | 0.78605 | 126.2299 | Again checked found ok.
Bhadla | July | SCB.21.12 | String fault | 179.2 | 44766 | 0.30625 | 44766 | 0.43125 | 3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.1405 | 0.78605 | 160.6563 | Again checked found ok.
Bhadla | July | SCB.21.19 | String fault | 166.4 | 44766 | 0.30625 | 44766 | 0.43125 | 3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.1405 | 0.78605 | 149.1808 | Again checked found ok.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44766 | 0.25833 | 44766 | 0.29931 | 0.98333 | Inverter Tripped in Riso Fault | 0.039237 | 0.78605 | 107.7745 | Auto-Restarted
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44766 | 0.31528 | 44766 | 0.33403 | 0.45 | Again Inverter Tripped in Riso Fault | 0.093614 | 0.78605 | 257.1362 | Auto-Restarted
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44766 | 0.36042 | 44766 | 0.37222 | 0.28333 | Again Inverter Tripped in Riso Fault | 0.080696 | 0.78605 | 221.6547 | DC Floating checked fault found in 2A5 keeping that Scb off then start the inv.
Bhadla | July | SCB.26.05 | String fault | 179.2 | 44766 | 0.37222 | 44766 | 0.42847 | 1.35 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.66965 | 0.78605 | 94.3275 | Again checked found ok.
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44766 | 0.37222 | 44766 | 0.42847 | 1.35 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.66965 | 0.78605 | 87.5898 | Again checked found ok.
Bhadla | July | SCB.17.17 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.53333 | 6.6 | String Manually Isolated (Low VOC Issue) | 2.8382 | 0.78605 | 28.556 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.74375 | 11.65 | String Manually Isolated (Low VOC Issue) | 6.086 | 0.78605 | 61.2336 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.51042 | 6.05 | String Manually Isolated (Low VOC Issue) | 2.5022 | 0.78605 | 25.1762 | Resoration WIP.
Bhadla | July | SCB.19.19 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.51042 | 6.05 | String Manually Isolated (Low VOC Issue) | 2.5022 | 0.78605 | 25.1762 | Resoration WIP.
Bhadla | July | SCB.20.02 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.74375 | 11.65 | String Manually Isolated (Low VOC Issue) | 6.086 | 0.78605 | 61.2336 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.73472 | 11.4333 | String Manually Isolated (Low VOC Issue) | 6.0415 | 0.78605 | 60.7864 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.73472 | 11.4333 | String Manually Isolated (Low VOC Issue) | 6.0415 | 0.78605 | 60.7864 | Resoration WIP.
Bhadla | July | SCB.20.01 | String fault | 12.8 | 44766 | 0.25833 | 44766 | 0.73472 | 11.4333 | String Manually Isolated (Low VOC Issue) | 6.0415 | 0.78605 | 60.7864 | Resoration WIP.
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44767 | 0.27847 | 44767 | 0.29444 | 0.38333 | Inverter Tripped in Riso Fault | 0.038701 | 0.80297 | 107.2575 | DC Floating checked fault found in 1B4, 1C4 & 1C5 keeping those Scb off then start the inv.
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44767 | 0.29444 | 44767 | 0.34722 | 1.2667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.28405 | 0.80297 | 35.0331 | Again checked found ok
Bhadla | July | SCB.01.14 | String fault | 153.6 | 44767 | 0.29444 | 44767 | 0.34722 | 1.2667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.28405 | 0.80297 | 35.0331 | Again checked found ok
Bhadla | July | SCB.01.15 | String fault | 166.4 | 44767 | 0.29444 | 44767 | 0.34722 | 1.2667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.28405 | 0.80297 | 37.9525 | Again checked found ok
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44767 | 0.34792 | 44767 | 0.36944 | 0.51667 | Again Inverter Tripped in Riso Fault. | 0.20386 | 0.80297 | 564.9887 | DC Floating checked fault found in 1B2, 1B4 & 1C4 keeping those SCb off then start the Inv.
Bhadla | July | SCB.01.07 | String fault | 166.4 | 44767 | 0.36944 | 44767 | 0.40972 | 0.96667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.52453 | 0.80297 | 70.0844 | Again checked found ok
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44767 | 0.36944 | 44767 | 0.40972 | 0.96667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.52453 | 0.80297 | 64.6933 | ST-2 Isolated then Start the SCB
Bhadla | July | SCB.01.09 | String fault | 12.8 | 44767 | 0.40972 | 44767 | 0.51389 | 2.5 | St-2 found abnormal Floating | 1.613 | 0.80297 | 16.5789 | Found (+Ve) String cable faulty 15 Mtr used with 2 set Mc4 connector.
Bhadla | July | SCB.01.15 | String fault | 166.4 | 44767 | 0.36944 | 44767 | 0.38264 | 0.31667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.14814 | 0.80297 | 19.7933 | Again checked found ok
Bhadla | July | Inverter 07 | RISO fault | 3495.8 | 44767 | 0.25208 | 44767 | 0.27917 | 0.65 | Inverter Tripped in Riso Fault | 0.021635 | 0.80297 | 60.729 | DC Floating checked fault found in 1A2 & 1B5 keeping that SCB off , then Start the Inv.
Bhadla | July | SCB.07.02 | String fault | 166.4 | 44767 | 0.27917 | 44767 | 0.325 | 1.1 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.1776 | 0.80297 | 23.7296 | Again checked found ok
Bhadla | July | SCB.07.10 | String fault | 166.4 | 44767 | 0.27917 | 44767 | 0.325 | 1.1 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.1776 | 0.80297 | 23.7296 | Again checked found ok
Bhadla | July | Inverter 08 | Ground fault | 3444.2 | 44767 | 0.53403 | 44767 | 0.5625 | 0.68333 | Inverter Tripped in Gnd Fault | 0.71934 | 0.80297 | 1989.3981 | DC Floating checked fault found in 2A3, 2B1 & 2B3 keeping those SCB off , then Start the Inv.
Bhadla | July | SCB.08.03 | String fault | 179.2 | 44767 | 0.5625 | 44767 | 0.56806 | 0.13333 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.084277 | 0.80297 | 12.1268 | St-8 Isolated then start SCB
Bhadla | July | SCB.08.03 | String fault | 12.8 | 44767 | 0.56806 | 44767 | 0.6875 | 2.8667 | ST-8 found Abnormal Floating | 1.5011 | 0.80297 | 15.4287 | Found (+Ve) String cable faulty 20 Mtr used with 2 set Mc4 connector.
Bhadla | July | SCB.08.06 | String fault | 179.2 | 44767 | 0.5625 | 44767 | 0.56667 | 0.1 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.069138 | 0.80297 | 9.9484 | Again checked found ok
Bhadla | July | SCB.08.08 | String fault | 166.4 | 44767 | 0.5625 | 44767 | 0.57153 | 0.21667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.11706 | 0.80297 | 15.6411 | Again checked found ok
Bhadla | July | Inverter 13 | RISO fault | 3411.2 | 44767 | 0.25208 | 44767 | 0.26667 | 0.35 | Inverter Tripped in Riso Fault | 0.0065083 | 0.80297 | 17.8269 | Auto-Restarted
Bhadla | July | Inverter 15 | RISO fault | 3475.2 | 44767 | 0.25208 | 44767 | 0.28125 | 0.7 | Inverter Tripped in Riso Fault | 0.025445 | 0.80297 | 71.0034 | Auto-Restarted
Bhadla | July | Inverter 16 | RISO fault | 3411.2 | 44767 | 0.25208 | 44767 | 0.26667 | 0.35 | Inverter Tripped in Riso Fault | 0.0065083 | 0.80297 | 17.8269 | Auto-Restarted
Bhadla | July | Inverter 20 | RISO fault | 3507.4 | 44767 | 0.25208 | 44767 | 0.26667 | 0.35 | Inverter Tripped in Riso Fault | 0.0065083 | 0.80297 | 18.3297 | Auto-Restarted
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44768 | 0.25347 | 44768 | 0.31875 | 1.5667 | Inverter Tripped in Riso Fault | 0.058481 | 0.7705 | 155.5237 | DC Floating fault found in 1A5, 1B4, 1B5 & 1D1 keeping those SCB Off then start the Inv.
Bhadla | July | SCB.01.05 | String fault | 179.2 | 44768 | 0.31875 | 44768 | 0.49931 | 4.3333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.6627 | 0.7705 | 229.5689 | Again checked found Ok.
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44768 | 0.31875 | 44768 | 0.49931 | 4.3333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.6627 | 0.7705 | 196.7733 | Again checked found Ok.
Bhadla | July | SCB.01.10 | String fault | 185.6 | 44768 | 0.31875 | 44768 | 0.49931 | 4.3333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.6627 | 0.7705 | 237.7678 | Again checked found Ok.
Bhadla | July | SCB.01.16 | String fault | 192 | 44768 | 0.31875 | 44768 | 0.51042 | 4.6 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.8077 | 0.7705 | 267.4256 | ST-7 & 10 Isolated then start the SCB
Bhadla | July | SCB.01.16 | String fault | 12.8 | 44768 | 0.51042 | 44768 | 0.80208 | 7 | ST-7 found Abnormal Floating | 1.0925 | 0.7705 | 10.7748 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.16 | String fault | 12.8 | 44768 | 0.51042 | 44768 | 0.80208 | 7 | ST-10 found Abnormal Floating | 1.0925 | 0.7705 | 10.7748 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 01 | DSP comm. fault | 3451.5 | 44768 | 0.51111 | 44768 | 0.51736 | 0.15 | Inverter Tripped in DSP Comm. Fault | 0.15796 | 0.7705 | 420.064 | Inverter Restarted.
Bhadla | July | Inverter 11 | RISO fault | 3379.2 | 44768 | 0.29444 | 44768 | 0.32639 | 0.76667 | Inverter Tripped in Riso Fault | 0.042722 | 0.7705 | 111.2337 | Auto-Restarted
Bhadla | July | Inverter 11 | RISO fault | 3379.2 | 44768 | 0.39167 | 44768 | 0.40208 | 0.25 | Inverter Tripped in Riso Fault | 0.11572 | 0.7705 | 301.2942 | DC Floating checked fault found in 1A5 keeping that SCB off then start the Inv.
Bhadla | July | SCB.11.05 | String fault | 179.2 | 44768 | 0.40278 | 44768 | 0.49861 | 2.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.3011 | 0.7705 | 179.6481 | ST-2 Isolated then start the SCB
Bhadla | July | SCB.11.05 | String fault | 12.5 | 44768 | 0.49861 | 44768 | 0.80208 | 7.2833 | St-2 found abnormal Floating | 1.2362 | 0.7705 | 11.906 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44768 | 0.26944 | 44768 | 0.32569 | 1.35 | Inverter Tripped in Riso Fault | 0.0085408 | 0.7705 | 22.9956 | DC Floating checked keeping mentioned below SCB's Off, then start the Inv.
Bhadla | July | SCB.21.06 | String fault | 179.2 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 78.2229 | Manually off for Floating check
Bhadla | July | SCB.21.08 | String fault | 179.2 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 78.2229 | Manually off for Floating check
Bhadla | July | SCB.21.12 | String fault | 179.2 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 78.2229 | Manually off for Floating check
Bhadla | July | SCB.21.15 | String fault | 166.4 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 72.6356 | Manually off for Floating check
Bhadla | July | SCB.21.16 | String fault | 179.2 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 78.2229 | Manually off for Floating check
Bhadla | July | SCB.21.19 | String fault | 153.6 | 44768 | 0.32569 | 44768 | 0.41528 | 2.15 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.56653 | 0.7705 | 67.0482 | Manually off for Floating check
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44768 | 0.41597 | 44768 | 0.45486 | 0.93333 | Inverter Tripped in Gnd Fault | 0.54546 | 0.7705 | 1468.6144 | DC Floating checked and we stopped all DC MCCB in Unit-2 for checking purpose.
Bhadla | July | SCB.21.06 | String fault | 179.2 | 44768 | 0.45486 | 44768 | 0.48264 | 0.66667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38159 | 0.7705 | 52.687 | Again checked found Ok.
Bhadla | July | SCB.21.07 | String fault | 192 | 44768 | 0.45486 | 44768 | 0.48264 | 0.66667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38159 | 0.7705 | 56.4504 | Again checked found Ok.
Bhadla | July | SCB.21.08 | String fault | 179.2 | 44768 | 0.45486 | 44768 | 0.48264 | 0.66667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38159 | 0.7705 | 52.687 | ST-2 Isolated then Start the SCB
Bhadla | July | SCB.21.08 | String fault | 12.8 | 44768 | 0.48264 | 44768 | 0.80208 | 7.6667 | St-2 found abnormal Floating | 1.4432 | 0.7705 | 14.2332 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.09 | String fault | 166.4 | 44768 | 0.45486 | 44768 | 0.48264 | 0.66667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38159 | 0.7705 | 48.9237 | Again checked found Ok.
Bhadla | July | SCB.21.10 | String fault | 166.4 | 44768 | 0.45486 | 44768 | 0.48264 | 0.66667 | Manually Stopped as found Abnormal Floating During INV Gnd fault attend | 0.38159 | 0.7705 | 48.9237 | Again checked found Ok.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44768 | 0.30139 | 44768 | 0.31944 | 0.43333 | Inverter Tripped in Riso Fault | 0.027437 | 0.7705 | 73.8733 | Auto-Restarted
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44768 | 0.34653 | 44768 | 0.36389 | 0.41667 | Again Inverter Tripped in Riso Fault | 0.036314 | 0.7705 | 97.7745 | DC Floating fault found in 2B4 & 2B5 keeping those SCB Off then start the Inv.
Bhadla | July | SCB.26.09 | String fault | 166.4 | 44768 | 0.36389 | 44768 | 0.48681 | 2.95 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.4267 | 0.7705 | 182.9132 | Again checked found Ok.
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44768 | 0.36389 | 44768 | 0.48681 | 2.95 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 1.4267 | 0.7705 | 182.9132 | Again checked found Ok.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44768 | 0.575 | 44768 | 0.60139 | 0.63333 | Inverter Tripped in Riso Fault | 0.14229 | 0.7705 | 383.1153 | DC checked no any fault found then start the Inv.
Bhadla | July | Inverter 01 | RISO fault | 3451.5 | 44768 | 0.64306 | 44768 | 0.68681 | 1.05 | Inverter Tripped in Riso Fault | 0.031822 | 0.7705 | 84.6282 | DC Floating checked keeping mentioned below SCB's Off, then start the Inv.
Bhadla | July | SCB.01.06 | String fault | 192 | 44768 | 0.68681 | 44768 | 0.80208 | 2.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.17065 | 0.7705 | 25.2454 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44768 | 0.68681 | 44768 | 0.80208 | 2.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.17065 | 0.7705 | 20.1963 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.10 | String fault | 185.6 | 44768 | 0.68681 | 44768 | 0.80208 | 2.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.17065 | 0.7705 | 24.4039 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.11 | String fault | 192 | 44768 | 0.68681 | 44768 | 0.80208 | 2.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.17065 | 0.7705 | 25.2454 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.18 | String fault | 166.4 | 44768 | 0.68681 | 44768 | 0.80208 | 2.7667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.17065 | 0.7705 | 21.8793 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 21 | RISO fault | 3494.4 | 44768 | 0.64444 | 44768 | 0.69653 | 1.25 | Inverter Tripped in Riso Fault | 0.041173 | 0.7705 | 110.8548 | DC checked no any fault found then start the Inv.
Bhadla | July | SCB.21.01 | String fault | 179.2 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 22.2411 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.02 | String fault | 179.2 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 22.2411 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.07 | String fault | 192 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 23.8298 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.10 | String fault | 166.4 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 20.6525 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.12 | String fault | 179.2 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 22.2411 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.16 | String fault | 179.2 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 22.2411 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.17 | String fault | 204.8 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 25.4184 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.21.18 | String fault | 179.2 | 44768 | 0.69653 | 44768 | 0.80208 | 2.5333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16108 | 0.7705 | 22.2411 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 11 | RISO fault | 3379.2 | 44768 | 0.69444 | 44768 | 0.72986 | 0.85 | Inverter Tripped in Riso Fault | 0.06659 | 0.7705 | 173.3795 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 23 | RISO fault | 3456 | 44768 | 0.63264 | 44768 | 0.76875 | 3.2667 | Inverter Tripped in Riso Fault | 0.17764 | 0.7705 | 473.0187 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 16 | RISO fault | 3411.2 | 44768 | 0.69028 | 44768 | 0.75417 | 1.5333 | Inverter Tripped in Riso Fault | 0.11967 | 0.7705 | 314.5257 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 26 | RISO fault | 3494.4 | 44768 | 0.68472 | 44768 | 0.76181 | 1.85 | Inverter Tripped in Riso Fault | 0.136 | 0.7705 | 366.1686 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 14 | RISO fault | 3430.4 | 44768 | 0.70278 | 44768 | 0.74792 | 1.0833 | Inverter Tripped in Riso Fault | 0.092219 | 0.7705 | 243.7454 | Fault not rectified due to continious raining at site.
Bhadla | July | Inverter 24 | RISO fault | 3392 | 44768 | 0.66875 | 44768 | 0.70347 | 0.83333 | Inverter Tripped in Riso Fault | 0.045205 | 0.7705 | 118.1449 | Fault not rectified due to continious raining at site.
Bhadla | July | SCB.01.06 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.48125 | 5.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.5264 | 0.82156 | 83.0333 | Yesterday Breakdown resumes.
Bhadla | July | SCB.01.09 | String fault | 153.6 | 44769 | 0.25486 | 44769 | 0.48125 | 5.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.5264 | 0.82156 | 66.4266 | Yesterday Breakdown resumes.
Bhadla | July | SCB.01.10 | String fault | 185.6 | 44769 | 0.25486 | 44769 | 0.36944 | 2.75 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.15671 | 0.82156 | 23.8951 | Yesterday Breakdown resumes.
Bhadla | July | SCB.01.11 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.36944 | 2.75 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.15671 | 0.82156 | 24.7191 | Yesterday Breakdown resumes.
Bhadla | July | SCB.01.18 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.36944 | 2.75 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.15671 | 0.82156 | 21.4232 | Yesterday Breakdown resumes.
Bhadla | July | Inverter 09 | RISO fault | 3424 | 44769 | 0.25486 | 44769 | 0.31875 | 1.5333 | Inverter Tripped in Riso Fault | 0.034933 | 0.82156 | 98.2672 | DC Floating checked keeping below mentioned SCB off thenm start the Inv.
Bhadla | July | SCB.09.04 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.44653 | 4.6 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.45186 | 0.82156 | 61.7725 | Again checked found ok
Bhadla | July | SCB.09.05 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.06 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.07 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.11 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.47847 | 5.3667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.50005 | 0.82156 | 73.6186 | St-12 Isolated then Start the SCB
Bhadla | July | SCB.09.11 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-12 found abnormal floating | 0.9753 | 0.82156 | 10.2562 | (-Ve) Y-connector Replaced with new One.
Bhadla | July | SCB.09.12 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.13 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.14 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.15 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.16 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.44792 | 4.6333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.45317 | 0.82156 | 61.9513 | Again checked found ok
Bhadla | July | SCB.09.17 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.47847 | 5.3667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.51962 | 0.82156 | 71.0355 | St-2,10,13,15,& 16 Isolated then start the SCB
Bhadla | July | SCB.09.17 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-2 found abnormal Floating | 0.9753 | 0.82156 | 10.2562 | Again checked found ok
Bhadla | July | SCB.09.17 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-10 found abnormal Floating | 0.9753 | 0.82156 | 10.2562 | Again checked found ok
Bhadla | July | SCB.09.17 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-13 found abnormal Floating | 0.9753 | 0.82156 | 10.2562 | Again checked found ok
Bhadla | July | SCB.09.17 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-15 found abnormal Floating | 0.9753 | 0.82156 | 10.2562 | Again checked found ok
Bhadla | July | SCB.09.17 | String fault | 12.8 | 44769 | 0.47847 | 44769 | 0.66667 | 4.5167 | St-16 found abnormal Floating | 0.9753 | 0.82156 | 10.2562 | Again checked found ok
Bhadla | July | SCB.09.18 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.09.19 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39236 | 3.3 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.24308 | 0.82156 | 33.2306 | Again checked found ok
Bhadla | July | SCB.14.01 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 30.1019 | Again checked found ok
Bhadla | July | SCB.14.03 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.48819 | 5.6 | Found DC Floating abnormal during fault attend | 0.54326 | 0.82156 | 74.2679 | Again checked found ok
Bhadla | July | SCB.14.07 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 30.1019 | Again checked found ok
Bhadla | July | SCB.14.07 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 30.1019 | Again checked found ok
Bhadla | July | SCB.14.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 30.1019 | Again checked found ok
Bhadla | July | SCB.14.09 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 34.733 | Again checked found ok
Bhadla | July | SCB.14.10 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.3875 | 3.1833 | Found DC Floating abnormal during fault attend | 0.22019 | 0.82156 | 34.733 | Again checked found ok
Bhadla | July | SCB.14.13 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.50417 | 5.9833 | Found DC Floating abnormal during fault attend | 0.58652 | 0.82156 | 86.3489 | Again checked found ok
Bhadla | July | SCB.14.19 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.46042 | 4.9333 | Found DC Floating abnormal during fault attend | 0.47371 | 0.82156 | 64.7591 | Again checked found ok
Bhadla | July | SCB.16.04 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.38264 | 3.0667 | Found DC Floating abnormal during fault attend | 0.19342 | 0.82156 | 28.4756 | Again checked found ok
Bhadla | July | SCB.16.05 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.38264 | 3.0667 | Found DC Floating abnormal during fault attend | 0.19342 | 0.82156 | 26.4417 | Again checked found ok
Bhadla | July | SCB.16.06 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.38264 | 3.0667 | Found DC Floating abnormal during fault attend | 0.19342 | 0.82156 | 26.4417 | Again checked found ok
Bhadla | July | SCB.16.07 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.38264 | 3.0667 | Found DC Floating abnormal during fault attend | 0.19342 | 0.82156 | 26.4417 | Again checked found ok
Bhadla | July | SCB.16.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.45694 | 4.85 | Found DC Floating abnormal during fault attend | 0.46693 | 0.82156 | 63.8322 | Again checked found ok
Bhadla | July | SCB.16.10 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.45694 | 4.85 | Found DC Floating abnormal during fault attend | 0.46693 | 0.82156 | 68.7423 | Again checked found ok
Bhadla | July | SCB.16.14 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.45694 | 4.85 | Found DC Floating abnormal during fault attend | 0.46693 | 0.82156 | 68.7423 | Again checked found ok
Bhadla | July | SCB.21.01 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.51944 | 6.35 | Found DC Floating abnormal during fault attend | 0.63149 | 0.82156 | 92.9708 | Again checked found ok
Bhadla | July | SCB.21.02 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.45278 | 4.75 | Found DC Floating abnormal during fault attend | 0.46009 | 0.82156 | 67.7363 | Again checked found ok
Bhadla | July | SCB.21.04 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.45278 | 4.75 | Found DC Floating abnormal during fault attend | 0.46009 | 0.82156 | 62.898 | Again checked found ok
Bhadla | July | SCB.21.07 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.45278 | 4.75 | Found DC Floating abnormal during fault attend | 0.46009 | 0.82156 | 72.5746 | Again checked found ok
Bhadla | July | SCB.21.10 | String fault | 140.8 | 44769 | 0.25486 | 44769 | 0.45278 | 4.75 | Found DC Floating abnormal during fault attend | 0.46009 | 0.82156 | 53.2214 | Again checked found ok
Bhadla | July | SCB.21.12 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.45278 | 4.75 | Found DC Floating abnormal during fault attend | 0.46009 | 0.82156 | 67.7363 | Again checked found ok
Bhadla | July | SCB.21.16 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.37847 | 2.9667 | Found DC Floating abnormal during fault attend | 0.17779 | 0.82156 | 26.1753 | Again checked found ok
Bhadla | July | SCB.21.17 | String fault | 153.5 | 44769 | 0.25486 | 44769 | 0.37847 | 2.9667 | Found DC Floating abnormal during fault attend | 0.17779 | 0.82156 | 22.4214 | Again checked found ok
Bhadla | July | SCB.21.18 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.37847 | 2.9667 | Found DC Floating abnormal during fault attend | 0.17779 | 0.82156 | 24.3056 | Again checked found ok
Bhadla | July | SCB.23.02 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 111.8996 | Again checked found ok
Bhadla | July | SCB.23.04 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 104.4396 | Again checked found ok
Bhadla | July | SCB.23.06 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 111.8996 | Again checked found ok
Bhadla | July | SCB.23.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 96.9797 | Again checked found ok
Bhadla | July | SCB.23.13 | String fault | 192 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 111.8996 | Again checked found ok
Bhadla | July | SCB.23.14 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 104.4396 | Again checked found ok
Bhadla | July | SCB.23.15 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 96.9797 | Again checked found ok
Bhadla | July | SCB.23.19 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 104.4396 | Again checked found ok
Bhadla | July | SCB.23.20 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 96.9797 | Again checked found ok
Bhadla | July | SCB.24.04 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 96.9797 | Again checked found ok
Bhadla | July | SCB.24.07 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.44653 | 4.6 | Found DC Floating abnormal during fault attend | 0.45186 | 0.82156 | 61.7725 | Again checked found ok
Bhadla | July | SCB.24.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.37222 | 2.8167 | Found DC Floating abnormal during fault attend | 0.16251 | 0.82156 | 22.2159 | Again checked found ok
Bhadla | July | SCB.24.08 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.44722 | 4.6167 | Found DC Floating abnormal during fault attend | 0.4525 | 0.82156 | 61.8607 | Again checked found ok
Bhadla | July | SCB.24.19 | String fault | 140.8 | 44769 | 0.25486 | 44769 | 0.54583 | 6.9833 | Found DC Floating abnormal during fault attend | 0.7094 | 0.82156 | 82.0597 | Again checked found ok
Bhadla | July | Inverter 25 | RISO fault | 3468.8 | 44769 | 0.27639 | 44769 | 0.30208 | 0.61667 | Inverter Tripped in riso fault | 0.0176 | 0.82156 | 50.1555 | DC Floating Checked Keeping Mentioned SCB Off, then Start the Inv.
Bhadla | July | SCB.25.01 | String fault | 192 | 44769 | 0.30208 | 44769 | 0.39722 | 2.2833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.23794 | 0.82156 | 37.5319 | Again checked found ok
Bhadla | July | SCB.25.10 | String fault | 166.4 | 44769 | 0.30208 | 44769 | 0.39722 | 2.2833 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.23794 | 0.82156 | 32.5276 | Again checked found ok
Bhadla | July | SCB.25.20 | String fault | 179.2 | 44769 | 0.30208 | 44769 | 0.54583 | 5.85 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.68632 | 0.82156 | 101.0426 | Again checked found ok
Bhadla | July | SCB.26.05 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 38.8557 | Again checked found ok
Bhadla | July | SCB.26.06 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.54653 | 7 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.71116 | 0.82156 | 97.2213 | Again checked found ok
Bhadla | July | SCB.26.10 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 36.0803 | Again checked found ok
Bhadla | July | SCB.26.12 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 38.8557 | Again checked found ok
Bhadla | July | SCB.26.14 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 36.0803 | Again checked found ok
Bhadla | July | SCB.26.15 | String fault | 179.2 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 38.8557 | Again checked found ok
Bhadla | July | SCB.26.18 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 36.0803 | Again checked found ok
Bhadla | July | SCB.26.19 | String fault | 166.4 | 44769 | 0.25486 | 44769 | 0.39792 | 3.4333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26392 | 0.82156 | 36.0803 | Again checked found ok
Bhadla | July | Inverter 27 | RISO fault | 3404.8 | 44769 | 0.40417 | 44769 | 0.42708 | 0.55 | Inverter Tripped in Riso fault | 0.12457 | 0.82156 | 348.4645 | DC Floating checked nothing found any abnormal then start the Inv.
Bhadla | July | Inverter 27 | DSP comm. fault | 856.8 | 44769 | 0.42708 | 44769 | 0.80903 | 9.1667 | Unit-3 Breakdown in DSP Com Fault | 1.3421 | 0.82156 | 944.7501 | Discussed with SG team we kept off Unit-3 After generation Hr SG Team replaced LVRT in Unit-3.
Bhadla | July | Inverter 28 | RISO fault | 3379.2 | 44769 | 0.25486 | 44769 | 0.30972 | 1.3167 | Inverter Tripped in Riso fault | 0.028599 | 0.82156 | 79.3978 | DC Floating Checked Keeping Mentioned SCB Off, then Start the Inv.
Bhadla | July | SCB.28.03 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.40278 | 2.2333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26668 | 0.82156 | 36.4576 | Again checked found ok
Bhadla | July | SCB.28.04 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.57917 | 6.4667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.90367 | 0.82156 | 123.5378 | Again checked found ok
Bhadla | July | SCB.28.06 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.40278 | 2.2333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26668 | 0.82156 | 36.4576 | Again checked found ok
Bhadla | July | SCB.28.07 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.57917 | 6.4667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.90367 | 0.82156 | 123.5378 | Again checked found ok
Bhadla | July | SCB.28.08 | String fault | 192 | 44769 | 0.30972 | 44769 | 0.40278 | 2.2333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.26668 | 0.82156 | 42.0665 | Again checked found ok
Bhadla | July | SCB.28.12 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.57917 | 6.4667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.90367 | 0.82156 | 123.5378 | DC Floating Checked Keeping Mentioned SCB Off, then Start the Inv.
Bhadla | July | SCB.28.14 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.57917 | 6.4667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.90367 | 0.82156 | 123.5378 | St-3,4,5,6,9 & 12 Isolated then start the SCB
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-3 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | Again checked found ok
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-4 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | Again checked found ok
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-5 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | (+VE) Y-Connector Found Faulty. Same Replaced with new One.
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-6 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | Again checked found ok
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-9 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | Again checked found ok
Bhadla | July | SCB.28.14 | String fault | 12.8 | 44769 | 0.57917 | 44769 | 0.70208 | 2.95 | St-12 found abnormal floating | 0.67615 | 0.82156 | 7.1103 | Again checked found ok
Bhadla | July | SCB.28.18 | String fault | 166.4 | 44769 | 0.30972 | 44769 | 0.43542 | 3.0167 | Inverter Tripped in Riso fault | 0.41387 | 0.82156 | 56.5787 | DC Floating Checked Keeping Mentioned SCB Off, then Start the Inv.
Bhadla | July | Inverter 07 | RISO fault | 3495.8 | 44770 | 0.25486 | 44770 | 0.29375 | 0.93333 | Inverter Tripped in Riso fault | 0.024165 | 0.83503 | 70.5406 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 10 | RISO fault | 3404.8 | 44770 | 0.25486 | 44770 | 0.28264 | 0.66667 | Inverter Tripped in Riso fault | 0.0088622 | 0.83503 | 25.196 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 12 | DSP comm. fault | 857.6 | 44770 | 0.45833 | 44770 | 0.81181 | 8.4833 | Unit-4 Tripped in DSP Com Fault | 0.25452 | 0.83503 | 2629 | Discussed with SG team we kept off Unit-4 then restart the Inv.
Bhadla | July | SCB.12.11 | String fault | 179.2 | 44770 | 0.67153 | 44770 | 0.81181 | 3.3667 | SCB Manually Stopped | 0.85177 | 0.83503 | 127.4564
Bhadla | July | Inverter 15 | Ground fault | 3475.2 | 44770 | 0.54236 | 44770 | 0.54792 | 0.13333 | Inverter Tripped in Gnd Fault | 0.10517 | 0.83503 | 305.1965 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 16 | Ground fault | 3411.2 | 44770 | 0.50208 | 44770 | 0.50764 | 0.13333 | Inverter Tripped in Gnd Fault | 0.062165 | 0.83503 | 177.0741 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 17 | RISO fault | 3404.8 | 44770 | 0.25486 | 44770 | 0.30069 | 1.1 | Inverter Tripped in Riso Fault | 0.046158 | 0.83503 | 131.2315 | DC Floating checked fault found in 1A4 keeping that SCB off then start the Inv.
Bhadla | July | SCB.17.04 | String fault | 166.4 | 44770 | 0.30069 | 44770 | 0.325 | 0.58333 | Manually stopped as found abnormal floating | 0.11018 | 0.83503 | 15.3089 | Again checked found Ok.
Bhadla | July | Inverter 19 | Ground fault | 3520 | 44770 | 0.54861 | 44770 | 0.55417 | 0.13333 | Inverter Tripped in Gnd Fault | 0.096689 | 0.83503 | 284.1964 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 20 | Ground fault | 3507.4 | 44770 | 0.59722 | 44770 | 0.60278 | 0.13333 | Inverter Tripped in Gnd Fault | 0.074499 | 0.83503 | 218.1917 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44770 | 0.41667 | 44770 | 0.43681 | 0.48333 | Inverter Tripped in Gnd Fault | 0.17798 | 0.83503 | 519.3339 | DC Floating checked keeping below SCB off then start the Inv.
Bhadla | July | SCB.21.06 | String fault | 179.2 | 44770 | 0.43681 | 44770 | 0.46736 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.30208 | 0.83503 | 45.2017 | Again checked found Ok.
Bhadla | July | SCB.21.07 | String fault | 192 | 44770 | 0.43681 | 44770 | 0.46736 | 0.73333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.30208 | 0.83503 | 48.4304 | St-2,8 & 13 Isolated then start the SCB
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44770 | 0.46736 | 44770 | 0.50625 | 0.93333 | St-2 found abnormal Floating | 0.37927 | 0.83503 | 4.0538 | (+VE) Y-Connector Found Faulty. Same Replaced with new One.
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44770 | 0.46736 | 44770 | 0.50625 | 0.93333 | St-8 found abnormal Floating | 0.37927 | 0.83503 | 4.0538 | (-VE) Y-Connector Found Faulty. Same Replaced with new One.
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44770 | 0.46736 | 44770 | 0.50625 | 0.93333 | St-13 found abnormal Floating | 0.37927 | 0.83503 | 4.0538 | (+VE) Y-Connector Found Faulty. Same Replaced with new One.
Bhadla | July | SCB.21.08 | String fault | 179.2 | 44770 | 0.43681 | 44770 | 0.46736 | 0.73333 | Manually stopped as found abnormal floating | 0.30208 | 0.83503 | 45.2017 | Again checked found Ok.
Bhadla | July | SCB.21.09 | String fault | 166.4 | 44770 | 0.43681 | 44770 | 0.46736 | 0.73333 | Manually stopped as found abnormal floating | 0.30208 | 0.83503 | 41.973 | Again checked found Ok.
Bhadla | July | SCB.21.10 | String fault | 166.4 | 44770 | 0.43681 | 44770 | 0.46736 | 0.73333 | Manually stopped as found abnormal floating | 0.30208 | 0.83503 | 41.973 | St-6 isolated then start the SCB
Bhadla | July | SCB.21.10 | String fault | 12.8 | 44770 | 0.46736 | 44770 | 0.64583 | 4.2833 | St-6 found abnormal floating | 2.2167 | 0.83503 | 23.6929 | Again checked found ok.
Bhadla | July | Inverter 21 | Ground fault | 3494.4 | 44770 | 0.46806 | 44770 | 0.475 | 0.16667 | Again Inverter Tripped in Gnd Fault | 0.071103 | 0.83503 | 207.4713 | DC Floating checked fault found in SCB 1B2 off then start the Inv.
Bhadla | July | SCB.21.07 | String fault | 192 | 44770 | 0.475 | 44770 | 0.50903 | 0.81667 | Manually stopped as found abnormal floating | 0.33009 | 0.83503 | 52.9215 | Again checked found ok.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44770 | 0.31597 | 44770 | 0.34514 | 0.7 | Inverter Tripped in Gnd Fault | 0.1313 | 0.83503 | 380.3291 | DC Floating Checked nothing found Abnormal then Start the SCB.
Bhadla | July | Inverter 25 | Ground fault | 3468.8 | 44770 | 0.47639 | 44770 | 0.49653 | 0.48333 | Inverter Tripped in Gnd Fault | 0.20199 | 0.83503 | 585.0668 | DC Floating checked fault found in SCB 1B3 & 1B4 off then start the Inv.
Bhadla | July | SCB.25.08 | String fault | 166.4 | 44770 | 0.49653 | 44770 | 0.52083 | 0.58333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.27098 | 0.83503 | 37.6527 | Again checked found ok.
Bhadla | July | SCB.25.09 | String fault | 166.4 | 44770 | 0.49653 | 44770 | 0.52083 | 0.58333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.27098 | 0.83503 | 37.6527 | St-8 Isolated then Start the SCB
Bhadla | July | SCB.25.09 | String fault | 12.8 | 44770 | 0.52083 | 44770 | 0.6875 | 4 | St-8 found abnormal Floating | 2.1098 | 0.83503 | 22.5506 | found (-Ve) String cable faulty 15mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.01.14 | String fault | 12.8 | 44770 | 0.25486 | 44770 | 0.53472 | 6.7167 | ST-11 found Abnormal Floating | 1.9382 | 0.83503 | 20.7166 | found (-Ve) String cable faulty 36mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.08.08 | String fault | 12.8 | 44770 | 0.25486 | 44770 | 0.55556 | 7.2167 | ST-11 found Abnormal Floating | 2.2868 | 0.83503 | 24.4423 | found (-Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.08.08 | String fault | 12.8 | 44770 | 0.25486 | 44770 | 0.59306 | 8.1167 | ST-8 found Abnormal Floating | 2.8481 | 0.83503 | 30.4417 | found (-Ve) String cable faulty 20mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.10.19 | String fault | 12.8 | 44770 | 0.25486 | 44770 | 0.69792 | 10.6333 | ST-1 found Abnormal Floating | 3.8931 | 0.83503 | 41.6112 | found 30A fuse faulty same replaced with new one.
Bhadla | July | Inverter 25 | RISO fault | 3468.8 | 44771 | 0.25556 | 44771 | 0.31736 | 1.4833 | Inverter Tripped in Riso Fault | 0.084697 | 0.78262 | 229.9311 | DC Floating checked and Mentioned below SCB off then Start the Inv
Bhadla | July | SCB.25.16 | String fault | 166.4 | 44771 | 0.31736 | 44771 | 0.35347 | 0.86667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.20627 | 0.78262 | 26.8617 | Again checked found ok.
Bhadla | July | SCB.25.17 | String fault | 166.4 | 44771 | 0.31736 | 44771 | 0.34931 | 0.76667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16676 | 0.78262 | 21.7172 | Again checked found ok.
Bhadla | July | SCB.25.18 | String fault | 192 | 44771 | 0.31736 | 44771 | 0.34931 | 0.76667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16676 | 0.78262 | 25.0583 | Again checked found ok.
Bhadla | July | SCB.25.19 | String fault | 166.4 | 44771 | 0.31736 | 44771 | 0.34931 | 0.76667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16676 | 0.78262 | 21.7172 | Again checked found ok.
Bhadla | July | SCB.25.20 | String fault | 179.2 | 44771 | 0.31736 | 44771 | 0.34931 | 0.76667 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.16676 | 0.78262 | 23.3877 | Again checked found ok.
Bhadla | July | SCB.20.12 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.48958 | 5.6167 | St-9 found abnormal floating | 2.4578 | 0.78262 | 24.6209 | found (-Ve) String cable faulty 18mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.21.08 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.52083 | 6.3667 | St-2 found abnormal floating | 3.1632 | 0.78262 | 31.6874 | found (-Ve) String cable faulty 18mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.21.10 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.53472 | 6.7 | St-6 found abnormal floating | 3.428 | 0.78262 | 34.3397 | Again checked found ok.
Bhadla | July | SCB.21.10 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.56944 | 7.5333 | St-11 found abnormal floating | 4.2119 | 0.78262 | 42.1931 | Again checked found ok.
Bhadla | July | SCB.21.10 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.64583 | 9.3667 | St-12 found abnormal floating | 5.6252 | 0.78262 | 56.3502 | found (-Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.65625 | 9.6167 | St-2 found abnormal floating | 5.8172 | 0.78262 | 58.2733 | Found (+ve) Y-Connector Damage same replaced with new one.
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.67708 | 10.1167 | St-8 found abnormal floating | 6.0995 | 0.78262 | 61.102 | Found (-ve) Y-Connector Damage same replaced with new one.
Bhadla | July | SCB.21.07 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.69444 | 10.5333 | St-13 found abnormal floating | 6.3072 | 0.78262 | 63.1827 | Found (-ve) Y-Connector Damage same replaced with new one.
Bhadla | July | SCB.23.19 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.72222 | 11.2 | St-3 found abnormal floating | 6.5686 | 0.78262 | 65.8004 | found string cable punctured on purlin 1set Mc4 connector used.
Bhadla | July | SCB.28.04 | String fault | 12.8 | 44771 | 0.25556 | 44771 | 0.73264 | 11.45 | St-1 found abnormal floating | 6.6072 | 0.78262 | 66.1876 | Found (-ve) Y-Connector Damage same replaced with new one.
Bhadla | July | Inverter 05 | RISO fault | 3476 | 44772 | 0.25486 | 44772 | 0.28264 | 0.66667 | Inverter Tripped in riso Fault | 0.013954 | 0.78366 | 38.0119 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | July | SCB.05.04 | String fault | 179.2 | 44772 | 0.28264 | 44772 | 0.29444 | 0.28333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.014169 | 0.78366 | 1.9898 | ST-6 isolated then start the SCB
Bhadla | July | SCB.23.09 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.47917 | 5.3833 | ST-14 found abnormal floating during suspected SCB Check | 2.0672 | 0.78366 | 20.7361 | found (-Ve) String cable faulty 28mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.23.08 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.50347 | 5.9667 | ST-1 found abnormal floating during suspected SCB Check | 2.5771 | 0.78366 | 25.8508 | found (+Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.23.08 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.51389 | 6.2167 | ST-12 found abnormal floating during suspected SCB Check | 2.8178 | 0.78366 | 28.2644 | found (-Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.26.06 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.53472 | 6.7167 | ST-12 found abnormal floating during suspected SCB Check | 3.2208 | 0.78366 | 32.3071 | found (-Ve) String cable faulty 28mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.27.12 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.64583 | 9.3833 | ST-12 found abnormal floating during suspected SCB Check | 5.1216 | 0.78366 | 51.3739 | found (-Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.03.04 | String fault | 12.8 | 44772 | 0.29444 | 44772 | 0.67708 | 9.1833 | ST-6 found abnormal floating. | 5.7655 | 0.78366 | 57.8329 | found (-Ve) String cable faulty 20mtr cable & 2 set Mc4 connector used.
Bhadla | July | SCB.08.03 | String fault | 12.8 | 44772 | 0.25486 | 44772 | 0.69792 | 10.6333 | ST-8 found abnormal floating during suspected SCB Check | 6.0396 | 0.78366 | 60.5817 | found (+Ve) String cable faulty 18mtr cable & 2 set Mc4 connector used.
Bhadla | August | SCB.15.12 | String fault | 12.8 | 44775 | 0.37778 | 44775 | 0.40833 | 0.73333 | ST-12 found abnormal floating during suspected SCB Check | 0.38065 | 0.77832 | 3.7923 | found (+Ve) String cable faulty 35mtr cable & 2 set Mc4 connector used.
Bhadla | August | SCB.15.12 | String fault | 12.8 | 44775 | 0.37778 | 44775 | 0.45278 | 1.8 | ST-12 found abnormal floating during suspected SCB Check | 1.0185 | 0.77832 | 10.1469 | found (+Ve) String cable faulty 35mtr cable & 2 set Mc4 connector used.
Bhadla | August | SCB.5.04 | String fault | 12.8 | 44775 | 0.37778 | 44775 | 0.45 | 1.7333 | ST-4 found abnormal floating during suspected SCB Check | 0.96259 | 0.77832 | 9.5898 | found (+Ve)&(-Ve) String cable faulty 20mtr cable & 3 set Mc4 connector used.
Bhadla | August | SCB.07.14 | String fault | 12.8 | 44775 | 0.37778 | 44775 | 0.53125 | 3.6833 | ST-14 found abnormal floating during suspected SCB Check | 2.6893 | 0.77832 | 26.7918 | found (+Ve)&(-Ve) String cable faulty 84mtr cable & 3 set Mc4 connector used.
Bhadla | August | SCB.10.01 | String fault | 12.8 | 44775 | 0.425 | 44775 | 0.48194 | 1.3667 | ST-1 found abnormal floating during suspected SCB Check | 1.0514 | 0.77832 | 10.4744 | found (+Ve) Y- Connector And 2 Nos 15amp fuse used.
Bhadla | August | SCB.03.07 | String fault | 12.8 | 44775 | 0.425 | 44775 | 0.51042 | 2.05 | ST-7 found abnormal floating during suspected SCB Check | 1.6536 | 0.77832 | 16.4737 | found (-Ve) Y- Connector used.
Bhadla | August | SCB.09.08 | String fault | 12.8 | 44775 | 0.61667 | 44775 | 0.65486 | 0.91667 | ST-8 found abnormal floating during suspected SCB Check | 0.6345 | 0.77832 | 6.3212 | found (-Ve) Y- Connector used.
Bhadla | August | SCB.07.11 | String fault | 12.8 | 44775 | 0.61667 | 44775 | 0.68056 | 1.5333 | ST-11 found abnormal floating during suspected SCB Check | 0.98125 | 0.77832 | 9.7757 | found (+Ve) String cable faulty 20mtr cable & 2 set Mc4 connector used.
Bhadla | August | SCB.08.1 | String fault | 12.8 | 44776 | 0.25694 | 44776 | 0.45 | 4.6333 | ST-1 found abnormal floating during suspected SCB Check | 1.7177 | 0.7684 | 16.8949 | found (-Ve) String cable faulty 10mtr cable & 2 set Mc4 connector used.
Bhadla | August | SCB.18.12 | String fault | 12.8 | 44776 | 0.25694 | 44776 | 0.47222 | 5.1667 | ST-12 found abnormal floating during suspected SCB Check | 2.1677 | 0.7684 | 21.3207 | found (+Ve) Y- Connector And 2nos 15Amp Fuse used.
Bhadla | August | SCB.18.08 | String fault | 6.4 | 44776 | 0.25694 | 44776 | 0.43611 | 4.3 | ST-08 Half String found abnormal floating during suspected SCB Check | 1.4578 | 0.7684 | 7.1692 | 1nos 15Amp Fuse used.
Bhadla | August | Inverter 07 | RISO fault | 3495.8 | 44778 | 0.2625 | 44778 | 0.29653 | 0.81667 | Inverter Tripped in riso Fault | 0.021593 | 0.78507 | 59.2601 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 10 | RISO fault | 3404.8 | 44778 | 0.2625 | 44778 | 0.30278 | 0.96667 | Inverter Tripped in riso Fault | 0.032084 | 0.78507 | 85.7611 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 24 | RISO fault | 3392 | 44778 | 0.2625 | 44778 | 0.30139 | 0.93333 | Inverter Tripped in riso Fault | 0.029679 | 0.78507 | 79.0339 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 10 | RISO fault | 3404.8 | 44781 | 0.25764 | 44781 | 0.30278 | 1.0833 | Inverter Tripped in riso Fault | 0.052147 | 0.78072 | 138.6177 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 03 | RISO fault | 3450.4 | 44782 | 0.26042 | 44782 | 0.29167 | 0.75 | Inverter Tripped in riso Fault | 0.023002 | 0.7727 | 61.3275 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 16 | RISO fault | 3411.2 | 44782 | 0.26042 | 44782 | 0.29861 | 0.91667 | Inverter Tripped in riso Fault | 0.036118 | 0.7727 | 95.2011 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 25 | RISO fault | 3468.8 | 44782 | 0.26042 | 44782 | 0.28681 | 0.63333 | Inverter Tripped in riso Fault | 0.015958 | 0.7727 | 42.7724 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | All Inverters | Wave trap jumper flashover | 96560.1 | 44782 | 0.58333 | 44782 | 0.73403 | 3.6167 | Line Breaker Manually Tripped due to Wave Trap Jumper Flashover. | 2.3417 | 0.7727 | 174720.1388 | Visually Checked All Equipments, then replaced the conductor in wavetrap, Tightness done properly. presence of our HT Expert Mr. Vijayan Sir Then Charged the Line Breaker.
Bhadla | August | Inverter 02 | RISO fault | 3469.9 | 44783 | 0.25764 | 44783 | 0.27083 | 0.31667 | Inverter Tripped in riso Fault | 0.0035533 | 0.7627 | 9.4039 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 03 | RISO fault | 3450.4 | 44783 | 0.25764 | 44783 | 0.28056 | 0.55 | Inverter Tripped in riso Fault | 0.010849 | 0.7627 | 28.5514 | DC Floating checked fault found in 1B2, 1B5, 1C4 & 1C5 keeping those SCB off then start the Inv.
Bhadla | August | SCB.03.07 | String fault | 166.4 | 44783 | 0.28125 | 44783 | 0.36181 | 1.9333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.41875 | 0.7627 | 53.1446 | Again checked found Ok
Bhadla | August | SCB.03.10 | String fault | 166.4 | 44783 | 0.28125 | 44783 | 0.36181 | 1.9333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.41875 | 0.7627 | 53.1446 | Again checked found Ok
Bhadla | August | SCB.03.14 | String fault | 166.4 | 44783 | 0.28125 | 44783 | 0.36181 | 1.9333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.41875 | 0.7627 | 53.1446 | Again checked found Ok
Bhadla | August | SCB.03.15 | String fault | 166.4 | 44783 | 0.28125 | 44783 | 0.36181 | 1.9333 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.41875 | 0.7627 | 53.1446 | Again checked found Ok
Bhadla | August | Inverter 04 | RISO fault | 3470.2 | 44783 | 0.25764 | 44783 | 0.27986 | 0.53333 | Inverter Tripped in riso Fault | 0.010146 | 0.7627 | 26.855 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 06 | RISO fault | 3450.7 | 44783 | 0.25764 | 44783 | 0.2875 | 0.71667 | Inverter Tripped in riso Fault | 0.019718 | 0.7627 | 51.8945 | DC Floating checked fault found in 2A2 & 2A5 keeping those SCB off , then Start the Inv.
Bhadla | August | SCB.06.02 | String fault | 166.4 | 44783 | 0.28819 | 44783 | 0.36806 | 1.9167 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.47475 | 0.7627 | 60.2525 | Again checked found Ok
Bhadla | August | SCB.06.05 | String fault | 166.4 | 44783 | 0.28819 | 44783 | 0.36806 | 1.9167 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.47475 | 0.7627 | 60.2525 | Again checked found Ok
Bhadla | August | Inverter 21 | RISO fault | 3494.4 | 44783 | 0.25764 | 44783 | 0.29514 | 0.9 | Inverter Tripped in riso Fault | 0.033259 | 0.7627 | 88.6415 | DC Floating checked fault found in 1C4 keeping that SCB off , then Start the Inv.
Bhadla | August | SCB.21.14 | String fault | 166.4 | 44783 | 0.29583 | 44783 | 0.37083 | 1.8 | Manually Stopped as found Abnormal Floating During INV Riso fault attend | 0.49175 | 0.7627 | 62.4103 | Again checked found Ok
Bhadla | August | Inverter 26 | RISO fault | 3494.4 | 44783 | 0.29653 | 44783 | 0.30347 | 0.16667 | Inverter Tripped in riso Fault | 0.020144 | 0.7627 | 53.6867 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter 26 | RISO fault | 3494.4 | 44783 | 0.31667 | 44783 | 0.32986 | 0.31667 | Inverter Tripped in riso Fault | 0.072854 | 0.7627 | 194.17 | DC Floating Checked nothing found abnormal then Start the Inv.
Bhadla | August | Inverter-1, 2, 6, 9, 11, 12, 13, 20, 24 & 25 | Grid voltage issue | 34397.9 | 44784 | 0.475 | 44784 | 0.47847 | 0.083333 | Inverter-1, 2, 6, 9, 11, 12, 13, 20, 24, 25 Tripped due to Over voltage in Line. | 0.083925 | 0.77625 | 2240.917 | Inverters resumes after Grid voltage normalised.
Bhadla | August | Inverter 13 | RISO fault | 3411.2 | 44786 | 0.27708 | 44786 | 0.39167 | 2.75 | Inverter Tripped in riso Fault | 0.12979 | 0.83683 | 370.5116 | DC Floating checked mentioned below SCB's Off then start the Inv.
Bhadla | August | SCB.13.05 | String fault | 179.2 | 44786 | 0.39236 | 44786 | 0.48264 | 2.1667 | Manually stopped as found abnormal floating | 0.56935 | 0.83683 | 85.3802 | Again checked found Ok.
Bhadla | August | SCB.13.06 | String fault | 192 | 44786 | 0.39236 | 44786 | 0.48264 | 2.1667 | Manually stopped as found abnormal floating | 0.56935 | 0.83683 | 91.4788 | Again checked found Ok.
Bhadla | August | SCB.13.13 | String fault | 166.4 | 44786 | 0.39236 | 44786 | 0.49514 | 2.4667 | Manually stopped as found abnormal floating | 0.67707 | 0.83683 | 94.2814 | Again checked found Ok.
Bhadla | August | SCB.13.14 | String fault | 166.4 | 44786 | 0.39236 | 44786 | 0.48264 | 2.1667 | Manually stopped as found abnormal floating | 0.56935 | 0.83683 | 79.2816 | Again checked found Ok.
Bhadla | August | SCB.13.15 | String fault | 166.4 | 44786 | 0.39236 | 44786 | 0.48264 | 2.1667 | Manually stopped as found abnormal floating | 0.56935 | 0.83683 | 79.2816 | Again checked found Ok.
Bhadla | August | SCB.13.16 | String fault | 166.4 | 44786 | 0.39236 | 44786 | 0.48264 | 2.1667 | Manually stopped as found abnormal floating | 0.56935 | 0.83683 | 79.2816 | Again checked found Ok.
Bhadla | August | Inverter 23 | RISO fault | 3456 | 44786 | 0.27708 | 44786 | 0.35556 | 1.8833 | Inverter Tripped in riso Fault | 0.042195 | 0.83683 | 122.0321 | Auto-Restarted
Bhadla | August | Inverter 26 | RISO fault | 3494.4 | 44786 | 0.34861 | 44786 | 0.36597 | 0.41667 | Inverter Tripped in riso Fault | 0.024357 | 0.83683 | 71.2253 | Auto-Restarted
Bhadla | August | Inverter 26 | RISO fault | 3494.4 | 44786 | 0.41806 | 44786 | 0.43333 | 0.36667 | Again Inverter Tripped in riso fault | 0.094162 | 0.83683 | 275.3496 | DC Floating Checked Fault Found in 2C4 keeping that SCB off , then Start the Inv.
Bhadla | August | SCB.26.14 | String fault | 166.4 | 44786 | 0.43403 | 44786 | 0.52222 | 2.1167 | manually stopped as found abnormal floating | 0.85795 | 0.83683 | 119.4679 | Again checked found ok.
Bhadla | August | Inverter 11 | RISO fault | 3379.2 | 44786 | 0.44306 | 44786 | 0.45139 | 0.2 | Inverter Tripped in riso Fault | 0.070788 | 0.83683 | 200.1747 | DC Floating checked fault found in 1A5 keeping that SCB off then start the Inv.
Bhadla | August | SCB.11.05 | String fault | 179.2 | 44786 | 0.45208 | 44786 | 0.50347 | 1.2333 | Manually stopped as found abnormal floating | 0.408 | 0.83683 | 61.1833 | ST-5 Isolated then Start the SCB
Bhadla | August | SCB.11.05 | String fault | 12.8 | 44786 | 0.50347 | 44786 | 0.79028 | 6.8833 | St-5 found abnormal floating | 0.9762 | 0.83683 | 10.4565 | String not rectified due to continious rain at site
Bhadla | August | Inverter 06 | RISO fault | 3450.7 | 44788 | 0.26181 | 44788 | 0.28958 | 0.66667 | Inverter Tripped in Riso Fault | 0.010758 | 0.82979 | 30.8045 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | August | Inverter 10 | RISO fault | 3404.8 | 44788 | 0.26181 | 44788 | 0.28958 | 0.66667 | Inverter Tripped in Riso Fault | 0.010758 | 0.82979 | 30.3947 | Auto-Restarted
Bhadla | August | Inverter 14 | RISO fault | 3430.4 | 44788 | 0.26181 | 44788 | 0.28958 | 0.66667 | Inverter Tripped in Riso Fault | 0.010758 | 0.82979 | 30.6232 | Auto-Restarted
Bhadla | August | Inverter 27 | RISO fault | 3404.8 | 44788 | 0.26181 | 44788 | 0.28958 | 0.66667 | Inverter Tripped in Riso Fault | 0.010758 | 0.82979 | 30.3947 | Auto-Restarted
Bhadla | August | Inverter 06 | RISO fault | 3450.7 | 44789 | 0.25972 | 44789 | 0.27431 | 0.35 | Inverter Tripped in Riso Fault | 0.0034675 | 0.78849 | 9.4346 | Auto-Restarted
Bhadla | August | Inverter 07 | RISO fault | 3495.8 | 44789 | 0.25972 | 44789 | 0.27431 | 0.35 | Inverter Tripped in Riso Fault | 0.0034675 | 0.78849 | 9.5579 | Auto-Restarted
Bhadla | August | Inverter 10 | RISO fault | 3404.8 | 44789 | 0.25972 | 44789 | 0.28819 | 0.68333 | Inverter Tripped in Riso Fault | 0.011502 | 0.78849 | 30.879 | Auto-Restarted
Bhadla | August | Inverter 01 | DSP comm. fault | 870.4 | 44790 | 0.64306 | 44790 | 0.8 | 3.7667 | Unit-3 Tripped in DSP Com Fault | 0.1624 | 0.87333 | 631 | Discussed with SG Team then checked all parameters then to restart the Inmverter.
Bhadla | August | Inverter 02 | RISO fault | 3469.9 | 44790 | 0.27361 | 44790 | 0.29722 | 0.56667 | Inverter Tripped in Riso Fault | 0.015539 | 0.87333 | 47.0886 | DC Floating checked fault found in 2C1 & 2C2 keeping those SCB off then start the Inv.
Bhadla | August | SCB.02.11 | String fault | 185.6 | 44790 | 0.29792 | 44790 | 0.35764 | 1.4333 | Manually stopped as found abnormal floating | 0.10112 | 0.87333 | 16.3906 | ST-12 & 13 Isolated then Start the SCB
Bhadla | August | SCB.02.11 | String fault | 12.8 | 44790 | 0.35833 | 44790 | 0.55556 | 4.7333 | St-12 found abnormal Floating. | 1.0457 | 0.87333 | 11.6899 | Both (+ve) & (-ve) Cable 80mtr with 2 Set MC4 Connector used.
Bhadla | August | SCB.02.11 | String fault | 12.8 | 44790 | 0.35833 | 44790 | 0.49653 | 3.3167 | St-13 found abnormal Floating. | 0.89214 | 0.87333 | 9.9729 | (-ve) Cable 40mtr with 2 Set MC4 Connector used.
Bhadla | August | SCB.02.12 | String fault | 192 | 44790 | 0.29792 | 44790 | 0.35764 | 1.4333 | Manually stopped as found abnormal floating | 0.10112 | 0.87333 | 16.9557 | ST-13 Isolated then Start the SCB
Bhadla | August | SCB.02.12 | String fault | 12.8 | 44790 | 0.35833 | 44790 | 0.53125 | 4.15 | St-13 found abnormal Floating. | 1.0016 | 0.87333 | 11.196 | (-ve) Cable 40mtr with 2 Set MC4 Connector used.
Bhadla | August | Inverter 19 | DSP comm. fault | 3520 | 44790 | 0.68194 | 44790 | 0.8 | 2.8333 | Inverter Tripped in DSP Comm. Fault | 0.42802 | 0.87333 | 1315.7892 | Discussed with SG Team checked all parameters. Then restart the inverter inverter again Tripped. Then we interchanged master & Slave between Unit-1 & Unit-2 but issue not resolved.
Bhadla | August | Inverter 01 | RISO fault | 3451.5 | 44791 | 0.26042 | 44791 | 0.28889 | 0.68333 | Inverter tripped in Riso fault | 0.01181 | 0.8244 | 33.6028 | DC Floating Checked fault found in 1B4, 1C1, 1D1 & 1D4. keeping those SCB off then start the Inv.
Bhadla | August | SCB.01.09 | String fault | 153.6 | 44791 | 0.28958 | 44791 | 0.41458 | 3 | Manually stopped as found abnormal floating | 0.47166 | 0.8244 | 59.7248 | ST-3 Isolated then start the SCB
Bhadla | August | SCB.01.09 | String fault | 12.8 | 44791 | 0.41458 | 44791 | 0.47917 | 1.55 | St-3 found abnormal floating | 0.91753 | 0.8244 | 9.682 | Again checked found Ok
Bhadla | August | SCB.01.11 | String fault | 166.4 | 44791 | 0.28958 | 44791 | 0.41458 | 3 | Manually stopped as found abnormal floating | 0.47166 | 0.8244 | 64.7019 | Again checked found Ok
Bhadla | August | SCB.01.16 | String fault | 179.2 | 44791 | 0.28958 | 44791 | 0.41458 | 3 | Manually stopped as found abnormal floating | 0.47166 | 0.8244 | 69.679 | Again checked found Ok
Bhadla | August | SCB.01.19 | String fault | 166.4 | 44791 | 0.28958 | 44791 | 0.41458 | 3 | Manually stopped as found abnormal floating | 0.47166 | 0.8244 | 64.7019 | ST-12 Isolated then start the SCB
Bhadla | August | SCB.01.19 | String fault | 12.8 | 44791 | 0.41458 | 44791 | 0.53472 | 2.8833 | St-12 found abnormal Floating | 1.5685 | 0.8244 | 16.5513 | (-ve) Cable 35mtr with 2 Set MC4 Connector used.
Bhadla | August | SCB.19.18 | String fault | 12.8 | 44791 | 0.26042 | 44791 | 0.59722 | 8.0833 | St-14 found abnormal Floating | 2.7902 | 0.8244 | 29.4426 | both (+ve) & (-ve) Cable 120mtr with 2 Set MC4 Connector used.
Bhadla | August | Inverter 07 | RISO fault | 3495.8 | 44791 | 0.26042 | 44791 | 0.28819 | 0.66667 | Inverter Tripped in riso Fault | 0.011565 | 0.8244 | 33.328 | Auto-Restarted
Bhadla | August | Inverter 24 | DSP comm. fault | 870.4 | 44791 | 0.58333 | 44791 | 0.58542 | 0.05 | Unit-3 Tripped in DSP Com Fault | 0.05844 | 0.8244 | 41.9336 | Auto-Restarted
Bhadla | August | Inverter 24 | DSP comm. fault | 870.4 | 44791 | 0.63333 | 44791 | 0.6375 | 0.1 | Unit-3 Tripped in DSP Com Fault | 0.095924 | 0.8244 | 68.8304 | Auto-Restarted
Bhadla | August | Inverter 10 | RISO fault | 3404.8 | 44792 | 0.26042 | 44792 | 0.28333 | 0.55 | Inverter Tripped in Riso fault | 0.014577 | 0.79797 | 39.605 | Dc Floating checked nothing found abnormal then start the Inv.
Bhadla | August | Inverter 25 | DSP comm. fault | 857.6 | 44792 | 0.44514 | 44792 | 0.45764 | 0.3 | Unit-2 Tripped in DSP com Fault | 0.099782 | 0.79797 | 319 | Discussed with Sungrow Team as per his instructions we restart the Inverter.
Bhadla | August | Inverter 25 | DSP comm. fault | 857.6 | 44792 | 0.45833 | 44792 | 0.80069 | 8.2167 | Unit-2 Tripped in DSP com Fault | 4.2011 | 0.79797 | 2874.9754 | After restarted again Unit-2 Tripped. Then Unit-2 Q1 off as per SG Instructions.. After Generation Hr O&M team replaced LVRT in Unit-2.
Bhadla | August | Inverter 11 | DC injection fault | 3379.2 | 44794 | 0.58611 | 44794 | 0.59236 | 0.15 | Inverter Tripped in DC Injection Fault | 0.15025 | 0.78749 | 399.8224 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | August | Inverter 04 | RISO fault | 3470.2 | 44795 | 0.26319 | 44795 | 0.28681 | 0.56667 | Inverter tripped in Riso fault | 0.013383 | 0.77614 | 36.0441 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | August | Inverter 16 | RISO fault | 3411.2 | 44795 | 0.26319 | 44795 | 0.29375 | 0.73333 | Inverter tripped in Riso fault | 0.024255 | 0.77614 | 64.2184 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | August | Inverter 21 | RISO fault | 3494.4 | 44795 | 0.26319 | 44795 | 0.30208 | 0.93333 | Inverter tripped in Riso fault | 0.043153 | 0.77614 | 117.0377 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | August | SCB.03.14 | String fault | 12.8 | 44795 | 0.26319 | 44795 | 0.49306 | 5.5167 | St-11 Found Faulty during Suspected SCB Check. | 2.5538 | 0.77614 | 25.3714 | (+ve) Cable 18mtr with 2 Set MC4 Connector used.
Bhadla | August | SCB.06.07 | String fault | 6.4 | 44795 | 0.26319 | 44795 | 0.52778 | 6.35 | St-12 Found Faulty during Suspected SCB Check. | 3.0753 | 0.77614 | 15.2761 | Found 15Amp fuse faulty same replaced with new one.
Bhadla | August | SCB.27.20 | String fault | 12.8 | 44795 | 0.26319 | 44795 | 0.65278 | 9.35 | St-8 Found Faulty during Suspected SCB Check. | 5.4995 | 0.77614 | 54.6357 | (-ve) Cable 20mtr with 2 Set MC4 Connector used.
Bhadla | September | Inverter 09 | Ground fault | 3424 | 44806 | 0.65139 | 44806 | 0.67569 | 0.58333 | Inveter Tripped in Gnd Fault | 0.3088 | 0.79608 | 841.7265 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | September | SCB.08.17 | String fault | 12.8 | 44807 | 0.26528 | 44807 | 0.64583 | 9.1333 | St-1 Found Faulty during Suspected SCB Check. | 6.0793 | 0.77683 | 60.4488 | both (+ve) & (-ve) Cable 100mtr with 4 Set MC4 Connector used.
Bhadla | September | SCB.05.01 | String fault | 12.8 | 44807 | 0.26528 | 44807 | 0.53472 | 6.4667 | St-10 Found Faulty during Suspected SCB Check. | 3.6977 | 0.77683 | 36.7681 | found MC4 Connector damage same replaced with new one.
Bhadla | September | SCB.17.13 | String fault | 12.8 | 44807 | 0.26528 | 44807 | 0.62153 | 8.55 | St-11 Found Faulty during Suspected SCB Check. | 5.6278 | 0.77683 | 55.9592 | found (-Ve) side MC4 Connector damage same replaced with new one.
Bhadla | September | Inverter 07 | RISO fault | 3495.8 | 44808 | 0.26597 | 44808 | 0.29097 | 0.6 | Inverter Tripped in Riso fault | 0.012441 | 0.78449 | 34.1193 | Dc floating checked fault found in 1A2 keeping that SCB off then start the Inv.
Bhadla | September | SCB.07.02 | String fault | 166.4 | 44808 | 0.29097 | 44808 | 0.32222 | 0.75 | Manually stopped as found abnormal floating | 0.093427 | 0.78449 | 12.1959 | Again checked found Ok.
Bhadla | September | Inverter 11 | RISO fault | 3379.2 | 44808 | 0.26597 | 44808 | 0.28264 | 0.4 | Inverter Tripped in Riso fault | 0.005105 | 0.78449 | 13.5331 | Dc floating checked fault found in 1A2 & 1C2 keeping that SCB off then start the Inv.
Bhadla | September | SCB.11.02 | String fault | 166.4 | 44808 | 0.28264 | 44808 | 0.31806 | 0.85 | Manually stopped as found abnormal floating | 0.080959 | 0.78449 | 10.5683 | Again checked found ok
Bhadla | September | SCB.11.12 | String fault | 140.8 | 44808 | 0.28264 | 44808 | 0.31806 | 0.85 | Manually stopped as found abnormal floating | 0.080959 | 0.78449 | 8.9424 | St-1 isolated then Start the SCB
Bhadla | September | SCB.11.12 | String fault | 12.8 | 44808 | 0.31806 | 44808 | 0.49514 | 4.25 | St-1 found abnormal floating | 2.679 | 0.78449 | 26.9011 | (+ve) Cable 18mtr with 2 Set MC4 Connector used.
Bhadla | September | Inverter 26 | RISO fault | 3494.4 | 44808 | 0.4 | 44808 | 0.41528 | 0.36667 | Inverter Tripped in Riso fault | 0.25552 | 0.78449 | 700.4522 | DC Floating checked nothing found abnormal then start the Inv.
Bhadla | September | SCB.26.12 | String fault | 179.2 | 44808 | 0.41528 | 44808 | 0.42986 | 0.35 | Manually stopped as found abnormal floating | 0.26785 | 0.78449 | 37.6544 | Again checked found ok.
Bhadla | September | Inverter 27 | RISO fault | 3404.8 | 44811 | 0.26667 | 44811 | 0.29097 | 0.58333 | Inveter Tripped in Riso Fault | 0.013621 | 0.74719 | 34.6528 | DC floating checked nothing found abnormal then start the Inv.
Bhadla | September | SCB.06.12 | String fault | 12.8 | 44811 | 0.26667 | 44811 | 0.51389 | 5.9333 | St-1 Found Faulty during Suspected SCB Check. | 3.0711 | 0.74719 | 29.372 | Found (+ve) Y-Connector Damage same replaced with new one.
Bhadla | September | SCB.08.06 | String fault | 12.8 | 44811 | 0.26667 | 44811 | 0.64583 | 9.1 | St-13 Found Faulty during Suspected SCB Check. | 5.8421 | 0.74719 | 55.874 | Found (-ve) Y-Connector Damage same replaced with new one.
Bhadla | September | SCB.26.04 | String fault | 12.8 | 44811 | 0.26667 | 44811 | 0.69653 | 10.3167 | St-3 Found Faulty during Suspected SCB Check. | 6.4559 | 0.74719 | 61.7447 | found 30A fuse faulty same replaced with new one.
Bhadla | September | Inverter 19 | Island protection fault | 3520 | 44812 | 0.55347 | 44812 | 0.56736 | 0.33333 | Inverter Tripped In Island Protection Fault | 0.29402 | 0.74906 | 775.2514 | Discussed with SG Team we restart the Inv.
Bhadla | September | Inverter 27 | RISO fault | 3404.8 | 44814 | 0.26875 | 44814 | 0.28542 | 0.4 | Inverter Tripped in Riso Fault | 0.005663 | 0.74132 | 14.2937 | Dc floating checked nothing found abnrmal then start the SCB.
Bhadla | September | Inverter-1, 2, 3, 4, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 23, 24, 25, 26, 27, 28 | Grid voltage issue | 89615.3 | 44815 | 0.51597 | 44815 | 0.51806 | 0.05 | Inverter-1, 2, 3, 4, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 23, 24, 25, 26, 27, 28 Tripped due to Over voltage in Line. | 0.05934 | 0.76265 | 4055.5844 | Inverters resumes after Grid voltage normalised.
Bhadla | September | Inverter-1, 2, 3, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 17, 18, 20, 21, 24, 25, 27, 28 | Grid voltage issue | 75739.5 | 44815 | 0.61944 | 44815 | 0.64375 | 0.58333 | Inverter-1, 2, 3, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 17, 18, 20, 21, 24, 25, 27, 28 Tripped due to Under Voltage in Line. | 0.44871 | 0.76265 | 25918.5937 | Inverters resumes after Grid voltage normalised. Manaul restart
Citra | April | All Inverters | Grid failure | 2064 | 44658 | 0.65556 | 44658 | 0.65903 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.6681 | 0 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44659 | 0.56667 | 44659 | 0.57014 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.08 | 0.6681 | 110.3167 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44664 | 0.48264 | 44664 | 0.76736 | 6.8333 | Grid outage from GSS for 132/11KV Transformer maintenance work at GSS end. | 3.34 | 0.6681 | 4605.7211 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44666 | 0.68264 | 44666 | 0.68611 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6681 | 27.5792 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44666 | 0.70139 | 44666 | 0.70417 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6681 | 27.5792 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44669 | 0.69097 | 44669 | 0.69375 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6681 | 27.5792 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44672 | 0.67986 | 44672 | 0.68264 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.6681 | 13.7896 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44672 | 0.68333 | 44672 | 0.68611 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.6681 | 13.7896 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44677 | 0.60139 | 44677 | 0.60486 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.08 | 0.6681 | 110.3167 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44680 | 0.63056 | 44680 | 0.63403 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.07 | 0.6681 | 96.5271 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44681 | 0.50069 | 44681 | 0.50347 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.08 | 0.6681 | 110.3167 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44681 | 0.57917 | 44681 | 0.58194 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.07 | 0.6681 | 96.5271 | Grid Resumed.
Citra | April | All Inverters | Grid failure | 2064 | 44681 | 0.69236 | 44681 | 0.69514 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.6681 | 13.7896 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44683 | 0.72986 | 44683 | 0.73681 | 0.16667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44684 | 0.29167 | 44684 | 0.29514 | 0.083333 | 11KV Grid supply failed from 132/11 KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44684 | 0.30833 | 44684 | 0.31111 | 0.066667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.03 | 0.6701 | 41.4926 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44684 | 0.66181 | 44684 | 0.66458 | 0.066667 | 11KV Grid supply failed from 132/11 KV GSS. | 0 | 0.6701 | 0 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44684 | 0.67639 | 44684 | 0.68056 | 0.1 | 11KV Grid supply failed from 132/11 KV GSS. | 0 | 0.6701 | 0 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44684 | 0.71181 | 44684 | 0.71597 | 0.1 | 11KV Grid supply failed from 132/11 KV GSS. | 0.01 | 0.6701 | 13.8309 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44687 | 0.33681 | 44687 | 0.34028 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.04 | 0.6701 | 55.3235 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44687 | 0.55556 | 44687 | 0.55972 | 0.1 | 11KV Grid supply failed from 132/11 KV GSS. | 0.1 | 0.6701 | 138.3086 | Grid Resumed.
Citra | May | SCB.02.09 | String fault | 61.09 | 44691 | 0.24306 | 44691 | 0.37361 | 3.1333 | 10 no strings under breakdown due to smu MCCB failed . | 0.83 | 0.6701 | 33.9772 | MCCB Replaced.
Citra | May | All Inverters | Grid failure | 2064 | 44691 | 0.57569 | 44691 | 0.57847 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44691 | 0.62083 | 44691 | 0.62361 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.05 | 0.6701 | 69.1543 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44692 | 0.575 | 44692 | 0.57778 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.06 | 0.6701 | 82.9852 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44694 | 0.67847 | 44694 | 0.68194 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44700 | 0.23958 | 44700 | 0.4375 | 4.75 | 11KV Transmission line fault due guarding wire broken because of heavy wind. | 1.86 | 0.6701 | 2572.5407 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44704 | 0.61042 | 44704 | 0.61319 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.06 | 0.6701 | 82.9852 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44705 | 0.61111 | 44705 | 0.61389 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.03 | 0.6701 | 41.4926 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44705 | 0.62153 | 44705 | 0.625 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.6701 | 0 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44706 | 0.74861 | 44706 | 0.75764 | 0.21667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed.
Citra | May | All Inverters | Grid failure | 2064 | 44708 | 0.65833 | 44708 | 0.66111 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.04 | 0.6701 | 55.3235 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44715 | 0.48056 | 44715 | 0.48403 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.09 | 0.64659 | 120.1103 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44721 | 0.66944 | 44721 | 0.67222 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.04 | 0.64107 | 52.9268 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44723 | 0.69375 | 44723 | 0.69653 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.67042 | 0 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44724 | 0.65 | 44724 | 0.65278 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.05 | 0.64896 | 66.9725 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44726 | 0.72361 | 44726 | 0.72639 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.66292 | 0 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44726 | 0.72917 | 44726 | 0.73264 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.66292 | 0 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44727 | 0.45556 | 44727 | 0.45903 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.08 | 0.6961 | 114.9403 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44727 | 0.52778 | 44727 | 0.53125 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.02 | 0.6961 | 28.7351 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44730 | 0.28264 | 44730 | 0.28611 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.71971 | 0 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44731 | 0.49097 | 44731 | 0.49444 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.03 | 0.69759 | 43.1947 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44732 | 0.23264 | 44732 | 0.4875 | 6.1167 | 11KV Grid supply failed from 132/11 KV GSS. | 1.96 | 0.70158 | 2838.2196 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44732 | 0.50833 | 44732 | 0.51111 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.07 | 0.70158 | 101.365 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44733 | 0.64861 | 44733 | 0.66111 | 0.3 | 11KV Grid supply failed from 132/11 KV GSS. | 0.04 | 0.71303 | 58.8679 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44735 | 0.53958 | 44735 | 0.54236 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.67962 | 14.0274 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44736 | 0.37708 | 44736 | 0.38056 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.04 | 0.68902 | 56.8852 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44736 | 0.53889 | 44736 | 0.54306 | 0.1 | 11KV Grid supply failed from 132/11 KV GSS. | 0.02 | 0.68902 | 28.4426 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44739 | 0.58194 | 44739 | 0.58472 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.03 | 0.71041 | 43.9888 | Grid Resumed.
Citra | June | All Inverters | Grid failure | 2064 | 44741 | 0.47639 | 44741 | 0.58542 | 2.6167 | 11KV Grid supply failed from 132/11 KV GSS. | 1.58 | 0.72905 | 2377.5238 | Grid Resumed.
Citra | July | All Inverters | Grid failure | 2064 | 44771 | 0.27431 | 44771 | 0.32569 | 1.2333 | 11KV Grid supply failed from 132/11 KV GSS. | 0.19 | 0.74069 | 290.4676 | Grid Resumed.
Citra | August | All Inverters | Feeder tripped | 2064 | 44780 | 0.25694 | 44780 | 0.55417 | 7.1333 | Citra plant 11 KV line tripped on phase to earth fault. Breakdown maintenance done. | 3.72 | 0.7218 | 5542.0381 | Work Completed & Inverter Started At- 13:18 hrs.
Citra | August | All Inverters | Grid failure | 2064 | 44781 | 0.38542 | 44781 | 0.38819 | 0.066667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.008 | 0.73621 | 12.1564 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44785 | 0.47917 | 44785 | 0.49653 | 0.41667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.25 | 0.76618 | 395.3488 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44785 | 0.64375 | 44785 | 0.64861 | 0.11667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.07 | 0.76618 | 110.6977 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44789 | 0.45903 | 44789 | 0.49167 | 0.78333 | 11KV Grid supply failed from 132/11 KV GSS. | 0.51 | 0.77119 | 811.7829 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44795 | 0.45694 | 44795 | 0.4625 | 0.13333 | 11KV Grid supply failed from 132/11 KV GSS. | 0.03 | 0.7218 | 44.6939 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44797 | 0.54097 | 44797 | 0.54375 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.08 | 0.74829 | 123.5569 | Grid Resumed.
Citra | August | All Inverters | Grid failure | 2064 | 44803 | 0.46528 | 44803 | 0.48056 | 0.36667 | 11KV Grid supply failed from 132/11 KV GSS. | 0.17 | 0.7325 | 257.0194 | Grid Resumed.
Citra | September | All Inverters | Feeder tripped | 2064 | 44805 | 0.34097 | 44805 | 0.77083 | 10.3167 | 11KV Grid Failure Due to 02 No's Y & B Phase PT Failed at Substation Switchyard. | 5.16 | 0.6565 | 6991.8826 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44807 | 0.61042 | 44807 | 0.61389 | 0.083333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.03 | 0.6565 | 40.6505 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44811 | 0.65139 | 44811 | 0.65694 | 0.13333 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.6565 | 13.5502 | Grid Resumed.
Citra | September | Inverter 02 | Ground fault | 1032 | 44811 | 0.65139 | 44811 | 0.67917 | 0.66667 | Inverter no 2 tripped on earth fault. Fault rectification done and inverter started | 0.06 | 0.6565 | 40.6505 | Fault Rectify & Inverter Started At : 16:18 hrs.
Citra | September | Inverter 02 | Ground fault | 1032 | 44811 | 0.69028 | 44811 | 0.71111 | 0.5 | Inverter no 2 tripped on earth fault. Fault rectification done and inverter started | 0.03 | 0.6565 | 20.3252 | Fault Rectify & Inverter Started At : 17:04 hrs.
Citra | September | Inverter 02 | Ground fault | 1032 | 44812 | 0.30833 | 44812 | 0.325 | 0.4 | Inverter no 2 tripped on earth fault. Fault rectification done and inverter started | 0.08 | 0.6565 | 54.2006 | Fault Rectify & Inverter Started At : 07:48 hrs.
Citra | September | All Inverters | Grid failure | 2064 | 44814 | 0.29722 | 44814 | 0.32153 | 0.58333 | 11KV Grid supply failed from 132/11 KV GSS. | 0.09 | 0.6565 | 121.9514 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44814 | 0.53264 | 44814 | 0.75139 | 5.25 | 11KV Grid supply failed from 132/11 KV GSS. | 2.37 | 0.6565 | 3211.3879 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44815 | 0.73056 | 44815 | 0.73333 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.6565 | 0 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44818 | 0.29653 | 44818 | 0.30139 | 0.11667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0.01 | 0.6565 | 13.5502 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44818 | 0.69722 | 44818 | 0.7 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.6565 | 0 | Grid Resumed.
Citra | September | All Inverters | Grid failure | 2064 | 44818 | 0.7125 | 44818 | 0.71528 | 0.066667 | 11KV Grid Fluctuation from 132/11KV GSS. | 0 | 0.6565 | 0 | Grid Resumed.
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44656 | 0.27986 | 44656 | 0.29375 | 0.33333 | Earth Fault | 0.022527 | 0.77065 | 20.9219 | Inverter tripped on Earth fault. Found two strings faulty. Isolated faulty strings & on the inverter
Hindupur | April | SCB.11.02 | String fault | 7.26 | 44656 | 0.27986 | 44656 | 0.51042 | 5.5333 | Earth Fault | 3.0815 | 0.77065 | 17.241 | String reconnected. now ok
Hindupur | April | SCB.11.02 | String fault | 7.26 | 44656 | 0.27986 | 44656 | 0.51042 | 5.5333 | Earth Fault | 3.0815 | 0.77065 | 17.241 | String reconnected. now ok
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44659 | 0.33681 | 44659 | 0.34444 | 0.18333 | Earth Fault | 0.145 | 0.78933 | 137.9345 | Inverter Manual Reset
Hindupur | April | inverter 30 | Short circuit fault | 1202.85 | 44659 | 0.56736 | 44659 | 0.57639 | 0.21667 | short circuit | 0.38 | 0.78933 | 360.7906 | Inverter Manual Reset
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44661 | 0.58472 | 44661 | 0.59167 | 0.16667 | EXT DI4 fault | 0.29 | 0.78448 | 274.1712 | Manually reset & turn on inverter
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44661 | 0.60556 | 44661 | 0.61111 | 0.13333 | EXT DI4 fault | 0.17 | 0.78448 | 160.7211 | Inverter tripped on Earth fault.Found one string faulty. Isolated faulty strings & on inverter
Hindupur | April | SCB.11.03 | String fault | 7.26 | 44661 | 0.58472 | 44661 | 0.625 | 0.96667 | Earth Fault | 0.65059 | 0.78448 | 3.7053 | MC4 Connector burnt at table end .Replaced with new one & reconnected.
Hindupur | April | inverter 34 | Short circuit fault | 1195.43 | 44662 | 0.27361 | 44662 | 0.27708 | 0.083333 | short circuit | 0.0098 | 0.79881 | 9.3582 | Manually reset & turn on inverter
Hindupur | April | Inverter 28 | Ground fault | 1195.43 | 44663 | 0.29444 | 44663 | 0.29653 | 0.05 | Earth Fault | 0.0098541 | 0.7801 | 9.1895 | Manually reset & turn on inverter
Hindupur | April | Inverter 28 | Ground fault | 1195.43 | 44663 | 0.35417 | 44663 | 0.36111 | 0.16667 | Earth Fault | 0.088898 | 0.7801 | 82.902 | Inverter tripped on Earth fault. Found two strings faulty. Isolated faulty strings & on inverter
Hindupur | April | SCB.28.04 | String fault | 7.425 | 44663 | 0.35417 | 44663 | 0.41667 | 1.5 | Earth Fault | 0.92223 | 0.7801 | 5.3418 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | April | SCB.28.04 | String fault | 7.425 | 44663 | 0.35417 | 44663 | 0.41667 | 1.5 | Earth Fault | 0.92223 | 0.7801 | 5.3418 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | April | SCB.28.04 | String fault | 597.7 | 44663 | 0.29167 | 44663 | 0.31944 | 0.66667 | Earth Fault | 0.12846 | 0.7801 | 59.8954 | Isolated faulty strings & turn on SCB .
Hindupur | April | Inverter 33 | RESET Fault | 1195.43 | 44664 | 0.59236 | 44664 | 0.59653 | 0.1 | RESET Fault | 0.10948 | 0.78786 | 103.1125 | Manually reset & turn on inverter
Hindupur | April | Inverter 09 | RESET fault | 1205.16 | 44666 | 0.34722 | 44666 | 0.35069 | 0.083333 | RESET Fault | 0.030933 | 0.78388 | 29.2221 | Manually reset & turn on inverter
Hindupur | April | Inverter 19 | Ground fault | 1219.68 | 44666 | 0.29167 | 44666 | 0.29653 | 0.11667 | Earth Fault | 0.008351 | 0.78388 | 7.9842 | Manually reset & turn on inverter
Hindupur | April | Inverter 19 | Ground fault | 1219.68 | 44666 | 0.32222 | 44666 | 0.33125 | 0.21667 | Earth Fault | 0.05081 | 0.78388 | 48.5786 | Inverter tripped on Earth fault.Found one string faulty .Isolated faulty string & on inverter
Hindupur | April | SCB.19.04 | String fault | 152.46 | 44666 | 0.32222 | 44666 | 0.33125 | 0.21667 | Earth Fault | 0.05081 | 0.78388 | 6.0723 | Isolated faulty string & turn on SCB .
Hindupur | April | SCB.19.04 | String fault | 7.26 | 44666 | 0.29167 | 44666 | 0.34722 | 1.3333 | Earth Fault | 0.23962 | 0.78388 | 1.3637 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | April | Inverter 09 | Ground fault | 1205.16 | 44668 | 0.32639 | 44668 | 0.32986 | 0.083333 | Earth Fault | 0.013752 | 0.7942 | 13.1624 | Manually reset & turn on inverter
Hindupur | April | Inverter 09 | Ground fault | 1205.16 | 44668 | 0.34444 | 44668 | 0.35972 | 0.36667 | Earth Fault | 0.14288 | 0.7942 | 136.7519 | Inverter tripped on Earth fault.Found two strings faulty .Isolated faulty strings & on inverter
Hindupur | April | Inverter 20 | Ground fault | 1205.16 | 44668 | 0.33264 | 44668 | 0.33681 | 0.1 | Earth Fault | 0.019776 | 0.7942 | 18.9278 | Manually reset & turn on inverter
Hindupur | April | SCB.09.06 | String fault | 14.52 | 44668 | 0.32639 | 44668 | 0.41667 | 2.1667 | Earth Fault | 1.1228 | 0.7942 | 12.9477 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | April | Inverter 21 | MAIN CNT Fault | 1190.64 | 44672 | 0.49306 | 44672 | 0.75972 | 6.4 | RDCO Card faulty A41 | 3.6189 | 0.75226 | 3241.3645 | Fault not cleared. ABB Er with spares reaching plant tomorrow by 8 am to attend fault
Hindupur | April | Inverter 24 | Hand Trip | 1205.16 | 44672 | 0.58472 | 44672 | 0.60694 | 0.53333 | As per instructions, Swapping of RDCO Card done from Inv 24 to Inv 21 for testing | 0.44259 | 0.75226 | 401.2516 | As it is replaced its RDCO Card & Restarted Inverter
Hindupur | April | Inverter 32 | RESET fault | 1195.43 | 44672 | 0.67917 | 44672 | 0.68542 | 0.15 | RESET Fault | 0.060467 | 0.75226 | 54.3767 | Manually reset & turn on inverter
Hindupur | April | Power Transformer-1 | Under voltage fault | 24103.2 | 44673 | 0.42361 | 44673 | 0.43611 | 0.3 | Under Voltage fault | 0.25579 | 0.77232 | 4761.6732 | Fault reset & charged Power transformer -1
Hindupur | April | Inverter 21 | MAIN CNT Fault | 1190.64 | 44673 | 0.27083 | 44673 | 0.38056 | 2.6333 | RDCO Card faulty A41 | 0.75311 | 0.77232 | 692.5275 | ABB Er visited site to attend fault .Updated software (ISXR 7390) & Checked found normal.
Hindupur | April | Inverter 11 | LCL fan fault | 1205.16 | 44673 | 0.50764 | 44673 | 0.58264 | 1.8 | LCL Filter fan faulty | 1.6101 | 0.77232 | 1498.6464 | Replaced with new filter fan taking support of ABB Er & checked found normal
Hindupur | April | Inverter 27 | Short circuit fault | 1195.43 | 44676 | 0.27847 | 44676 | 0.28472 | 0.15 | short circuit | 0.0193 | 0.77689 | 17.9242 | Manually reset & turn on inverter
Hindupur | April | Inverter 26 | Ground fault | 1195.43 | 44676 | 0.50764 | 44676 | 0.51597 | 0.2 | Earth Fault | 0.421 | 0.77689 | 390.9888 | Manually reset & turn on inverter
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44676 | 0.66875 | 44676 | 0.69028 | 0.51667 | Earth Fault | 0.088 | 0.77689 | 82.3921 | Manually reset & turn on inverter
Hindupur | April | Inverter 27 | Ground fault | 1195.43 | 44676 | 0.66875 | 44676 | 0.69028 | 0.51667 | Earth Fault | 0.088 | 0.77689 | 81.7269 | Manually reset & turn on inverter
Hindupur | April | Inverter 06 | Ground fault | 1205.16 | 44676 | 0.66875 | 44676 | 0.69028 | 0.51667 | Earth Fault | 0.088 | 0.77689 | 82.3921 | Manually reset & turn on inverter
Hindupur | April | Inverter 33 | Short circuit fault | 1195.43 | 44677 | 0.26944 | 44677 | 0.27361 | 0.1 | short circuit | 0.004889 | 0.76936 | 4.4965 | Manually reset & turn on inverter
Hindupur | April | Inverter 33 | LCL fan fault | 1195.43 | 44679 | 0.47014 | 44679 | 0.5 | 0.71667 | LCL Filter fan faulty | 0.67776 | 0.76926 | 623.2646 | Replaced with new filter fan taking support of ABB Er & checked found normal
Hindupur | April | Inverter 11 | Ground fault | 1205.16 | 44679 | 0.37292 | 44679 | 0.37639 | 0.083333 | Earth Fault | 0.055178 | 0.76926 | 51.1539 | Manually reset & turn on inverter
Hindupur | April | Inverter 04 | MAIN CNT Fault | 1205.16 | 44681 | 0.71597 | 44681 | 0.72847 | 0.3 | MAIN CNT F | 0.048706 | 0.7703 | 45.2152 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44682 | 0.29097 | 44682 | 0.33333 | 1.0167 | Earth Fault | 0.20333 | 0.77363 | 189.578 | Inverter tripped on Earth fault. Found two strings faulty. Isolated faulty strings & on inverter
Hindupur | May | SCB.09.01 | String fault | 172.16 | 44682 | 0.33333 | 44682 | 0.34722 | 0.33333 | Earth Fault | 0.115 | 0.77363 | 15.3167 | scb check no fault found breaker on
Hindupur | May | SCB.09.02 | String fault | 172.16 | 44682 | 0.33333 | 44682 | 0.36042 | 0.65 | Earth Fault | 0.24635 | 0.77363 | 32.811 | scb check no fault found breaker on
Hindupur | May | SCB.09.03 | String fault | 172.16 | 44682 | 0.33333 | 44682 | 0.36181 | 0.68333 | Earth Fault | 0.26103 | 0.77363 | 34.7667 | scb check no fault found breaker on
Hindupur | May | SCB.09.05 | String fault | 172.16 | 44682 | 0.33333 | 44682 | 0.36389 | 0.73333 | Earth Fault | 0.28453 | 0.77363 | 37.8966 | scb check no fault found breaker on
Hindupur | May | SCB.09.06 | String fault | 172.16 | 44682 | 0.33333 | 44682 | 0.36597 | 0.78333 | Earth Fault | 0.30863 | 0.77363 | 41.1064 | scb check no fault found breaker on
Hindupur | May | Inverter 32 | RESET fault | 1195.43 | 44682 | 0.50972 | 44682 | 0.51736 | 0.18333 | RESET fault | 0.16995 | 0.77363 | 157.1737 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Gnd leakage current fault | 1205.16 | 44683 | 0.28264 | 44683 | 0.28403 | 0.033333 | RESET fault | 0.0035 | 0.79758 | 3.3642 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44683 | 0.29375 | 44683 | 0.30417 | 0.25 | Earth Fault | 0.029 | 0.79758 | 27.875 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Gnd leakage current fault | 1205.16 | 44683 | 0.29653 | 44683 | 0.30417 | 0.18333 | RESET fault | 0.022 | 0.79758 | 21.1465 | Manually reset & turn on inverter
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44683 | 0.29722 | 44683 | 0.31944 | 0.53333 | Earth Fault | 0.075 | 0.79758 | 72.0905 | Manually reset & turn on inverter
Hindupur | May | SCB.17.07 | String fault | 150.645 | 44683 | 0.31944 | 44683 | 0.35625 | 0.88333 | RESET fault | 0.26986 | 0.79758 | 32.4237 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | RESET fault | 1195.43 | 44683 | 0.35278 | 44683 | 0.36528 | 0.3 | RESET fault | 0.1201 | 0.79758 | 114.5089 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | RESET fault | 1195.43 | 44683 | 0.74167 | 44683 | 0.74931 | 0.18333 | RESET fault | 0.01183 | 0.79758 | 11.2793 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | RESET fault | 1195.43 | 44684 | 0.28125 | 44684 | 0.30556 | 0.58333 | RESET fault | 0.05828 | 0.78203 | 54.4837 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | RESET fault | 1205.16 | 44685 | 0.28958 | 44685 | 0.29583 | 0.15 | RESET fault | 0.01752 | 0.79577 | 16.8022 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | RESET fault | 1205.16 | 44686 | 0.26389 | 44686 | 0.32292 | 1.4167 | RESET fault | 0.204 | 0.78414 | 192.7823 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44687 | 0.26042 | 44687 | 0.36667 | 2.55 | Ground close Er & Grd leak current | 0.62245 | 0.7848 | 588.7253 | Checked all SCBs one by one .But tripping continuously .Not found any string fault .Finally turn on at 8:48 am
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44687 | 0.26042 | 44687 | 0.31111 | 1.2167 | Ground leakage current | 0.12678 | 0.7848 | 119.9069 | Found 1 string faulty .Isolated faulty string & turn on inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44687 | 0.29306 | 44687 | 0.34861 | 1.3333 | Ground high vol & Gnd leak current | 0.396 | 0.7848 | 379.054 | Checked all SCBs one by one .But tripping continuously .Not found any string fault .Finally turn on at 8:22 am
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44687 | 0.27569 | 44687 | 0.28472 | 0.21667 | Ground leak current | 0.017333 | 0.7848 | 16.3941 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44687 | 0.26042 | 44687 | 0.32986 | 1.6667 | String fault | 0.245 | 0.7848 | 228.932 | Found two strings faulty .Isolated faulty string & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44687 | 0.33194 | 44687 | 0.36528 | 0.8 | String fault | 0.3448 | 0.7848 | 326.1159 | Checked all SCBs one by one .But tripping continuously . found 1 string faulty .Finally turn on at 8:46 am
Hindupur | May | Inverter 25 | Ground fault | 1195.43 | 44687 | 0.3 | 44687 | 0.31389 | 0.33333 | String fault | 0.063667 | 0.7848 | 59.7305 | Manually reset & turn on inverter
Hindupur | May | Inverter 25 | Ground fault | 1195.43 | 44687 | 0.37847 | 44687 | 0.39028 | 0.28333 | String fault | 0.17425 | 0.7848 | 163.4771 | Found 1 string faulty .Isolated faulty string & turn on inverter
Hindupur | May | Inverter 28 | Ground fault | 1195.43 | 44687 | 0.29236 | 44687 | 0.31319 | 0.5 | Ground leak current | 0.085 | 0.7848 | 79.7449 | Manually reset & turn on inverter
Hindupur | May | Inverter 31 | Ground fault | 1188 | 44687 | 0.34583 | 44687 | 0.35556 | 0.23333 | Ground fault | 0.10407 | 0.7848 | 97.026 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | AC breaker off | 1195.43 | 44687 | 0.48472 | 44687 | 0.49375 | 0.21667 | AC Breaker off | 0.1976 | 0.7848 | 185.3835 | TU Button reset in ac breaker & turn on inverter
Hindupur | May | SCB.20.02 | String fault | 7.26 | 44687 | 0.25278 | 44687 | 0.52083 | 6.4333 | String fault | 3.6236 | 0.7848 | 20.6463 | String fault rectified by providing new MC4 Connectors. now ok
Hindupur | May | SCB.25.05 | String fault | 7.425 | 44687 | 0.25278 | 44687 | 0.52083 | 6.4333 | String fault | 3.6236 | 0.7848 | 21.1155 | String fault rectified by providing new MC4 Connectors. now ok
Hindupur | May | SCB.21.03 | String fault | 14.52 | 44687 | 0.25278 | 44687 | 0.76597 | 12.3167 | String fault | 6.56 | 0.7848 | 74.7533 | Two Strings open (Inv 21/SCB 3/Str 1 & Inv 21/SCB-5 /Str 4 .Need to rectify
Hindupur | May | SCB.24.03 | String fault | 7.26 | 44687 | 0.25278 | 44687 | 0.76597 | 12.3167 | String fault | 6.56 | 0.7848 | 37.3767 | One String open (Inv 24/SCB 3/Str 1 .Need to rectify
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44688 | 0.38194 | 44688 | 0.38681 | 0.11667 | String fault | 0.080183 | 0.77784 | 75.1647 | Found two strings faulty .Isolated faulty strings & turn on inverter
Hindupur | May | SCB.20.05 | String fault | 7.26 | 44688 | 0.38194 | 44688 | 0.51875 | 3.2833 | String fault | 2.6643 | 0.77784 | 15.0454 | Found -ve string cable minor insulation failure .Properly dressed & provided new MC4 Connectors
Hindupur | May | SCB.20.05 | String fault | 7.26 | 44688 | 0.38194 | 44688 | 0.53472 | 3.6667 | String fault | 3.0166 | 0.77784 | 17.0349 | Provided new MC4 Connectors .Now ok
Hindupur | May | SCB.20.07 | String fault | 14.52 | 44688 | 0.25278 | 44688 | 0.47917 | 5.4333 | String fault | 1.8144 | 0.77784 | 20.4926 | Provided new MC4 Connectors .Now ok
Hindupur | May | SCB.20.07 | String fault | 7.26 | 44688 | 0.25278 | 44688 | 0.47917 | 5.4333 | String fault | 1.8144 | 0.77784 | 10.2463 | Provided new MC4 Connectors .Now ok
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44689 | 0.27986 | 44689 | 0.29306 | 0.31667 | String fault | 0.022388 | 0.78578 | 21.2017 | Isolated the faulty string and turn ON inverter
Hindupur | May | Inverter 10 | Ground fault | 1205.16 | 44689 | 0.25833 | 44689 | 0.29167 | 0.8 | String fault | 0.0436 | 0.78578 | 41.289 | Isolated the faulty string and turn ON inverter
Hindupur | May | SCB.10.01 | String fault | 7.6 | 44689 | 0.29167 | 44689 | 0.45833 | 4 | String fault | 1.972 | 0.78578 | 11.7767 | Inv-10 SCB-1 one string fault, replaced damaged -Ve cable with new one.
Hindupur | May | Inverter 15 | RESET fault | 1205.16 | 44689 | 0.28542 | 44689 | 0.28819 | 0.066667 | RESET fault | 0.0048 | 0.78578 | 4.5456 | Manually reset & turn on inverter
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44689 | 0.25833 | 44689 | 0.28125 | 0.55 | String fault | 0.02585 | 0.78578 | 24.4799 | Isolated the faulty string and turn ON inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44689 | 0.25833 | 44689 | 0.28403 | 0.61667 | String fault | 0.030217 | 0.78578 | 28.9598 | Manually reset & turn on inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44689 | 0.33958 | 44689 | 0.34167 | 0.05 | String fault | 0.0165 | 0.78578 | 15.8137 | Isolated the faulty string and turn ON inverter
Hindupur | May | SCB.19.06 | String fault | 7.6 | 44689 | 0.34167 | 44689 | 0.46875 | 3.05 | String fault | 1.9489 | 0.78578 | 11.6391 | Inv-19 SCB-6 one string fault, replaced damaged MC4 with new one.
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44689 | 0.38542 | 44689 | 0.38889 | 0.083333 | String fault | 0.046167 | 0.78578 | 43.1929 | Isolated the faulty string and turn ON inverter
Hindupur | May | SCB.21.03 | String fault | 148.8 | 44689 | 0.38889 | 44689 | 0.39236 | 0.083333 | String fault | 0.047167 | 0.78578 | 5.515 | Isolated the faulty string and turn ON SCB
Hindupur | May | SCB.21.03 | String fault | 7.6 | 44689 | 0.39236 | 44689 | 0.47222 | 1.9167 | String fault | 1.4528 | 0.78578 | 8.6763 | Inv-21 SCB-3 one string fault, replaced damaged MC4 with new one.
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44689 | 0.30556 | 44689 | 0.32222 | 0.4 | String fault | 0.0776 | 0.78578 | 72.8936 | Isolated the faulty string and turn ON inverter
Hindupur | May | Inverter 04 | RESET fault | 1205.16 | 44689 | 0.37847 | 44689 | 0.38125 | 0.066667 | RESET fault | 0.035467 | 0.78578 | 33.5868 | Manually reset & turn on inverter
Hindupur | May | Inverter 04 | Ground fault | 1205.16 | 44689 | 0.40625 | 44689 | 0.41042 | 0.1 | String fault | 0.0692 | 0.78578 | 65.5322 | Isolated the faulty string and turn ON inverter
Hindupur | May | SCB.04.07 | String fault | 7.6 | 44689 | 0.41042 | 44689 | 0.43819 | 0.66667 | String fault | 0.49867 | 0.78578 | 2.978 | Inv-4 SCB-7 one string fault, replaced damaged MC4 with new one.
Hindupur | May | Inverter 11 | Ground fault | 1205.16 | 44689 | 0.69028 | 44689 | 0.69514 | 0.11667 | RESET fault | 0.012717 | 0.78578 | 12.0426 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44689 | 0.69236 | 44689 | 0.70556 | 0.31667 | RESET fault | 0.2565 | 0.78578 | 239.978 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | Ground fault | 1195.43 | 44689 | 0.68889 | 44689 | 0.69931 | 0.25 | RESET fault | 0.0255 | 0.78578 | 23.9534 | Manually reset & turn on inverter
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44690 | 0.27986 | 44690 | 0.28403 | 0.1 | DI4 Fault | 0.00792 | 0.79408 | 7.5794 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44690 | 0.2875 | 44690 | 0.29097 | 0.083333 | DI4 Fault | 0.0079126 | 0.79408 | 7.5723 | Manually reset & turn on inverter
Hindupur | May | SCB.40.06 | String fault | 7.425 | 44690 | 0.49306 | 44690 | 0.52222 | 0.7 | String fault | 0.57948 | 0.79408 | 3.4166 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44691 | 0.275 | 44691 | 0.29444 | 0.46667 | DI4 Fault | 0.024865 | 0.83373 | 24.7822 | Manually reset & turn on inverter
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44691 | 0.42153 | 44691 | 0.42639 | 0.11667 | String fault | 0.034059 | 0.83373 | 33.9461 | Isolated the faulty string and turn ON inverter
Hindupur | May | SCB.38.04 | String fault | 7.425 | 44691 | 0.42153 | 44691 | 0.47917 | 1.3833 | String fault | 0.28506 | 0.83373 | 1.7646 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44692 | 0.29167 | 44692 | 0.3125 | 0.5 | EXT DI4 fault | 0.029468 | 0.82156 | 29.177 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44692 | 0.30208 | 44692 | 0.30556 | 0.083333 | EXT DI4 fault | 0.0043731 | 0.82156 | 4.3299 | Manually reset & turn on inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44694 | 0.32222 | 44694 | 0.32986 | 0.18333 | EXT DI4 fault | 0.00715 | 0.82993 | 7.2376 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44694 | 0.71944 | 44694 | 0.74028 | 0.5 | EXT DI4 fault | 0.021 | 0.82993 | 21.0042 | Manually reset & turn on inverter
Hindupur | May | Inverter 15 | Ground fault | 1205.16 | 44695 | 0.27847 | 44695 | 0.28264 | 0.1 | EXT DI4 fault | 0.0124 | 0.79852 | 11.933 | Manually reset & turn on inverter
Hindupur | May | Inverter 17 | Ground fault | 1205.16 | 44695 | 0.28125 | 44695 | 0.28542 | 0.1 | EXT DI4 fault | 0.014 | 0.79852 | 13.4728 | Manually reset & turn on inverter
Hindupur | May | Inverter 22 | Ground fault | 1190.64 | 44695 | 0.49236 | 44695 | 0.50833 | 0.38333 | EXT DI4 fault | 0.36302 | 0.79852 | 345.1364 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44697 | 0.28403 | 44697 | 0.2875 | 0.083333 | EXT DI4 fault | 0.0046464 | 0.79454 | 4.4492 | Manually reset & turn on inverter
Hindupur | May | Inverter 30 | Short circuit fault | 1202.85 | 44697 | 0.39583 | 44697 | 0.40139 | 0.13333 | short circuit | 0.089073 | 0.79454 | 85.1282 | Manually reset & turn on inverter
Hindupur | May | Inverter 30 | Short circuit fault | 1202.85 | 44697 | 0.41042 | 44697 | 0.41944 | 0.21667 | short circuit | 0.15808 | 0.79454 | 151.0779 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44697 | 0.50278 | 44697 | 0.50833 | 0.13333 | EXT DI4 fault | 0.10621 | 0.79454 | 101.7023 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44697 | 0.53194 | 44697 | 0.54514 | 0.31667 | EXT DI4 fault | 0.29534 | 0.79454 | 282.806 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44697 | 0.55833 | 44697 | 0.56875 | 0.25 | EXT DI4 fault | 0.20684 | 0.79454 | 198.0552 | Isolated faulty string & turn on inverter.
Hindupur | May | SCB.13.01 | String fault | 7.26 | 44697 | 0.50278 | 44697 | 0.57639 | 1.7667 | String fault | 1.4078 | 0.79454 | 8.1206 | String fault rectified by replacing with new cable . now ok
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44698 | 0.26458 | 44698 | 0.28403 | 0.46667 | EXT DI4 fault | 0.19133 | 0.83458 | 192.4436 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44698 | 0.34028 | 44698 | 0.35486 | 0.35 | EXT DI4 fault | 0.0532 | 0.83458 | 53.5087 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44698 | 0.49931 | 44698 | 0.50833 | 0.21667 | EXT DI4 fault | 0.11288 | 0.83458 | 113.5383 | Manually reset & turn on inverter
Hindupur | May | Inverter 30 | Ground fault | 1202.85 | 44698 | 0.50278 | 44698 | 0.52361 | 0.5 | EXT DI4 fault | 0.245 | 0.83458 | 245.9493 | Manually reset & turn on inverter
Hindupur | May | Inverter 30 | Ground fault | 1202.85 | 44698 | 0.5375 | 44698 | 0.5625 | 0.6 | EXT DI4 fault | 0.4398 | 0.83458 | 441.5041 | Manually reset & turn on inverter
Hindupur | May | Inverter 08 | Ground fault | 1205.16 | 44699 | 0.36528 | 44699 | 0.37778 | 0.3 | EXT DI4 fault | 0.297 | 0.85979 | 307.7457 | Manually reset & turn on inverter
Hindupur | May | Inverter 28 | Ground fault | 1195.43 | 44699 | 0.37153 | 44699 | 0.37917 | 0.18333 | EXT DI4 fault | 0.019983 | 0.85979 | 20.5392 | Manually reset & turn on inverter
Hindupur | May | Inverter 22 | Ground fault | 1190.64 | 44699 | 0.37153 | 44699 | 0.38542 | 0.33333 | EXT DI4 fault | 0.043667 | 0.85979 | 44.7014 | Manually reset & turn on inverter
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44699 | 0.37778 | 44699 | 0.39583 | 0.43333 | EXT DI4 fault | 0.076267 | 0.85979 | 78.388 | Manually reset & turn on inverter
Hindupur | May | Inverter 35 | Ground fault | 1136.03 | 44699 | 0.38333 | 44699 | 0.39236 | 0.21667 | EXT DI4 fault | 0.040517 | 0.85979 | 39.5744 | Manually reset & turn on inverter
Hindupur | May | Inverter 08 | Ground fault | 1205.16 | 44699 | 0.38681 | 44699 | 0.40764 | 0.5 | EXT DI4 fault | 0.098 | 0.85979 | 101.5457 | Manually reset & turn on inverter
Hindupur | May | Inverter 35 | Ground fault | 1136.03 | 44699 | 0.39583 | 44699 | 0.40139 | 0.13333 | EXT DI4 fault | 0.027467 | 0.85979 | 26.8279 | Manually reset & turn on inverter
Hindupur | May | Inverter 04 | Ground fault | 1205.16 | 44699 | 0.39861 | 44699 | 0.40625 | 0.18333 | EXT DI4 fault | 0.035383 | 0.85979 | 36.6635 | Manually reset & turn on inverter
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44699 | 0.4 | 44699 | 0.40486 | 0.11667 | EXT DI4 fault | 0.022283 | 0.85979 | 22.9031 | Manually reset & turn on inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44699 | 0.40486 | 44699 | 0.41389 | 0.21667 | EXT DI4 fault | 0.0403 | 0.85979 | 42.2612 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44699 | 0.43194 | 44699 | 0.43958 | 0.18333 | EXT DI4 fault | 0.04455 | 0.85979 | 45.6057 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44699 | 0.52639 | 44699 | 0.53403 | 0.18333 | EXT DI4 fault | 0.1276 | 0.85979 | 132.2167 | Manually reset & turn on inverter
Hindupur | May | Inverter 08 | Ground fault | 1205.16 | 44699 | 0.58125 | 44699 | 0.58681 | 0.13333 | EXT DI4 fault | 0.0248 | 0.85979 | 25.6973 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44699 | 0.54444 | 44699 | 0.56875 | 0.58333 | EXT DI4 fault | 0.34825 | 0.85979 | 360.85 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44699 | 0.58264 | 44699 | 0.59028 | 0.18333 | EXT DI4 fault | 0.030067 | 0.85979 | 31.1545 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44699 | 0.63194 | 44699 | 0.63958 | 0.18333 | EXT DI4 fault | 0.165 | 0.85979 | 170.9698 | Manually reset & turn on inverter
Hindupur | May | Inverter 19 | Ground fault | 1219.68 | 44699 | 0.62917 | 44699 | 0.64861 | 0.46667 | EXT DI4 fault | 0.048067 | 0.85979 | 50.4058 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44699 | 0.62639 | 44699 | 0.63333 | 0.16667 | EXT DI4 fault | 0.145 | 0.85979 | 148.436 | Manually reset & turn on inverter
Hindupur | May | Inverter 15 | Ground fault | 1205.16 | 44699 | 0.63194 | 44699 | 0.64931 | 0.41667 | EXT DI4 fault | 0.044583 | 0.85979 | 46.1964 | Manually reset & turn on inverter
Hindupur | May | Inverter 15 | Ground fault | 1205.16 | 44699 | 0.6625 | 44699 | 0.66806 | 0.13333 | EXT DI4 fault | 0.12533 | 0.85979 | 129.868 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44699 | 0.68472 | 44699 | 0.69236 | 0.18333 | EXT DI4 fault | 0.11367 | 0.85979 | 117.7792 | Manually reset & turn on inverter
Hindupur | May | Inverter 37 | Ground fault | 1195.43 | 44700 | 0.27222 | 44700 | 0.30347 | 0.75 | EXT DI4 fault | 0.5625 | 0.82665 | 555.8619 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44700 | 0.27639 | 44700 | 0.33819 | 1.4833 | EXT DI4 fault | 0.18838 | 0.82665 | 185.4143 | Manually reset & turn on inverter
Hindupur | May | Inverter 28 | Ground fault | 1195.43 | 44700 | 0.30694 | 44700 | 0.31597 | 0.21667 | EXT DI4 fault | 0.033583 | 0.82665 | 33.187 | Manually reset & turn on inverter
Hindupur | May | Inverter 37 | Ground fault | 1195.43 | 44700 | 0.30833 | 44700 | 0.31458 | 0.15 | EXT DI4 fault | 0.02355 | 0.82665 | 23.2721 | Manually reset & turn on inverter
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44700 | 0.3125 | 44700 | 0.31875 | 0.15 | EXT DI4 fault | 0.02985 | 0.82665 | 29.4977 | Manually reset & turn on inverter
Hindupur | May | Inverter 05 | Ground fault | 1205.16 | 44700 | 0.31597 | 44700 | 0.325 | 0.21667 | EXT DI4 fault | 0.0468 | 0.82665 | 46.6241 | Manually reset & turn on inverter
Hindupur | May | Inverter 31 | Ground fault | 1188 | 44700 | 0.325 | 44700 | 0.33819 | 0.31667 | EXT DI4 fault | 0.04845 | 0.82665 | 47.5807 | Manually reset & turn on inverter
Hindupur | May | Inverter 38 | Ground fault | 1195.43 | 44700 | 0.32778 | 44700 | 0.33819 | 0.25 | EXT DI4 fault | 0.0345 | 0.82665 | 34.0929 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44700 | 0.33264 | 44700 | 0.34722 | 0.35 | EXT DI4 fault | 0.04235 | 0.82665 | 42.1909 | Manually reset & turn on inverter
Hindupur | May | Inverter 25 | Ground fault | 1195.43 | 44700 | 0.34306 | 44700 | 0.34583 | 0.066667 | EXT DI4 fault | 0.0091333 | 0.82665 | 9.0256 | Manually reset & turn on inverter
Hindupur | May | Inverter 11 | Ground fault | 1205.16 | 44700 | 0.34583 | 44700 | 0.34931 | 0.083333 | EXT DI4 fault | 0.012417 | 0.82665 | 12.37 | Manually reset & turn on inverter
Hindupur | May | Inverter 21 | Ground fault | 1190.64 | 44700 | 0.34722 | 44700 | 0.35486 | 0.18333 | EXT DI4 fault | 0.027133 | 0.82665 | 26.7057 | Manually reset & turn on inverter
Hindupur | May | Inverter 33 | Ground fault | 1195.43 | 44700 | 0.4375 | 44700 | 0.44514 | 0.18333 | EXT DI4 fault | 0.11037 | 0.82665 | 109.0642 | Manually reset & turn on inverter
Hindupur | May | Inverter 33 | Ground fault | 1195.43 | 44700 | 0.44861 | 44700 | 0.45417 | 0.13333 | EXT DI4 fault | 0.098933 | 0.82665 | 97.7658 | Manually reset & turn on inverter
Hindupur | May | Inverter 39 | Ground fault | 1195.43 | 44700 | 0.47083 | 44700 | 0.48125 | 0.25 | EXT DI4 fault | 0.12225 | 0.82665 | 120.8073 | Manually reset & turn on inverter
Hindupur | May | Inverter 10 | Ground fault | 1205.16 | 44700 | 0.47847 | 44700 | 0.48333 | 0.11667 | EXT DI4 fault | 0.033483 | 0.82665 | 33.3575 | Manually reset & turn on inverter
Hindupur | May | Inverter 39 | Ground fault | 1195.43 | 44700 | 0.48472 | 44700 | 0.49236 | 0.18333 | EXT DI4 fault | 0.05335 | 0.82665 | 52.7204 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | Ground fault | 1195.43 | 44700 | 0.65347 | 44700 | 0.65625 | 0.066667 | EXT DI4 fault | 0.012333 | 0.82665 | 12.1878 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | Ground fault | 1195.43 | 44701 | 0.32778 | 44701 | 0.33681 | 0.21667 | EXT DI4 fault | 0.091 | 0.86553 | 94.1557 | Manually reset & turn on inverter
Hindupur | May | Inverter 15 | Ground fault | 1205.16 | 44701 | 0.36736 | 44701 | 0.38542 | 0.43333 | EXT DI4 fault | 0.056767 | 0.86553 | 59.2133 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44701 | 0.36736 | 44701 | 0.38056 | 0.31667 | EXT DI4 fault | 0.034833 | 0.86553 | 36.3346 | Manually reset & turn on inverter
Hindupur | May | Inverter 24 | Ground fault | 1205.16 | 44701 | 0.36875 | 44701 | 0.38333 | 0.35 | EXT DI4 fault | 0.04375 | 0.86553 | 45.6356 | Manually reset & turn on inverter
Hindupur | May | Inverter 22 | Ground fault | 1190.64 | 44701 | 0.40625 | 44701 | 0.41528 | 0.21667 | EXT DI4 fault | 0.0936 | 0.86553 | 96.4578 | Manually reset & turn on inverter
Hindupur | May | Inverter 35 | Ground fault | 1136.03 | 44701 | 0.43333 | 44701 | 0.45417 | 0.5 | EXT DI4 fault | 0.1235 | 0.86553 | 121.4333 | Manually reset & turn on inverter
Hindupur | May | Inverter 01 | Ground fault | 1205.16 | 44701 | 0.44236 | 44701 | 0.47083 | 0.68333 | EXT DI4 fault | 0.17288 | 0.86553 | 180.3345 | Manually reset & turn on inverter
Hindupur | May | Inverter 11 | Ground fault | 1205.16 | 44701 | 0.50417 | 44701 | 0.51181 | 0.18333 | EXT DI4 fault | 0.072233 | 0.86553 | 75.3465 | Manually reset & turn on inverter
Hindupur | May | Inverter 37 | Ground fault | 1195.43 | 44701 | 0.56597 | 44701 | 0.58125 | 0.36667 | EXT DI4 fault | 0.091667 | 0.86553 | 94.8455 | Manually reset & turn on inverter
Hindupur | May | Inverter 18 | Ground fault | 1190.64 | 44701 | 0.65764 | 44701 | 0.66806 | 0.25 | EXT DI4 fault | 0.13675 | 0.86553 | 140.9252 | Manually reset & turn on inverter
Hindupur | May | Inverter 06 | Ground fault | 1205.16 | 44701 | 0.66667 | 44701 | 0.6875 | 0.5 | EXT DI4 fault | 0.1915 | 0.86553 | 199.7535 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44701 | 0.66806 | 44701 | 0.67431 | 0.15 | EXT DI4 fault | 0.0582 | 0.86553 | 60.7084 | Manually reset & turn on inverter
Hindupur | May | Inverter 01 | Ground fault | 1205.16 | 44702 | 0.34931 | 44702 | 0.35208 | 0.066667 | EXT DI4 fault | 0.014867 | 0.83874 | 15.0275 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44703 | 0.29306 | 44703 | 0.3125 | 0.46667 | EXT DI4 fault | 0.065333 | 0.825 | 64.9582 | Manually reset & turn on inverter
Hindupur | May | Inverter 03 | Ground fault | 1205.16 | 44703 | 0.29653 | 44703 | 0.31736 | 0.5 | EXT DI4 fault | 0.0785 | 0.825 | 78.0493 | Manually reset & turn on inverter
Hindupur | May | Inverter 25 | Ground fault | 1195.43 | 44703 | 0.4125 | 44703 | 0.42292 | 0.25 | EXT DI4 fault | 0.1925 | 0.825 | 189.8494 | Manually reset & turn on inverter
Hindupur | May | Inverter 12 | Ground fault | 1205.16 | 44703 | 0.59306 | 44703 | 0.60625 | 0.31667 | EXT DI4 fault | 0.22167 | 0.825 | 220.3939 | Manually reset & turn on inverter
Hindupur | May | Inverter 32 | Ground fault | 1195.43 | 44704 | 0.26597 | 44704 | 0.27153 | 0.13333 | EXT DI4 fault | 0.074667 | 0.77833 | 69.4725 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44704 | 0.27222 | 44704 | 0.27639 | 0.1 | EXT DI4 fault | 0.073 | 0.77833 | 68.4746 | Manually reset & turn on inverter
Hindupur | May | Inverter 03 | Ground fault | 1205.16 | 44704 | 0.46042 | 44704 | 0.46389 | 0.083333 | EXT DI4 fault | 0.070083 | 0.77833 | 65.7387 | Manually reset & turn on inverter
Hindupur | May | Inverter 09 | Ground fault | 1205.16 | 44704 | 0.5 | 44704 | 0.50556 | 0.13333 | EXT DI4 fault | 0.13067 | 0.77833 | 122.5664 | Manually reset & turn on inverter
Hindupur | May | Inverter 03 | Ground fault | 1205.16 | 44704 | 0.51181 | 44704 | 0.51528 | 0.083333 | EXT DI4 fault | 0.066417 | 0.77833 | 62.2994 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44704 | 0.52014 | 44704 | 0.52569 | 0.13333 | EXT DI4 fault | 0.013667 | 0.77833 | 12.8194 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44704 | 0.55 | 44704 | 0.55903 | 0.21667 | EXT DI4 fault | 0.21212 | 0.77833 | 198.9671 | Manually reset & turn on inverter
Hindupur | May | Inverter 28 | Ground fault | 1195.43 | 44704 | 0.55 | 44704 | 0.55486 | 0.11667 | EXT DI4 fault | 0.11107 | 0.77833 | 103.3403 | Manually reset & turn on inverter
Hindupur | May | Inverter 31 | Ground fault | 1188 | 44704 | 0.55139 | 44704 | 0.55694 | 0.13333 | EXT DI4 fault | 0.013693 | 0.77833 | 12.6616 | Manually reset & turn on inverter
Hindupur | May | Inverter 18 | Ground fault | 1190.64 | 44704 | 0.57847 | 44704 | 0.58472 | 0.15 | EXT DI4 fault | 0.13425 | 0.77833 | 124.4104 | Manually reset & turn on inverter
Hindupur | May | Inverter 29 | Ground fault | 1195.43 | 44705 | 0.27361 | 44705 | 0.28056 | 0.16667 | EXT DI4 fault | 0.14333 | 0.77333 | 132.5057 | Manually reset & turn on inverter
Hindupur | May | Inverter 29 | Ground fault | 1195.43 | 44705 | 0.44028 | 44705 | 0.44722 | 0.16667 | EXT DI4 fault | 0.094833 | 0.77333 | 87.6695 | Manually reset & turn on inverter
Hindupur | May | Inverter 29 | Ground fault | 1195.43 | 44705 | 0.44931 | 44705 | 0.45972 | 0.25 | EXT DI4 fault | 0.1765 | 0.77333 | 163.1669 | Manually reset & turn on inverter
Hindupur | May | Inverter 31 | Ground fault | 1188 | 44706 | 0.30069 | 44706 | 0.30972 | 0.21667 | EXT DI4 fault | 0.04485 | 0.79557 | 42.3896 | Manually reset & turn on inverter
Hindupur | May | Inverter 03 | Ground fault | 1205.16 | 44706 | 0.43333 | 44706 | 0.44236 | 0.21667 | EXT DI4 fault | 0.1859 | 0.79557 | 178.2398 | Manually reset & turn on inverter
Hindupur | May | Inverter 28 | Ground fault | 1195.43 | 44707 | 0.2625 | 44707 | 0.27917 | 0.4 | EXT DI4 fault | 0.244 | 0.78361 | 228.5664 | Manually reset & turn on inverter
Hindupur | May | Inverter 29 | Ground fault | 1195.43 | 44707 | 0.27222 | 44707 | 0.29097 | 0.45 | EXT DI4 fault | 0.04545 | 0.78361 | 42.5752 | Manually reset & turn on inverter
Hindupur | May | Inverter 13 | Ground fault | 1205.16 | 44711 | 0.26736 | 44711 | 0.27431 | 0.16667 | EXT DI4 fault | 0.10333 | 0.79165 | 98.5861 | Manually reset & turn on inverter
Hindupur | May | Inverter 20 | Ground fault | 1205.16 | 44712 | 0.47847 | 44712 | 0.50139 | 0.55 | EXT DI4 fault | 0.38995 | 0.79695 | 374.5286 | Manually reset & turn on inverter
Hindupur | May | SCB.13.04 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.46667 | 5.1333 | String fault | 1.7402 | 0.79695 | 10.0686 | Inv-13 SCB-4 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.13.04 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.47569 | 5.35 | String fault | 1.8779 | 0.79695 | 10.865 | Inv-13 SCB-4 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.13.05 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.48889 | 5.6667 | String fault | 2.0513 | 0.79695 | 11.8687 | Inv-13 SCB-5 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.13.07 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.49861 | 5.9 | String fault | 2.2361 | 0.79695 | 12.9378 | Inv-13 SCB-7 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.14.05 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.52083 | 6.4333 | String fault | 2.7728 | 0.79695 | 16.0428 | Inv-14 SCB-5 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.14.06 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.53125 | 6.6833 | String fault | 2.9808 | 0.79695 | 17.2463 | Inv-14 SCB-6 one string fault, replaced damaged MC4 with new one.
Hindupur | May | SCB.14.07 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.54097 | 6.9167 | String fault | 3.1817 | 0.79695 | 18.4087 | Inv-14 SCB-7 one string fault, Replaced with new Fuse.now ok
Hindupur | May | SCB.31.08 | String fault | 7.26 | 44712 | 0.25278 | 44712 | 0.56458 | 7.4833 | String fault | 3.5471 | 0.79695 | 20.523 | Inv-31 SCB-8 one string fault, Replaced with new Fuse.now ok
Hindupur | June | Inverter 24 | Ground fault | 1205.16 | 44713 | 0.30556 | 44713 | 0.31111 | 0.13333 | EXT DI4 fault | 0.032933 | 0.79754 | 31.6544 | Manually reset & turn on inverter
Hindupur | June | Inverter 22 | Ground fault | 1190.64 | 44713 | 0.33542 | 44713 | 0.33958 | 0.1 | EXT DI4 fault | 0.0382 | 0.79754 | 36.2742 | Manually reset & turn on inverter
Hindupur | June | Inverter 33 | Ground fault | 1195.43 | 44713 | 0.51181 | 44713 | 0.51458 | 0.066667 | EXT DI4 fault | 0.033333 | 0.79754 | 31.7802 | Manually reset & turn on inverter
Hindupur | June | Inverter 34 | Ground fault | 1195.43 | 44713 | 0.51181 | 44713 | 0.51458 | 0.066667 | EXT DI4 fault | 0.033333 | 0.79754 | 31.7802 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44713 | 0.51181 | 44713 | 0.51458 | 0.066667 | EXT DI4 fault | 0.033333 | 0.79754 | 30.201 | Manually reset & turn on inverter
Hindupur | June | Inverter 36 | Ground fault | 1225.13 | 44713 | 0.51181 | 44713 | 0.51458 | 0.066667 | EXT DI4 fault | 0.033333 | 0.79754 | 32.5697 | Manually reset & turn on inverter
Hindupur | June | Inverter 12 | Ground fault | 1205.16 | 44713 | 0.52639 | 44713 | 0.54028 | 0.33333 | EXT DI4 fault | 0.23667 | 0.79754 | 227.4758 | Manually reset & turn on inverter
Hindupur | June | Inverter 28 | Ground fault | 1195.43 | 44713 | 0.53125 | 44713 | 0.53472 | 0.083333 | EXT DI4 fault | 0.08325 | 0.79754 | 79.371 | Manually reset & turn on inverter
Hindupur | June | Inverter 08 | Ground fault | 1205.16 | 44713 | 0.53403 | 44713 | 0.54028 | 0.15 | EXT DI4 fault | 0.10095 | 0.79754 | 97.0297 | Manually reset & turn on inverter
Hindupur | June | Inverter 25 | Ground fault | 1195.43 | 44713 | 0.56736 | 44713 | 0.57083 | 0.083333 | EXT DI4 fault | 0.078333 | 0.79754 | 74.6834 | Manually reset & turn on inverter
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44714 | 0.32569 | 44714 | 0.33056 | 0.11667 | EXT DI4 fault | 0.033367 | 0.79372 | 31.9174 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44714 | 0.60972 | 44714 | 0.61736 | 0.18333 | EXT DI4 fault | 0.11422 | 0.79372 | 102.9885 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44714 | 0.62917 | 44714 | 0.63889 | 0.23333 | EXT DI4 fault | 0.13113 | 0.79372 | 118.2422 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44714 | 0.65278 | 44714 | 0.65625 | 0.083333 | EXT DI4 fault | 0.036833 | 0.79372 | 33.2124 | Manually reset & turn on inverter
Hindupur | June | Inverter 14 | Ground fault | 1205.16 | 44715 | 0.25139 | 44715 | 0.3125 | 1.4667 | EXT DI4 fault | 0.13053 | 0.78202 | 123.0221 | Manually reset & turn on inverter (Due to servers issue all inverters condition checked physically, so that delay happened)
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44718 | 0.27083 | 44718 | 0.28611 | 0.36667 | EXT DI4 fault | 0.014667 | 0.79584 | 14.0669 | Manually reset & turn on inverter
Hindupur | June | Inverter 15 | Ground fault | 1205.16 | 44718 | 0.27292 | 44718 | 0.30625 | 0.8 | EXT DI4 fault | 0.0568 | 0.79584 | 54.4774 | Manually reset & turn on inverter
Hindupur | June | Inverter 22 | Ground fault | 1190.64 | 44718 | 0.27292 | 44718 | 0.29167 | 0.45 | EXT DI4 fault | 0.0234 | 0.79584 | 22.1728 | Manually reset & turn on inverter
Hindupur | June | Inverter 18 | Ground fault | 1190.64 | 44718 | 0.27431 | 44718 | 0.30833 | 0.81667 | EXT DI4 fault | 0.06125 | 0.79584 | 58.0377 | Manually reset & turn on inverter
Hindupur | June | Inverter 26 | Ground fault | 1195.43 | 44718 | 0.27431 | 44718 | 0.30417 | 0.71667 | EXT DI4 fault | 0.050883 | 0.79584 | 48.4087 | Manually reset & turn on inverter
Hindupur | June | Inverter 37 | Ground fault | 1195.43 | 44718 | 0.27431 | 44718 | 0.28819 | 0.33333 | EXT DI4 fault | 0.016 | 0.79584 | 15.2219 | Manually reset & turn on inverter
Hindupur | June | Inverter 38 | Ground fault | 1195.43 | 44718 | 0.27431 | 44718 | 0.28819 | 0.33333 | EXT DI4 fault | 0.016 | 0.79584 | 15.2219 | Manually reset & turn on inverter
Hindupur | June | Inverter 29 | Ground fault | 1195.43 | 44718 | 0.28472 | 44718 | 0.29236 | 0.18333 | EXT DI4 fault | 0.013383 | 0.79584 | 12.7324 | Manually reset & turn on inverter
Hindupur | June | Inverter 05 | Ground fault | 1205.16 | 44718 | 0.28472 | 44718 | 0.28958 | 0.11667 | EXT DI4 fault | 0.0079333 | 0.79584 | 7.6089 | Manually reset & turn on inverter
Hindupur | June | Inverter 32 | Ground fault | 1195.43 | 44718 | 0.31667 | 44718 | 0.32292 | 0.15 | EXT DI4 fault | 0.0237 | 0.79584 | 22.5474 | Manually reset & turn on inverter
Hindupur | June | Inverter 24 | Ground fault | 1205.16 | 44718 | 0.33194 | 44718 | 0.34097 | 0.21667 | EXT DI4 fault | 0.068467 | 0.79584 | 65.667 | Manually reset & turn on inverter
Hindupur | June | Inverter 12 | Ground fault | 1205.16 | 44718 | 0.35139 | 44718 | 0.35625 | 0.11667 | EXT DI4 fault | 0.047367 | 0.79584 | 45.4298 | Manually reset & turn on inverter
Hindupur | June | Inverter 16 | Ground fault | 1205.16 | 44718 | 0.3875 | 44718 | 0.39653 | 0.21667 | EXT DI4 fault | 0.13087 | 0.79584 | 125.5155 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44718 | 0.41458 | 44718 | 0.425 | 0.25 | EXT DI4 fault | 0.182 | 0.79584 | 174.5579 | Manually reset & turn on inverter
Hindupur | June | Inverter 11 | Ground fault | 1205.16 | 44718 | 0.42361 | 44718 | 0.42847 | 0.11667 | EXT DI4 fault | 0.089717 | 0.79584 | 86.0481 | Manually reset & turn on inverter
Hindupur | June | Inverter 07 | Ground fault | 1205.16 | 44718 | 0.42569 | 44718 | 0.44097 | 0.36667 | EXT DI4 fault | 0.29077 | 0.79584 | 278.8771 | Manually reset & turn on inverter
Hindupur | June | Inverter 09 | Ground fault | 1205.16 | 44718 | 0.43264 | 44718 | 0.43542 | 0.066667 | EXT DI4 fault | 0.052867 | 0.79584 | 50.7049 | Manually reset & turn on inverter
Hindupur | June | Inverter 18 | Ground fault | 1190.64 | 44718 | 0.44444 | 44718 | 0.45208 | 0.18333 | EXT DI4 fault | 0.1529 | 0.79584 | 144.881 | Manually reset & turn on inverter
Hindupur | June | Inverter 06 | Ground fault | 1205.16 | 44718 | 0.44583 | 44718 | 0.44861 | 0.066667 | EXT DI4 fault | 0.0552 | 0.79584 | 52.9428 | Manually reset & turn on inverter
Hindupur | June | Inverter 07 | Ground fault | 1205.16 | 44718 | 0.44931 | 44718 | 0.45556 | 0.15 | EXT DI4 fault | 0.12765 | 0.79584 | 122.4303 | Manually reset & turn on inverter
Hindupur | June | Inverter 06 | Ground fault | 1205.16 | 44718 | 0.47569 | 44718 | 0.47917 | 0.083333 | EXT DI4 fault | 0.075583 | 0.79584 | 72.4927 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44718 | 0.56389 | 44718 | 0.57153 | 0.18333 | EXT DI4 fault | 0.1155 | 0.79584 | 110.7772 | Manually reset & turn on inverter
Hindupur | June | Inverter 21 | Ground fault | 1190.64 | 44718 | 0.57847 | 44718 | 0.58542 | 0.16667 | EXT DI4 fault | 0.13817 | 0.79584 | 130.9204 | Manually reset & turn on inverter
Hindupur | June | Inverter 13 | Ground fault | 1205.16 | 44718 | 0.58056 | 44718 | 0.59236 | 0.28333 | EXT DI4 fault | 0.17765 | 0.79584 | 170.3858 | Manually reset & turn on inverter
Hindupur | June | Inverter 31 | Ground fault | 1188 | 44719 | 0.26319 | 44719 | 0.275 | 0.28333 | EXT DI4 fault | 0.015017 | 0.80112 | 14.2918 | Manually reset & turn on inverter
Hindupur | June | Inverter 12 | Ground fault | 1205.16 | 44719 | 0.26736 | 44719 | 0.275 | 0.18333 | EXT DI4 fault | 0.010083 | 0.80112 | 9.7352 | Manually reset & turn on inverter
Hindupur | June | Inverter 04 | Ground fault | 1205.16 | 44719 | 0.27222 | 44719 | 0.28403 | 0.28333 | EXT DI4 fault | 0.016717 | 0.80112 | 16.1396 | Manually reset & turn on inverter
Hindupur | June | Inverter 12 | Ground fault | 1205.16 | 44719 | 0.27986 | 44719 | 0.29167 | 0.28333 | EXT DI4 fault | 0.01785 | 0.80112 | 17.2338 | Manually reset & turn on inverter
Hindupur | June | Inverter 37 | Ground fault | 1195.43 | 44719 | 0.28264 | 44719 | 0.2875 | 0.11667 | EXT DI4 fault | 0.0071167 | 0.80112 | 6.8155 | Manually reset & turn on inverter
Hindupur | June | Inverter 04 | Ground fault | 1205.16 | 44720 | 0.25694 | 44720 | 0.28403 | 0.65 | EXT DI4 fault | 0.03055 | 0.79984 | 29.4483 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44720 | 0.28056 | 44720 | 0.28958 | 0.21667 | EXT DI4 fault | 0.02275 | 0.79984 | 21.9296 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44720 | 0.30139 | 44720 | 0.30625 | 0.11667 | EXT DI4 fault | 0.021817 | 0.79984 | 21.0299 | Manually reset & turn on inverter
Hindupur | June | Inverter 30 | Ground fault | 1202.85 | 44720 | 0.30486 | 44720 | 0.31389 | 0.21667 | EXT DI4 fault | 0.046583 | 0.79984 | 44.8173 | Manually reset & turn on inverter
Hindupur | June | Inverter 18 | Ground fault | 1190.64 | 44720 | 0.38889 | 44720 | 0.39167 | 0.066667 | EXT DI4 fault | 0.0408 | 0.79984 | 38.8548 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44720 | 0.39097 | 44720 | 0.39514 | 0.1 | EXT DI4 fault | 0.0632 | 0.79984 | 60.9208 | Manually reset & turn on inverter
Hindupur | June | Inverter 03 | Ground fault | 1205.16 | 44721 | 0.275 | 44721 | 0.27917 | 0.1 | EXT DI4 fault | 0.0056 | 0.80368 | 5.4239 | Manually reset & turn on inverter
Hindupur | June | Inverter 08 | Ground fault | 1205.16 | 44723 | 0.36944 | 44723 | 0.37153 | 0.05 | EXT DI4 fault | 0.02455 | 0.79832 | 23.6197 | Manually reset & turn on inverter
Hindupur | June | Inverter 19 | Ground fault | 1219.68 | 44725 | 0.29028 | 44725 | 0.29653 | 0.15 | EXT DI4 fault | 0.01005 | 0.81179 | 9.9508 | Manually reset & turn on inverter
Hindupur | June | Inverter 11 | Ground fault | 1205.16 | 44725 | 0.29514 | 44725 | 0.30278 | 0.18333 | EXT DI4 fault | 0.01485 | 0.81179 | 14.5283 | Manually reset & turn on inverter
Hindupur | June | Inverter 38 | Ground fault | 1195.43 | 44725 | 0.3 | 44725 | 0.30417 | 0.1 | EXT DI4 fault | 0.0089 | 0.81179 | 8.6369 | Manually reset & turn on inverter
Hindupur | June | Inverter 38 | Ground fault | 1195.43 | 44725 | 0.31597 | 44725 | 0.32014 | 0.1 | EXT DI4 fault | 0.0136 | 0.81179 | 13.198 | Manually reset & turn on inverter
Hindupur | June | Inverter 24 | Ground fault | 1205.16 | 44725 | 0.32917 | 44725 | 0.33056 | 0.033333 | EXT DI4 fault | 0.0046333 | 0.81179 | 4.533 | Manually reset & turn on inverter
Hindupur | June | Inverter 13 | Ground fault | 1205.16 | 44725 | 0.35278 | 44725 | 0.35694 | 0.1 | EXT DI4 fault | 0.0281 | 0.81179 | 27.4913 | Manually reset & turn on inverter
Hindupur | June | B-8 IDT-2 | WTI-2 & MT Relay operated on high temperature | 2383.43 | 44726 | 0.57222 | 44726 | 0.59167 | 0.46667 | WTI-2 mallfunction | 0.31692 | 0.79947 | 603.8784 | As WTI-2 sesnor got failed, Relay trip contacts kept open & charged IDT-2
Hindupur | June | B-8 IDT-2 | WTI-2 & MT Relay operated on high temperature | 2383.43 | 44726 | 0.60556 | 44726 | 0.60833 | 0.066667 | While carrying out releasing of trip contacts of WTI-2, by mistake happened NC of trip contacts | 0.043416 | 0.79947 | 82.7283 | Immediately breaker charged & restored IDT-2 .
Hindupur | June | Inverter 12 | Ground fault | 1205.16 | 44727 | 0.28472 | 44727 | 0.30833 | 0.56667 | EXT DI4 fault | 0.011333 | 0.85212 | 11.6387 | Manually reset & turn on inverter
Hindupur | June | Inverter 18 | Ground fault | 1190.64 | 44727 | 0.31528 | 44727 | 0.31667 | 0.033333 | EXT DI4 fault | 0.0013 | 0.85212 | 1.3189 | Manually reset & turn on inverter
Hindupur | June | Inverter 15 | Ground fault | 1205.16 | 44727 | 0.31736 | 44727 | 0.325 | 0.18333 | EXT DI4 fault | 0.0084333 | 0.85212 | 8.6606 | Manually reset & turn on inverter
Hindupur | June | Inverter 24 | Ground fault | 1205.16 | 44727 | 0.31806 | 44727 | 0.32847 | 0.25 | EXT DI4 fault | 0.012 | 0.85212 | 12.3233 | Manually reset & turn on inverter
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44727 | 0.34722 | 44727 | 0.34931 | 0.05 | EXT DI4 fault | 0.00585 | 0.85212 | 6.0076 | Manually reset & turn on inverter
Hindupur | June | Inverter 04 | Ground fault | 1205.16 | 44727 | 0.35417 | 44727 | 0.35903 | 0.11667 | EXT DI4 fault | 0.01645 | 0.85212 | 16.8933 | Manually reset & turn on inverter
Hindupur | June | Inverter 11 | Ground fault | 1205.16 | 44727 | 0.35833 | 44727 | 0.36389 | 0.13333 | EXT DI4 fault | 0.020267 | 0.85212 | 20.8128 | Manually reset & turn on inverter
Hindupur | June | Inverter 04 | Ground fault | 1205.16 | 44727 | 0.36181 | 44727 | 0.36806 | 0.15 | EXT DI4 fault | 0.02505 | 0.85212 | 25.725 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44727 | 0.38611 | 44727 | 0.38819 | 0.05 | EXT DI4 fault | 0.01285 | 0.85212 | 12.4393 | Manually reset & turn on inverter
Hindupur | June | Inverter 39 | Ground fault | 1195.43 | 44727 | 0.46042 | 44727 | 0.4625 | 0.05 | EXT DI4 fault | 0.01875 | 0.85212 | 19.0998 | Manually reset & turn on inverter
Hindupur | June | Inverter 25 | Ground fault | 1195.43 | 44727 | 0.57917 | 44727 | 0.58194 | 0.066667 | EXT DI4 fault | 0.025267 | 0.85212 | 25.738 | Manually reset & turn on inverter
Hindupur | June | Inverter 26 | Ground fault | 1195.43 | 44728 | 0.55556 | 44728 | 0.56806 | 0.3 | EXT DI4 fault | 0.2682 | 0.80945 | 259.5211 | Manually reset & turn on inverter
Hindupur | June | Inverter 01 | Ground fault | 1205.16 | 44729 | 0.26736 | 44729 | 0.28542 | 0.43333 | EXT DI4 fault | 0.0234 | 0.76695 | 21.6285 | Manually reset & turn on inverter
Hindupur | June | Inverter 02 | Ground fault | 1205.16 | 44729 | 0.26736 | 44729 | 0.28611 | 0.45 | EXT DI4 fault | 0.0252 | 0.76695 | 23.2922 | Manually reset & turn on inverter
Hindupur | June | Inverter 38 | Ground fault | 1195.43 | 44729 | 0.26736 | 44729 | 0.2875 | 0.48333 | EXT DI4 fault | 0.029 | 0.76695 | 26.5881 | Manually reset & turn on inverter
Hindupur | June | Inverter 39 | Ground fault | 1195.43 | 44729 | 0.26736 | 44729 | 0.30694 | 0.95 | EXT DI4 fault | 0.12635 | 0.76695 | 115.8415 | Manually reset & turn on inverter
Hindupur | June | Inverter 19 | Ground fault | 1219.68 | 44729 | 0.26736 | 44729 | 0.29653 | 0.7 | EXT DI4 fault | 0.0665 | 0.76695 | 62.206 | Manually reset & turn on inverter
Hindupur | June | Inverter 11 | Ground fault | 1205.16 | 44729 | 0.27778 | 44729 | 0.28125 | 0.083333 | EXT DI4 fault | 0.0056667 | 0.76695 | 5.2377 | Manually reset & turn on inverter
Hindupur | June | Inverter 05 | Ground fault | 1205.16 | 44729 | 0.27917 | 44729 | 0.28194 | 0.066667 | EXT DI4 fault | 0.0053333 | 0.76695 | 4.9296 | Manually reset & turn on inverter
Hindupur | June | Inverter 20 | Ground fault | 1205.16 | 44729 | 0.28056 | 44729 | 0.29722 | 0.4 | EXT DI4 fault | 0.0572 | 0.76695 | 52.8695 | Manually reset & turn on inverter
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44729 | 0.28056 | 44729 | 0.29097 | 0.25 | EXT DI4 fault | 0.02975 | 0.76695 | 27.4977 | Manually reset & turn on inverter
Hindupur | June | Inverter 21 | Ground fault | 1190.64 | 44729 | 0.28194 | 44729 | 0.28611 | 0.1 | EXT DI4 fault | 0.0102 | 0.76695 | 9.3142 | Manually reset & turn on inverter
Hindupur | June | Inverter 21 | Ground fault | 1190.64 | 44729 | 0.29167 | 44729 | 0.29861 | 0.16667 | EXT DI4 fault | 0.031333 | 0.76695 | 28.6122 | Manually reset & turn on inverter
Hindupur | June | Inverter 38 | Ground fault | 1195.43 | 44729 | 0.29167 | 44729 | 0.30764 | 0.38333 | EXT DI4 fault | 0.086633 | 0.76695 | 79.4281 | Manually reset & turn on inverter
Hindupur | June | Inverter 28 | Ground fault | 1195.43 | 44729 | 0.29236 | 44729 | 0.30208 | 0.23333 | EXT DI4 fault | 0.046433 | 0.76695 | 42.5715 | Manually reset & turn on inverter
Hindupur | June | Inverter 25 | Ground fault | 1195.43 | 44729 | 0.29861 | 44729 | 0.30417 | 0.13333 | EXT DI4 fault | 0.031067 | 0.76695 | 28.4829 | Manually reset & turn on inverter
Hindupur | June | Inverter 11 | Ground fault | 1205.16 | 44729 | 0.30972 | 44729 | 0.31528 | 0.13333 | EXT DI4 fault | 0.0436 | 0.76695 | 40.2992 | Manually reset & turn on inverter
Hindupur | June | Inverter 13 | Ground fault | 1205.16 | 44729 | 0.33611 | 44729 | 0.34097 | 0.11667 | EXT DI4 fault | 0.043167 | 0.76695 | 39.8986 | Manually reset & turn on inverter
Hindupur | June | Inverter 13 | Ground fault | 1205.16 | 44729 | 0.47014 | 44729 | 0.47361 | 0.083333 | EXT DI4 fault | 0.047 | 0.76695 | 43.4418 | Manually reset & turn on inverter
Hindupur | June | Inverter 03 | Ground fault | 1205.16 | 44729 | 0.47639 | 44729 | 0.48056 | 0.1 | EXT DI4 fault | 0.098 | 0.76695 | 90.5807 | Manually reset & turn on inverter
Hindupur | June | Inverter 13 | Ground fault | 1205.16 | 44729 | 0.48681 | 44729 | 0.49097 | 0.1 | EXT DI4 fault | 0.0788 | 0.76695 | 72.8343 | Manually reset & turn on inverter
Hindupur | June | Inverter 16 | Ground fault | 1205.16 | 44729 | 0.49722 | 44729 | 0.50625 | 0.21667 | EXT DI4 fault | 0.18048 | 0.76695 | 166.8194 | Manually reset & turn on inverter
Hindupur | June | Inverter 09 | Ground fault | 1205.16 | 44729 | 0.53194 | 44729 | 0.54653 | 0.35 | EXT DI4 fault | 0.2562 | 0.76695 | 236.8038 | Manually reset & turn on inverter
Hindupur | June | Inverter 32 | Ground fault | 1195.43 | 44730 | 0.30556 | 44730 | 0.31181 | 0.15 | EXT DI4 fault | 0.039 | 0.81102 | 37.8114 | Manually reset & turn on inverter
Hindupur | June | Inverter 40 | Ground fault | 1195.43 | 44730 | 0.36111 | 44730 | 0.36736 | 0.15 | EXT DI4 fault | 0.04755 | 0.81102 | 46.1008 | Manually reset & turn on inverter
Hindupur | June | Inverter 31 | Ground fault | 1188 | 44730 | 0.64653 | 44730 | 0.64931 | 0.066667 | EXT DI4 fault | 0.0156 | 0.81102 | 15.0305 | Manually reset & turn on inverter
Hindupur | June | Inverter 40 | Ground fault | 1195.43 | 44731 | 0.27014 | 44731 | 0.27708 | 0.16667 | EXT DI4 fault | 0.0115 | 0.80734 | 11.0988 | Manually reset & turn on inverter
Hindupur | June | Inverter 05 | Ground fault | 1205.16 | 44731 | 0.27083 | 44731 | 0.27431 | 0.083333 | EXT DI4 fault | 0.0049167 | 0.80734 | 4.7838 | Manually reset & turn on inverter
Hindupur | June | Inverter 31 | Ground fault | 1188 | 44731 | 0.29514 | 44731 | 0.29861 | 0.083333 | EXT DI4 fault | 0.012417 | 0.80734 | 11.9091 | Manually reset & turn on inverter
Hindupur | June | Inverter 29 | Ground fault | 1195.43 | 44731 | 0.30625 | 44731 | 0.30972 | 0.083333 | EXT DI4 fault | 0.018333 | 0.80734 | 17.6938 | Manually reset & turn on inverter
Hindupur | June | Inverter 31 | Ground fault | 1188 | 44731 | 0.31181 | 44731 | 0.31528 | 0.083333 | EXT DI4 fault | 0.018917 | 0.80734 | 18.1433 | Manually reset & turn on inverter
Hindupur | June | Inverter 27 | Ground fault | 1195.43 | 44731 | 0.32083 | 44731 | 0.32847 | 0.18333 | EXT DI4 fault | 0.052617 | 0.80734 | 50.7813 | Manually reset & turn on inverter
Hindupur | June | Inverter 31 | Ground fault | 1188 | 44731 | 0.32708 | 44731 | 0.33264 | 0.13333 | EXT DI4 fault | 0.034933 | 0.80734 | 33.5052 | Manually reset & turn on inverter
Hindupur | June | Inverter 36 | Ground fault | 1225.13 | 44731 | 0.42361 | 44731 | 0.43125 | 0.18333 | EXT DI4 fault | 0.13915 | 0.80734 | 137.6326 | Manually reset & turn on inverter
Hindupur | June | Inverter 05 | Ground fault | 1205.16 | 44732 | 0.48264 | 44732 | 0.48889 | 0.15 | EXT DI4 fault | 0.08535 | 0.82019 | 84.3649 | Manually reset & turn on inverter
Hindupur | June | Inverter 09 | Ground fault | 1205.16 | 44732 | 0.53819 | 44732 | 0.54097 | 0.066667 | EXT DI4 fault | 0.0624 | 0.82019 | 61.6798 | Manually reset & turn on inverter
Hindupur | June | SCB.05.03 | String fault | 7.26 | 44732 | 0.26042 | 44732 | 0.45833 | 4.75 | String fault | 1.7765 | 0.82019 | 10.5783 | Inv-05 SCB-3 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.06.03 | String fault | 7.26 | 44732 | 0.26042 | 44732 | 0.47917 | 5.25 | String fault | 2.1368 | 0.82019 | 12.7234 | Inv-6 SCB-3 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.05.04 | String fault | 7.26 | 44732 | 0.26042 | 44732 | 0.50903 | 5.9667 | String fault | 2.6134 | 0.82019 | 15.5617 | Inv-5 SCB-4 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.01.06 | String fault | 7.26 | 44732 | 0.26042 | 44732 | 0.53819 | 6.6667 | String fault | 3.1867 | 0.82019 | 18.9752 | Inv-1 SCB-6 one string fault, replaced damaged MC4 with new one.
Hindupur | June | Inverter 35 | Short circuit fault | 1136.03 | 44734 | 0.27847 | 44734 | 0.29167 | 0.31667 | short circuit | 0.031033 | 0.81527 | 28.7423 | Manually reset & turn on inverter
Hindupur | June | Inverter 35 | Ground fault | 1136.03 | 44734 | 0.42639 | 44734 | 0.43333 | 0.16667 | EXT DI4 fault | 0.107 | 0.81527 | 99.1008 | Manually reset & turn on inverter
Hindupur | June | SCB.35.02 | String fault | 7.26 | 44734 | 0.43403 | 44734 | 0.48958 | 1.3333 | String fault | 0.89067 | 0.81527 | 5.2718 | Inv-35 SCB-2 one string fault, replaced damaged MC4 with new one.
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44734 | 0.72708 | 44734 | 0.74931 | 0.53333 | EXT DI4 fault | 0.0144 | 0.81527 | 14.1485 | Manually reset & turn on inverter
Hindupur | June | Inverter 26 | Ground fault | 1195.43 | 44735 | 0.34375 | 44735 | 0.34583 | 0.05 | EXT DI4 fault | 0.01175 | 0.85441 | 12.0013 | Manually reset & turn on inverter
Hindupur | June | Inverter 39 | Ground fault | 1195.43 | 44736 | 0.27083 | 44736 | 0.27292 | 0.05 | EXT DI4 fault | 0.00265 | 0.80917 | 2.5634 | Manually reset & turn on inverter
Hindupur | June | SCB.37.01 | String fault | 7.26 | 44736 | 0.26042 | 44736 | 0.48264 | 5.3333 | String fault | 2.688 | 0.80917 | 15.7908 | Inv-37 SCB-1 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.37.02 | String fault | 7.26 | 44736 | 0.26042 | 44736 | 0.49167 | 5.55 | String fault | 2.8582 | 0.80917 | 16.791 | Inv-37 SCB-2 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.37.06 | String fault | 7.26 | 44736 | 0.26042 | 44736 | 0.52778 | 6.4167 | String fault | 3.5612 | 0.80917 | 20.9208 | Inv-37 SCB-6 one string fault, replaced damaged MC4 with new one.
Hindupur | June | Inverter 03 | Ground fault | 1205.16 | 44737 | 0.54722 | 44737 | 0.54931 | 0.05 | EXT DI4 fault | 0.03755 | 0.8211 | 37.1579 | Manually reset & turn on inverter
Hindupur | June | SCB.09.05 | String fault | 7.26 | 44737 | 0.26042 | 44737 | 0.46875 | 5 | String fault | 2.005 | 0.8211 | 11.9522 | Inv-09 SCB-05 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.09.03 | String fault | 7.26 | 44737 | 0.26042 | 44737 | 0.48125 | 5.3 | String fault | 2.1783 | 0.8211 | 12.9853 | Inv-09 SCB-03 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.09.03 | String fault | 7.26 | 44737 | 0.26042 | 44737 | 0.49236 | 5.5667 | String fault | 2.3992 | 0.8211 | 14.3023 | Inv-09 SCB-03 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.09.03 | String fault | 7.26 | 44737 | 0.26042 | 44737 | 0.50139 | 5.7833 | String fault | 2.5562 | 0.8211 | 15.2382 | Inv-09 SCB-03 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.09.03 | String fault | 7.26 | 44737 | 0.26042 | 44737 | 0.52639 | 6.3833 | String fault | 2.9746 | 0.8211 | 17.7324 | Inv-09 SCB-03 one string fault, replaced damaged MC4 with new one.
Hindupur | June | Inverter 09 | Ground fault | 1205.16 | 44738 | 0.28611 | 44738 | 0.28958 | 0.083333 | EXT DI4 fault | 0.012 | 0.81319 | 11.7603 | Manually reset & turn on inverter
Hindupur | June | Inverter 09 | Ground fault | 1205.16 | 44738 | 0.47569 | 44738 | 0.49444 | 0.45 | EXT DI4 fault | 0.31005 | 0.81319 | 303.8561 | Manually reset & turn on inverter
Hindupur | June | Inverter 30 | Ground fault | 1202.85 | 44738 | 0.68611 | 44738 | 0.69444 | 0.2 | EXT DI4 fault | 0.0216 | 0.81319 | 21.1279 | Manually reset & turn on inverter
Hindupur | June | Inverter 29 | Ground fault | 1195.43 | 44738 | 0.71181 | 44738 | 0.71875 | 0.16667 | EXT DI4 fault | 0.013333 | 0.81319 | 12.9615 | Manually reset & turn on inverter
Hindupur | June | Inverter 27 | Ground fault | 1195.43 | 44739 | 0.26042 | 44739 | 0.27292 | 0.3 | EXT DI4 fault | 0.0081 | 0.84053 | 8.1389 | Manually reset & turn on inverter
Hindupur | June | Inverter 30 | Ground fault | 1202.85 | 44739 | 0.47986 | 44739 | 0.48125 | 0.033333 | EXT DI4 fault | 0.021933 | 0.84053 | 22.1754 | Manually reset & turn on inverter
Hindupur | June | Inverter 29 | Ground fault | 1195.43 | 44739 | 0.48056 | 44739 | 0.48194 | 0.033333 | EXT DI4 fault | 0.0211 | 0.84053 | 21.2013 | Manually reset & turn on inverter
Hindupur | June | SCB.26.06 | String fault | 7.26 | 44739 | 0.26042 | 44739 | 0.53125 | 6.5 | String fault | 2.535 | 0.84053 | 15.4693 | Inv-26 SCB-06 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.40.03 | String fault | 7.26 | 44740 | 0.26389 | 44740 | 0.50208 | 5.7167 | String fault | 1.7607 | 0.84606 | 10.8151 | Inv-40 SCB-03 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.40.04 | String fault | 7.26 | 44740 | 0.26389 | 44740 | 0.51944 | 6.1333 | String fault | 1.9811 | 0.84606 | 12.1685 | Inv-40 SCB-04 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.40.06 | String fault | 7.26 | 44740 | 0.26389 | 44740 | 0.53125 | 6.4167 | String fault | 2.1175 | 0.84606 | 13.0065 | Inv-40 SCB-06 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.30.01 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.48611 | 5.4167 | String fault | 2.8275 | 0.80454 | 16.5154 | Inv-30 SCB-01 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.30.04 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.49167 | 5.55 | String fault | 2.936 | 0.80454 | 17.1489 | Inv-30 SCB-04 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.29.07 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.50833 | 5.95 | String fault | 3.2963 | 0.80454 | 19.2537 | Inv-29 SCB-07 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.29.08 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.52014 | 6.2333 | String fault | 3.5156 | 0.80454 | 20.5346 | Inv-29 SCB-08 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.31.01 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.52917 | 6.45 | String fault | 3.6829 | 0.80454 | 21.5121 | Inv-31 SCB-01 one string fault, replaced damaged MC4 with new one.
Hindupur | June | SCB.31.07 | String fault | 7.26 | 44741 | 0.26042 | 44741 | 0.53819 | 6.6667 | String fault | 3.8067 | 0.80454 | 22.2347 | Inv-31 SCB-07 one string fault, replaced damaged MC4 with new one.
Hindupur | June | Inverter 30 | Ground fault | 1202.85 | 44742 | 0.35903 | 44742 | 0.36111 | 0.05 | EXT DI4 fault | 0.02325 | 0.80365 | 22.4751 | Manually reset & turn on inverter
Hindupur | June | Inverter 03 | Ground fault | 1205.16 | 44742 | 0.70069 | 44742 | 0.70417 | 0.083333 | EXT DI4 fault | 0.0065 | 0.80365 | 6.2954 | Manually reset & turn on inverter
Hindupur | June | Inverter 08 | Ground fault | 1205.16 | 44742 | 0.70069 | 44742 | 0.70278 | 0.05 | EXT DI4 fault | 0.0038 | 0.80365 | 3.6804 | Manually reset & turn on inverter
Hindupur | June | Inverter 10 | Ground fault | 1205.16 | 44742 | 0.72083 | 44742 | 0.72361 | 0.066667 | EXT DI4 fault | 0.010267 | 0.80365 | 9.9435 | Manually reset & turn on inverter
Hindupur | June | SCB.30.04 | String fault | 7.26 | 44742 | 0.26042 | 44742 | 0.47708 | 5.2 | String fault | 1.82 | 0.80365 | 10.6188 | Inv-30 SCB-04 one string fault, replaced damaged Cable with new Cable.
Hindupur | June | SCB.30.07 | String fault | 7.26 | 44742 | 0.26042 | 44742 | 0.4875 | 5.45 | String fault | 1.9892 | 0.80365 | 11.6063 | Inv-30 SCB-07 one string fault, replaced damaged MC4 with new one.
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44743 | 0.67222 | 44743 | 0.67639 | 0.1 | EXT DI4 fault | 0.008 | 0.82117 | 7.9172 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Ground fault | 1195.43 | 44743 | 0.68542 | 44743 | 0.70625 | 0.5 | EXT DI4 fault | 0.018 | 0.82117 | 17.6698 | Manually reset & turn on inverter
Hindupur | July | Inverter 38 | Ground fault | 1195.43 | 44743 | 0.69375 | 44743 | 0.71042 | 0.4 | EXT DI4 fault | 0.0204 | 0.82117 | 20.0258 | Manually reset & turn on inverter
Hindupur | July | Inverter 35 | Ground fault | 1136.03 | 44743 | 0.70903 | 44743 | 0.71806 | 0.21667 | EXT DI4 fault | 0.021883 | 0.82117 | 20.4145 | Manually reset & turn on inverter
Hindupur | July | Inverter 03 | Ground fault | 1205.16 | 44743 | 0.71181 | 44743 | 0.71667 | 0.11667 | EXT DI4 fault | 0.013417 | 0.82117 | 13.2778 | Manually reset & turn on inverter
Hindupur | July | Inverter 38 | Ground fault | 1195.43 | 44743 | 0.71667 | 44743 | 0.72431 | 0.18333 | EXT DI4 fault | 0.021633 | 0.82117 | 21.2365 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44744 | 0.26042 | 44744 | 0.27639 | 0.38333 | EXT DI4 fault | 0.00805 | 0.819 | 7.9456 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Ground fault | 1195.43 | 44744 | 0.26042 | 44744 | 0.27917 | 0.45 | EXT DI4 fault | 0.01035 | 0.819 | 10.1332 | Manually reset & turn on inverter
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44744 | 0.26042 | 44744 | 0.27917 | 0.45 | EXT DI4 fault | 0.01035 | 0.819 | 10.1332 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44744 | 0.28542 | 44744 | 0.29306 | 0.18333 | short circuit | 0.011183 | 0.819 | 10.9491 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44744 | 0.29653 | 44744 | 0.30139 | 0.11667 | short circuit | 0.0112 | 0.819 | 10.9654 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44744 | 0.45833 | 44744 | 0.475 | 0.4 | short circuit | 0.3188 | 0.819 | 312.1232 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44744 | 0.47708 | 44744 | 0.47917 | 0.05 | short circuit | 0.0458 | 0.819 | 44.8408 | Manually reset & turn on inverter
Hindupur | July | SCB.06.03 | String fault | 7.26 | 44744 | 0.26042 | 44744 | 0.47569 | 5.1667 | String fault | 1.7463 | 0.819 | 10.3836 | Inv-06 SCB-03 one string fault, replaced damaged Cable with new Cable.
Hindupur | July | SCB.06.03 | String fault | 7.26 | 44744 | 0.26042 | 44744 | 0.48889 | 5.4833 | String fault | 2.0234 | 0.819 | 12.0307 | Inv-06 SCB-03 one string fault, replaced damaged Cable with new Cable.
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44745 | 0.27847 | 44745 | 0.29097 | 0.3 | short circuit | 0.0189 | 0.82992 | 18.7508 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44745 | 0.30069 | 44745 | 0.32292 | 0.53333 | short circuit | 0.0752 | 0.82992 | 74.6065 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44745 | 0.63194 | 44745 | 0.63889 | 0.16667 | short circuit | 0.063333 | 0.82992 | 62.8335 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44745 | 0.67153 | 44745 | 0.67917 | 0.18333 | short circuit | 0.049133 | 0.82992 | 48.7456 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44746 | 0.28681 | 44746 | 0.29167 | 0.11667 | short circuit | 0.00525 | 0.85495 | 5.3657 | Manually reset & turn on inverter
Hindupur | July | Inverter 16 | Ground fault | 1205.16 | 44746 | 0.55 | 44746 | 0.55903 | 0.21667 | EXT DI4 fault | 0.070633 | 0.85495 | 72.7772 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44747 | 0.47083 | 44747 | 0.475 | 0.1 | EXT DI4 fault | 0.0312 | 0.8505 | 31.9798 | Manually reset & turn on inverter
Hindupur | July | Inverter 35 | Ground fault | 1136.03 | 44747 | 0.52986 | 44747 | 0.53125 | 0.033333 | EXT DI4 fault | 0.0215 | 0.8505 | 20.7732 | Manually reset & turn on inverter
Hindupur | July | Inverter 04 | Ground fault | 1205.16 | 44749 | 0.55764 | 44749 | 0.56528 | 0.18333 | EXT DI4 fault | 0.0748 | 0.84467 | 76.1437 | Manually reset & turn on inverter
Hindupur | July | Inverter 04 | Ground fault | 1205.16 | 44749 | 0.57153 | 44749 | 0.57986 | 0.2 | EXT DI4 fault | 0.0796 | 0.84467 | 81.0299 | Manually reset & turn on inverter
Hindupur | July | PT 01 | Breaker mechanism issue | 24103.2 | 44750 | 0.26597 | 44750 | 0.32639 | 1.45 | Breaker mechanism issue | 0.1102 | 0.86914 | 2308.5921 | Motor spring charge AC mcb Kept in off position .Manually charged breaker
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44750 | 0.26042 | 44750 | 0.34792 | 2.1 | EXT DI4 fault | 0.2205 | 0.86914 | 229.0992 | Manually reset & turn on inverter
Hindupur | July | Inverter 34 | Ground fault | 1195.43 | 44750 | 0.3125 | 44750 | 0.35208 | 0.95 | EXT DI4 fault | 0.17765 | 0.86914 | 184.5781 | Manually reset & turn on inverter
Hindupur | July | Inverter 26 | Ground fault | 1195.43 | 44750 | 0.41458 | 44750 | 0.42083 | 0.15 | EXT DI4 fault | 0.05865 | 0.86914 | 60.9373 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44750 | 0.55486 | 44750 | 0.57847 | 0.56667 | EXT DI4 fault | 0.14677 | 0.86914 | 153.7316 | Manually reset & turn on inverter
Hindupur | July | Inverter 35 | Ground fault | 1136.03 | 44750 | 0.64306 | 44750 | 0.64653 | 0.083333 | EXT DI4 fault | 0.01675 | 0.86914 | 16.5385 | Manually reset & turn on inverter
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44750 | 0.65694 | 44750 | 0.66875 | 0.28333 | EXT DI4 fault | 0.05865 | 0.86914 | 60.9373 | Manually reset & turn on inverter
Hindupur | July | Inverter 35 | Ground fault | 1136.03 | 44752 | 0.27639 | 44752 | 0.28472 | 0.2 | EXT DI4 fault | 0.0102 | 0.83872 | 9.7186 | Manually reset & turn on inverter
Hindupur | July | Inverter 40 | Ground fault | 1195.43 | 44752 | 0.65972 | 44752 | 0.66597 | 0.15 | EXT DI4 fault | 0.0138 | 0.83872 | 13.8362 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44753 | 0.28264 | 44753 | 0.29028 | 0.18333 | EXT DI4 fault | 0.0089833 | 0.85363 | 9.2417 | Manually reset & turn on inverter
Hindupur | July | Inverter 40 | Ground fault | 1195.43 | 44754 | 0.6125 | 44754 | 0.61944 | 0.16667 | EXT DI4 fault | 0.10517 | 0.84623 | 106.3872 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44754 | 0.62361 | 44754 | 0.62847 | 0.11667 | EXT DI4 fault | 0.060083 | 0.84623 | 61.2754 | Manually reset & turn on inverter
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44755 | 0.56667 | 44755 | 0.57708 | 0.25 | EXT DI4 fault | 0.091 | 0.86776 | 94.3988 | Manually reset & turn on inverter
Hindupur | July | Inverter 16 | Ground fault | 1205.16 | 44756 | 0.47222 | 44756 | 0.49236 | 0.48333 | EXT DI4 fault | 0.36008 | 0.81245 | 352.5711 | Manually reset & turn on inverter
Hindupur | July | Inverter 03 | Ground fault | 1205.16 | 44758 | 0.51319 | 44758 | 0.53264 | 0.46667 | EXT DI4 fault | 0.25293 | 0.81884 | 249.6045 | Inverter tripped on Earth fault.Found one string faulty. Isolated faulty strings & on inverter
Hindupur | July | SCB.03.03 | String fault | 7.26 | 44758 | 0.26042 | 44758 | 0.48264 | 5.3333 | String fault | 2.2507 | 0.81884 | 13.3798 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | July | SCB.03.03 | String fault | 7.26 | 44758 | 0.53333 | 44758 | 0.53819 | 0.11667 | String fault | 0.0476 | 0.81884 | 0.28297 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | July | Inverter 19 | Ground fault | 1219.68 | 44759 | 0.39861 | 44759 | 0.40347 | 0.11667 | EXT DI4 fault | 0.057983 | 0.82789 | 58.5492 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44760 | 0.26667 | 44760 | 0.29514 | 0.68333 | short circuit | 0.021867 | 0.87674 | 22.9181 | Manually reset & turn on inverter
Hindupur | July | Inverter 13 | Ground fault | 1205.16 | 44760 | 0.38333 | 44760 | 0.39375 | 0.25 | RESET fault | 0.031 | 0.87674 | 32.7551 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | RESET fault | 1205.16 | 44760 | 0.45278 | 44760 | 0.46042 | 0.18333 | RESET fault | 0.075167 | 0.87674 | 79.4223 | Manually reset & turn on inverter
Hindupur | July | Inverter 15 | RESET fault | 1205.16 | 44760 | 0.49931 | 44760 | 0.50486 | 0.13333 | RESET fault | 0.0552 | 0.87674 | 58.3252 | Manually reset & turn on inverter
Hindupur | July | Inverter 16 | Gnd leakage current fault | 1205.16 | 44760 | 0.56111 | 44760 | 0.56736 | 0.15 | EXT DI4 fault | 0.0423 | 0.87674 | 44.6948 | Manually reset & turn on inverter
Hindupur | July | Inverter 29 | Ground fault | 1195.43 | 44761 | 0.34722 | 44761 | 0.35069 | 0.083333 | EXT DI4 | 0.034766 | 0.79615 | 33.0877 | Manually reset & turn on inverter
Hindupur | July | Inverter 29 | Ground fault | 1195.43 | 44761 | 0.4875 | 44761 | 0.49028 | 0.066667 | EXT DI4 | 0.075244 | 0.79615 | 71.6125 | Manually reset & turn on inverter
Hindupur | July | Inverter 30 | Ground fault | 1202.85 | 44761 | 0.4875 | 44761 | 0.49236 | 0.11667 | EXT DI4 | 0.12983 | 0.79615 | 124.332 | Manually reset & turn on inverter
Hindupur | July | Inverter 31 | Ground fault | 1188 | 44761 | 0.4875 | 44761 | 0.49236 | 0.11667 | EXT DI4 | 0.12983 | 0.79615 | 122.797 | Manually reset & turn on inverter
Hindupur | July | Inverter 32 | Recharge Alarm | 1195.43 | 44761 | 0.31875 | 44761 | 0.33264 | 0.33333 | Recharge Alarm | 0.10161 | 0.79615 | 96.7032 | Manually reset & turn on inverter
Hindupur | July | Inverter 32 | Ground fault | 1195.43 | 44761 | 0.4875 | 44761 | 0.49028 | 0.066667 | EXT DI4 | 0.075244 | 0.79615 | 71.6125 | Manually reset & turn on inverter
Hindupur | July | Inverter 35 | Ground fault | 1136.03 | 44761 | 0.6125 | 44761 | 0.61875 | 0.15 | EXT DI4 | 0.10781 | 0.79615 | 97.5084 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44761 | 0.63194 | 44761 | 0.68056 | 1.1667 | Short circuit fault | 0.59456 | 0.79615 | 565.8659 | Due to SCADA Communication error delayed in fault identification. Inverter restored after resetted Manually .
Hindupur | July | Inverter 32 | Ground fault | 1195.43 | 44762 | 0.31042 | 44762 | 0.32292 | 0.3 | EXT DI4 | 0.0843 | 0.8104 | 81.6677 | Manually reset & turn on inverter
Hindupur | July | Inverter 15 | Ground fault | 1205.16 | 44762 | 0.32917 | 44762 | 0.34028 | 0.26667 | EXT DI4 | 0.097067 | 0.8104 | 94.8011 | Manually reset & turn on inverter
Hindupur | July | Inverter 03 | Ground fault | 1205.16 | 44762 | 0.40069 | 44762 | 0.40278 | 0.05 | EXT DI4 | 0.02845 | 0.8104 | 27.786 | Manually reset & turn on inverter
Hindupur | July | Inverter 32 | Ground fault | 1195.43 | 44763 | 0.4625 | 44763 | 0.46458 | 0.05 | EXT DI4 | 0.01815 | 0.79423 | 17.2325 | Manually reset & turn on inverter
Hindupur | July | Inverter 01 | Ground fault | 1205.16 | 44763 | 0.49167 | 44763 | 0.49306 | 0.033333 | EXT DI4 | 0.023467 | 0.79423 | 22.4617 | Manually reset & turn on inverter
Hindupur | July | Inverter 08 | Ground fault | 1205.16 | 44763 | 0.50347 | 44763 | 0.50486 | 0.033333 | EXT DI4 | 0.021033 | 0.79423 | 20.1326 | Manually reset & turn on inverter
Hindupur | July | Inverter 10 | Ground fault | 1205.16 | 44764 | 0.38194 | 44764 | 0.38889 | 0.16667 | EXT DI4 | 0.035333 | 0.85373 | 36.3538 | Manually reset & turn on inverter
Hindupur | July | Inverter 32 | Ground fault | 1195.43 | 44765 | 0.27847 | 44765 | 0.28125 | 0.066667 | EXT DI4 | 0.003 | 0.83485 | 2.994 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44766 | 0.26319 | 44766 | 0.28889 | 0.61667 | Short circuit fault | 0.019733 | 0.82226 | 19.397 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Ground fault | 1195.43 | 44766 | 0.57014 | 44766 | 0.57361 | 0.083333 | EXT DI4 | 0.061667 | 0.82226 | 60.6155 | Manually reset & turn on inverter
Hindupur | July | Inverter 11 | Ground fault | 1205.16 | 44766 | 0.68958 | 44766 | 0.70417 | 0.35 | EXT DI4 | 0.02625 | 0.82226 | 26.0125 | Manually reset & turn on inverter
Hindupur | July | Inverter 03 | Ground fault | 1205.16 | 44766 | 0.69236 | 44766 | 0.7 | 0.18333 | EXT DI4 | 0.017233 | 0.82226 | 17.0774 | Manually reset & turn on inverter
Hindupur | July | Inverter 01 | Ground fault | 1205.16 | 44766 | 0.71042 | 44766 | 0.71458 | 0.1 | EXT DI4 | 0.0187 | 0.82226 | 18.5308 | Manually reset & turn on inverter
Hindupur | July | Inverter 38 | Ground fault | 1195.43 | 44766 | 0.72708 | 44766 | 0.72986 | 0.066667 | EXT DI4 | 0.0082 | 0.82226 | 8.0602 | Manually reset & turn on inverter
Hindupur | July | Inverter 40 | Ground fault | 1195.43 | 44767 | 0.275 | 44767 | 0.27847 | 0.083333 | EXT DI4 | 0.0033333 | 0.80257 | 3.198 | Manually reset & turn on inverter
Hindupur | July | Inverter 25 | Ground fault | 1195.43 | 44767 | 0.40486 | 44767 | 0.4125 | 0.18333 | EXT DI4 | 0.12063 | 0.80257 | 115.7369 | Manually reset & turn on inverter
Hindupur | July | Inverter 31 | Ground fault | 1188 | 44767 | 0.51597 | 44767 | 0.51667 | 0.016667 | EXT DI4 | 0.016517 | 0.80257 | 15.7478 | Manually reset & turn on inverter
Hindupur | July | Inverter 01 | Ground fault | 1205.16 | 44770 | 0.26319 | 44770 | 0.26944 | 0.15 | EXT DI4 | 0.004594 | 0.79319 | 4.3915 | Manually reset & turn on inverter
Hindupur | July | Inverter 01 | A411 card issue | 1205.16 | 44770 | 0.34583 | 44770 | 0.36875 | 0.55 | A411 card issue | 0.15326 | 0.79319 | 146.5 | A411 card removed & reconnected.
Hindupur | July | Inverter 03 | Ground fault | 1205.16 | 44771 | 0.47431 | 44771 | 0.47639 | 0.05 | EXT DI4 | 0.02969 | 0.78241 | 27.9955 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44771 | 0.29167 | 44771 | 0.29444 | 0.066667 | Short ckt fault | 0.0084048 | 0.78241 | 7.8611 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Short circuit fault | 1195.43 | 44771 | 0.72569 | 44771 | 0.72986 | 0.1 | Short ckt fault | 0.01858 | 0.78241 | 17.3785 | Manually reset & turn on inverter
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44771 | 0.29444 | 44771 | 0.30347 | 0.21667 | EXT DI4 | 0.014036 | 0.78241 | 13.128 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Ground fault | 1195.43 | 44772 | 0.29167 | 44772 | 0.29653 | 0.11667 | EXT DI4 | 0.0055282 | 0.77149 | 5.0984 | Manually reset & turn on inverter
Hindupur | July | Inverter 28 | Ground fault | 1195.43 | 44772 | 0.26458 | 44772 | 0.27361 | 0.21667 | EXT DI4 | 0.0066981 | 0.77149 | 6.1774 | Manually reset & turn on inverter
Hindupur | July | Inverter 40 | Ground fault | 1195.43 | 44772 | 0.4 | 44772 | 0.40347 | 0.083333 | EXT DI4 | 0.058858 | 0.77149 | 54.283 | Manually reset & turn on inverter
Hindupur | July | Inverter 29 | Ground fault | 1195.43 | 44773 | 0.33403 | 44773 | 0.33819 | 0.1 | EXT DI4 | 0.025475 | 0.80885 | 24.6322 | Manually reset & turn on inverter
Hindupur | July | Inverter 38 | Ground fault | 1195.43 | 44773 | 0.28264 | 44773 | 0.28542 | 0.066667 | EXT DI4 | 0.0046033 | 0.80885 | 4.4511 | Manually reset & turn on inverter
Hindupur | July | Inverter 27 | Ground fault | 1195.43 | 44773 | 0.52847 | 44773 | 0.53333 | 0.11667 | EXT DI4 | 0.074523 | 0.80885 | 72.058 | Manually reset & turn on inverter
Hindupur | July | Inverter 40 | Ground fault | 1195.43 | 44773 | 0.4125 | 44773 | 0.41528 | 0.066667 | EXT DI4 | 0.019207 | 0.80885 | 18.5718 | Manually reset & turn on inverter
Hindupur | July | Inverter 30 | Ground fault | 1202.85 | 44773 | 0.50556 | 44773 | 0.50694 | 0.033333 | EXT DI4 | 0.015595 | 0.80885 | 15.1729 | Manually reset & turn on inverter
Hindupur | July | Inverter 30 | Ground fault | 1202.85 | 44773 | 0.59028 | 44773 | 0.59444 | 0.1 | EXT DI4 | 0.069921 | 0.80885 | 68.0272 | Manually reset & turn on inverter
Hindupur | July | Inverter 04 | Ground fault | 1205.16 | 44773 | 0.32014 | 44773 | 0.325 | 0.11667 | EXT DI4 | 0.030871 | 0.80885 | 30.0923 | Manually reset & turn on inverter
Hindupur | July | Inverter 39 | Ground fault | 1195.43 | 44773 | 0.25833 | 44773 | 0.29931 | 0.98333 | EXT DI4 | 0.059718 | 0.80885 | 57.7422 | Manually reset & turn on inverter
Hindupur | August | Inverter 20 | Ground fault | 1205.16 | 44774 | 0.30556 | 44774 | 0.31111 | 0.13333 | EXT DI4 | 0.01653 | 0.79634 | 15.8641 | Manually reset & turn on inverter
Hindupur | August | Inverter 25 | Ground fault | 1195.43 | 44774 | 0.31458 | 44774 | 0.31597 | 0.033333 | EXT DI4 | 0.0062829 | 0.79634 | 5.9811 | Manually reset & turn on inverter
Hindupur | August | Inverter 32 | Ground fault | 1195.43 | 44774 | 0.31875 | 44774 | 0.32361 | 0.11667 | EXT DI4 | 0.028353 | 0.79634 | 26.9914 | Manually reset & turn on inverter
Hindupur | August | Inverter 37 | Ground fault | 1195.43 | 44774 | 0.32014 | 44774 | 0.32361 | 0.083333 | EXT DI4 | 0.018482 | 0.79634 | 17.5947 | Manually reset & turn on inverter
Hindupur | August | Inverter 37 | Ground fault | 1195.43 | 44774 | 0.33403 | 44774 | 0.33681 | 0.066667 | EXT DI4 | 0.029534 | 0.79634 | 28.1155 | Manually reset & turn on inverter
Hindupur | August | Inverter 09 | Ground fault | 1205.16 | 44774 | 0.45417 | 44774 | 0.45764 | 0.083333 | EXT DI4 | 0.06293 | 0.79634 | 60.3953 | Manually reset & turn on inverter
Hindupur | August | Inverter 36 | Ground fault | 1225.13 | 44774 | 0.48889 | 44774 | 0.50278 | 0.33333 | EXT DI4 | 0.21473 | 0.79634 | 209.4915 | Manually reset & turn on inverter
Hindupur | August | Inverter 27 | Ground fault | 1195.43 | 44774 | 0.59931 | 44774 | 0.60347 | 0.1 | EXT DI4 | 0.040533 | 0.79634 | 38.5863 | Manually reset & turn on inverter
Hindupur | August | Inverter 27 | Ground fault | 1195.43 | 44774 | 0.61736 | 44774 | 0.62639 | 0.21667 | EXT DI4 | 0.16674 | 0.79634 | 158.7274 | Manually reset & turn on inverter
Hindupur | August | Inverter 27 | Ground fault | 1195.43 | 44775 | 0.75556 | 44775 | 0.76597 | 0.25 | EXT DI4 | 0.011509 | 0.80816 | 11.1186 | Manually reset & turn on inverter
Hindupur | August | Inverter 01 | Ground fault | 1205.16 | 44776 | 0.29653 | 44776 | 0.30694 | 0.25 | EXT DI4 | 0.0085117 | 0.82252 | 8.4373 | Manually reset & turn on inverter
Hindupur | August | Inverter 34 | Ground fault | 1195.43 | 44776 | 0.32222 | 44776 | 0.33681 | 0.35 | EXT DI4 | 0.020844 | 0.82252 | 20.4953 | Manually reset & turn on inverter
Hindupur | August | Inverter 04 | Ground fault | 1205.16 | 44776 | 0.72222 | 44776 | 0.72986 | 0.18333 | EXT DI4 | 0.026224 | 0.82252 | 25.9947 | Manually reset & turn on inverter
Hindupur | August | Inverter 06 | Ground fault | 1205.16 | 44776 | 0.27986 | 44776 | 0.29653 | 0.4 | EXT DI4 | 0.0066717 | 0.82252 | 6.6134 | Manually reset & turn on inverter
Hindupur | August | Inverter 38 | Ground fault | 1195.43 | 44776 | 0.35069 | 44776 | 0.35278 | 0.05 | EXT DI4 | 0.003021 | 0.82252 | 2.9704 | Manually reset & turn on inverter
Hindupur | August | Inverter 28 | Ground fault | 1195.43 | 44776 | 0.34583 | 44776 | 0.34722 | 0.033333 | EXT DI4 | 0.0017466 | 0.82252 | 1.7174 | Manually reset & turn on inverter
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44777 | 0.39583 | 44777 | 0.77431 | 9.0833 | Cable Damege | 3.3336 | 0.84272 | 407.908 | Need to Replace the new cable work going on.
Hindupur | August | Inverter 37 | Short circuit fault | 1195.43 | 44777 | 0.6625 | 44777 | 0.67431 | 0.28333 | Short circuit fault | 0.0816 | 0.84272 | 82.2051 | Manually reset & turn on inverter
Hindupur | August | SCB.17.03 | String fault | 7.26 | 44778 | 0.26389 | 44778 | 0.47569 | 5.0833 | String fault | 1.3623 | 0.85166 | 8.4234 | Inv-17 SCB-3 one string fault, Replaced with new Fuse.now ok
Hindupur | August | SCB.17.08 | String fault | 7.26 | 44778 | 0.26389 | 44778 | 0.49097 | 5.45 | String fault | 1.5533 | 0.85166 | 9.6039 | Inv-17 SCB-8 one string fault, Replaced with new Fuse.now ok
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44778 | 0.26181 | 44778 | 0.76875 | 12.1667 | Cable Damege | 3.7108 | 0.85166 | 458.8869 | Need to Replace the new cable work going on.
Hindupur | August | Inverter 32 | Ground fault | 1195.43 | 44779 | 0.44236 | 44779 | 0.45 | 0.18333 | EXT DI4 | 0.14832 | 0.82249 | 145.83 | Manually reset & turn on inverter
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44779 | 0.2625 | 44779 | 0.75556 | 11.8333 | Cable Damege | 4.0825 | 0.82249 | 487.557 | Need to Replace the new cable work going on.
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44780 | 0.26389 | 44780 | 0.77431 | 12.25 | Cable Damege | 3.5525 | 0.85343 | 440.2174 | Need to Replace the new cable work going on.
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44781 | 0.26528 | 44781 | 0.75903 | 11.85 | Cable Damege | 3.1877 | 0.84288 | 390.1245 | Need to Replace the new cable work going on.
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44782 | 0.26806 | 44782 | 0.77569 | 12.1833 | Cable Damege | 4.7271 | 0.79592 | 546.3005 | Need to Replace the new cable work going on.
Hindupur | August | PT 02 | Over current fault | 23874 | 44783 | 0.31597 | 44783 | 0.35764 | 1 | Over current | 0.37 | 0.79601 | 7031.4679 | Fault reset & charged Power transformer -2
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44783 | 0.26319 | 44783 | 0.77292 | 12.2333 | Cable Damege | 4.3184 | 0.79601 | 499.1203 | Need to Replace the new cable work going on.
Hindupur | August | PT 02 | Over current fault | 23874 | 44784 | 0.32222 | 44784 | 0.34722 | 0.6 | Over current | 0.14819 | 0.8256 | 2920.9592 | Fault reset & charged Power transformer -2
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44784 | 0.26458 | 44784 | 0.475 | 5.05 | positive Cable Damage | 2.1816 | 0.8256 | 261.5239 | Need to Replace the new cable work going on.
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44784 | 0.67431 | 44784 | 0.77431 | 2.4 | positive Cable Damage | 0.4128 | 0.8256 | 49.4853 | Need to Replace the new cable work going on.
Hindupur | August | PT 02 | Over current fault | 23874 | 44785 | 0.33542 | 44785 | 0.34444 | 0.21667 | Over current | 0.063483 | 0.79807 | 1209.5621 | Fault reset & charged Power transformer -2
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44785 | 0.26181 | 44785 | 0.77639 | 12.35 | positive Cable Damage | 4.9153 | 0.79807 | 569.5868 | Need to Replace the new cable work going on.
Hindupur | August | Block-9 IDT-1 | Over current fault | 2390.86 | 44786 | 0.26181 | 44786 | 0.44514 | 4.4 | R,Y Phase HV Bussing Flashover | 1.76 | 0.7708 | 3243.457 | Testing and trouble shooting was going on & parallely replacement of bushings along with oil filteration under progress
Hindupur | August | SCB.17.02 | String fault | 145.2 | 44786 | 0.26181 | 44786 | 0.375 | 2.7167 | positive Cable Damage | 0.55148 | 0.7708 | 61.722 | new scb cable replacemt done
Hindupur | August | Inverter 09 | Ground fault | 1205.16 | 44786 | 0.52222 | 44786 | 0.525 | 0.066667 | EXT DI4 | 0.031133 | 0.7708 | 28.9209 | Manually reset & turn on inverter
Hindupur | August | Block-9 IDT-1 | Over current fault | 2390.86 | 44786 | 0.52153 | 44786 | 0.76875 | 5.9333 | R,Y Phase HV Bussing Flashover | 2.0114 | 0.7708 | 3706.7553 | Testing and trouble shooting was going on & parallely replacement of bushings along with oil filteration under progress
Hindupur | August | Block-9 IDT-1 | Over current fault | 2390.86 | 44787 | 0.26389 | 44787 | 0.38194 | 2.8333 | R,Y Phase HV Bussing Flashover | 0.527 | 0.76844 | 968.2221 | Replaced the HV bushings along with oil filteration and after all necessary tests completed, charged the IDT
Hindupur | August | Block-9 IDT-1 | WTI-2 Alaram | 2390.86 | 44787 | 0.42153 | 44787 | 0.6625 | 5.7833 | WTI-2 Alaram | 2.8917 | 0.76844 | 5312.6673 | After IR, Ratio & Magnetic balance tests complted, charged the IDT
Hindupur | August | PT 02 | Over current fault | 23874 | 44787 | 0.48333 | 44787 | 0.48611 | 0.066667 | Over current | 0.044667 | 0.76844 | 819.4434 | Isolated the fault occurred block-6 feeder and charged the PTR
Hindupur | August | Block-6 IDT-2 | Over current fault | 2395.8 | 44787 | 0.48681 | 44787 | 0.49375 | 0.16667 | Over current | 0.12417 | 0.76844 | 228.5945 | Isolated the fault occurred IDT-1 feeder and charged the IDT-2
Hindupur | August | Block-6 IDT-1 | Over current fault | 2381.28 | 44787 | 0.48681 | 44787 | 0.76806 | 6.75 | R,Y Phase HV Bussing Flashover | 2.4165 | 0.76844 | 4421.8857 | Testing and trouble shooting was going on & parallely replacement of bushings along with oil filteration under progress
Hindupur | August | Block-6 IDT-1 | Over current fault | 2381.28 | 44788 | 0.26528 | 44788 | 0.57917 | 7.5333 | R,Y Phase HV Bussing Flashover | 3.5105 | 0.78337 | 6548.6569 | Testing and trouble shooting was going on & parallely replacement of bushings along with oil filteration under progress
Hindupur | August | Block-6 IDT-1 | Over current fault | 2381.28 | 44788 | 0.63611 | 44788 | 0.76944 | 3.2 | R,Y Phase HV Bussing Flashover | 0.672 | 0.78337 | 1253.5695 | Testing and trouble shooting was going on & parallely replacement of bushings along with oil filteration under progress
Hindupur | August | PT 01 | Over current fault | 23826.023 | 44793 | 0.40208 | 44793 | 0.41389 | 0.28333 | Over Current | 0.16348 | 0.76857 | 2993.7066 | PTR-1 LV side breaker trpped along with Block-5 feeder, isolated the Block-5 feeder and charged the PTR
Hindupur | August | Block-5 IDT-1 | Over current fault | 2395.8 | 44793 | 0.41458 | 44793 | 0.45 | 0.85 | Over Current | 0.4556 | 0.76857 | 838.916 | Afeter Inspection found IDT2 has issue, so isolated the IDT-2 and charged IDT-1
Hindupur | August | Block-5 IDT-2 | Over current fault | 2424.84 | 44793 | 0.41458 | 44793 | 0.63889 | 5.3833 | Over Current | 3.483 | 0.76857 | 6491.1677 | After IR, Ratio & Magnetic balance tests complted, charged the IDT
Hindupur | August | Inverter 04 | ISU fault | 1205.16 | 44794 | 0.26736 | 44794 | 0.28889 | 0.51667 | ISU fault | 0.021183 | 0.80511 | 20.5538 | Manually reset & turn on inverter
Hindupur | August | Inverter 30 | ISU fault | 1202.85 | 44795 | 0.25972 | 44795 | 0.30694 | 1.1333 | ISU fault | 0.062333 | 0.8056 | 60.4021 | Inverter filters fan removed and blowering done then reset and turn on inverter
Hindupur | August | Inverter 32 | ISU fault | 1195.43 | 44795 | 0.28403 | 44795 | 0.29028 | 0.15 | ISU fault | 0.0135 | 0.8056 | 13.001 | Manually reset & turn on inverter
Hindupur | August | Inverter 30 | Recharge Alarm | 1202.85 | 44796 | 0.29653 | 44796 | 0.3125 | 0.38333 | Recharge Alarm | 0.060567 | 0.78074 | 56.879 | Manually reset & turn on inverter
Hindupur | August | SCB.13.02 | String fault | 7.26 | 44798 | 0.26528 | 44798 | 0.61458 | 8.3833 | String fault | 3.7976 | 0.80338 | 22.15 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | August | SCB.13.08 | String fault | 7.26 | 44798 | 0.26528 | 44798 | 0.62361 | 8.6 | String fault | 3.9302 | 0.80338 | 22.9231 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | August | SCB.18.06 | String fault | 7.26 | 44798 | 0.26528 | 44798 | 0.63472 | 8.8667 | String fault | 3.9811 | 0.80338 | 23.2202 | Replaced with new fuse
Hindupur | August | SCB.19.02 | String fault | 7.26 | 44798 | 0.26528 | 44798 | 0.64514 | 9.1167 | String fault | 4.0296 | 0.80338 | 23.5027 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | August | SCB.26.06 | String fault | 7.26 | 44800 | 0.2625 | 44800 | 0.61806 | 8.5333 | String fault | 3.9595 | 0.81599 | 23.4563 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | August | SCB.25.03 | String fault | 7.26 | 44800 | 0.2625 | 44800 | 0.64722 | 9.2333 | String fault | 4.3489 | 0.81599 | 25.7634 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | August | Inverter 31 | Ground fault | 1188 | 44801 | 0.275 | 44801 | 0.28125 | 0.15 | EXT DI4 | 0.00435 | 0.8218 | 4.2469 | Manually reset & turn on inverter
Hindupur | September | Inverter 34 | Short circuit fault | 1195.43 | 44805 | 0.26944 | 44805 | 0.275 | 0.13333 | Short circuit fault | 0.0058667 | 0.78109 | 5.4779 | Manually reset & turn on inverter
Hindupur | September | Inverter 30 | Short circuit fault | 1202.85 | 44807 | 0.48264 | 44807 | 0.48403 | 0.033333 | Short circuit fault | 0.028567 | 0.76639 | 26.3343 | Manually reset & turn on inverter
Hindupur | September | Inverter 30 | Short circuit fault | 1202.85 | 44807 | 0.52847 | 44807 | 0.53194 | 0.083333 | Short circuit fault | 0.048167 | 0.76639 | 44.4027 | Manually reset & turn on inverter
Hindupur | September | SCB.30.05 | String fault | 7.26 | 44808 | 0.26319 | 44808 | 0.48958 | 5.4333 | String fault | 2.3037 | 0.8072 | 13.5006 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | September | SCB.31.07 | String fault | 7.26 | 44808 | 0.26319 | 44808 | 0.49792 | 5.6333 | String fault | 2.5068 | 0.8072 | 14.6908 | Replaced with new MC4 Connector & reconnected back .now ok
Hindupur | September | SCB.32.08 | String fault | 7.26 | 44808 | 0.26319 | 44808 | 0.51597 | 6.0667 | String fault | 2.7543 | 0.8072 | 16.1409 | Replaced with new fuse
Hindupur | September | SCB.17.7 | String fault | 7.26 | 44809 | 0.28056 | 44809 | 0.62361 | 8.2333 | String fault | 5.4175 | 0.809 | 31.8192 | Replaced with new Cable reconnected back. now ok
Karoor | April | All Inverters | Feeder tripped | 18043 | 44667 | 0.62222 | 44667 | 0.63056 | 0.2 | Supply failed from GSS end | 0.039002 | 0.80021 | 563.1158 | Supply resumed at 15:08
Karoor | April | All Inverters | Feeder tripped | 18043 | 44668 | 0.67361 | 44668 | 0.77153 | 2.35 | B-Phase Line differential due to tree branches touchng between Tower 1 &2 | 0.40404 | 0.77188 | 5627.0796 | Tree removed from location and charged the line
Karoor | April | Inverter 05 | Ground fault | 1205.82 | 44670 | 0.72917 | 44670 | 0.75903 | 0.71667 | EXT DI4 | 0.031209 | 0.81204 | 30.5587 | Autorestarted after rain stopped
Karoor | April | Inverter 11 | Ground fault | 1206.15 | 44670 | 0.72917 | 44670 | 0.75903 | 0.71667 | EXT DI4 | 0.031209 | 0.81204 | 30.567 | Autorestarted after rain stopped
Karoor | April | Inverter 13 | Ground fault | 1206.15 | 44670 | 0.72917 | 44670 | 0.75903 | 0.71667 | EXT DI4 | 0.031209 | 0.81204 | 30.567 | Autorestarted after rain stopped
Karoor | April | Inverter 05 | Ground fault | 1205.82 | 44671 | 0.25625 | 44671 | 0.25833 | 0.05 | EXT DI4 | 0.000836 | 0.77756 | 0.78384 | back charge done
Karoor | April | Inverter 05 | Ground fault | 1205.82 | 44671 | 0.26181 | 44671 | 0.27153 | 0.23333 | EXT DI4 | 0.0077847 | 0.77756 | 7.2989 | SCBs fault identification
Karoor | April | Inverter 05 | Ground fault | 1205.82 | 44671 | 0.27569 | 44671 | 0.29861 | 0.55 | EXT DI4 | 0.062037 | 0.77756 | 58.1663 | SCBs fault identification
Karoor | April | Inverter 05 | Ground fault | 1205.82 | 44671 | 0.30694 | 44671 | 0.31736 | 0.25 | EXT DI4 | 0.054914 | 0.77756 | 51.4878 | ground fault cleared
Karoor | April | Inverter 07 | Short circuit fault | 1205.82 | 44671 | 0.34236 | 44671 | 0.47708 | 3.2333 | SHORT CIRC | 2.2342 | 0.77756 | 2094.7943 | SHORT CIRC
Karoor | April | Inverter 07 | Short circuit fault | 1205.82 | 44671 | 0.48056 | 44671 | 0.48264 | 0.05 | SHORT CIRC | 0.061669 | 0.77756 | 57.8208 | SHORT CIRC
Karoor | April | Inverter 07 | Short circuit fault | 1205.82 | 44671 | 0.67569 | 44671 | 0.69583 | 0.48333 | SHORT CIRC | 0.17173 | 0.77756 | 161.0099 | SHORT CIRC
Karoor | April | Inverter 07 | IGBT failure | 1205.82 | 44671 | 0.48333 | 44671 | 0.675 | 4.6 | Clipping loss (Inverter runs on 65% load) | 0.17173 | 0.77756 | 950 | New IGBT installed at Cubicle-3 on B phase
Karoor | April | All Inverters | Grid failure | 18043 | 44677 | 0.50972 | 44677 | 0.51667 | 0.16667 | Incoming to GSS Bothpur and shadnagar feeder trip | 0.11872 | 0.80983 | 1734.6298 | Grid supply resumed at 12:24
Karoor | May | All Inverters | Feeder tripped | 18043 | 44692 | 0.49236 | 44692 | 0.49931 | 0.16667 | Transmission line tripped due to bird hit pole no 45 | 0.074 | 0.86607 | 1156.3625 | Rest master trip Transmission line tail run charge after then plant charge at 11:59
Karoor | May | Inverter 11 | Ground fault | 1206.15 | 44692 | 0.36042 | 44692 | 0.38056 | 0.48333 | EXT DI4 | 0.0451 | 0.86607 | 47.112 | ground fault cleared
Karoor | May | Inverter 11 | Ground fault | 1206.15 | 44692 | 0.44444 | 44692 | 0.47917 | 0.83333 | EXT DI4 | 0.14 | 0.86607 | 146.2456 | ground fault cleared
Karoor | May | Inverter 05 | Ground fault | 1205.82 | 44700 | 0.60208 | 44700 | 0.61528 | 0.31667 | EXT DI4 | 0.044467 | 0.85736 | 45.9709 | ground fault cleared
Karoor | May | Inverter 05 | Ground fault | 1205.82 | 44700 | 0.69583 | 44700 | 0.70069 | 0.11667 | EXT DI4 | 0.0057208 | 0.85736 | 5.9144 | ground fault cleared
Karoor | June | Inverter 11 | Ground fault | 1206.15 | 44727 | 0.38403 | 44727 | 0.39931 | 0.36667 | Inverter tripped due to ground fault | 0.151 | 0.86774 | 158.0403 | ground fault cleared
Karoor | June | Inverter 05 | Ground fault | 1205.82 | 44727 | 0.3125 | 44727 | 0.33681 | 0.58333 | Inverter tripped due to ground fault | 0.009 | 0.86774 | 9.417 | ground fault cleared
Karoor | July | All Inverters | Grid failure | 18043 | 44755 | 0.57083 | 44755 | 0.58264 | 0.28333 | Incoming to GSS Bothpur and shadnagar feeder trip | 0.065555 | 0.8236 | 974.1614 | Grid supply resumed at 14:00
Karoor | July | Inverter 09 | Ground fault | 1205.82 | 44760 | 0.55278 | 44760 | 0.55556 | 0.066667 | EXT DI4 | 0.032784 | 0.8236 | 32.5586 | Reset the fault and start the inverter
Karoor | July | SCB.01.14 | String fault | 6.93 | 44760 | 0.25833 | 44760 | 0.53819 | 6.7167 | Negative string cable failure due to ground fault | 1.6814 | 0.8236 | 9.5966 | string cable lying and now ground fault cleared
Karoor | July | Inverter 09 | Ground fault | 1205.82 | 44760 | 0.56875 | 44760 | 0.57014 | 0.033333 | EXT DI4 | 0.016601 | 0.8236 | 16.4865 | Reset the fault and start the inverter
Karoor | July | SCB.08.05 | String fault | 6.251 | 44761 | 0.25486 | 44761 | 0.71042 | 10.9333 | Positive string cable failure due to ground fault | 6.251 | 0.8203 | 32.0532 | string cable laid and ground fault restored
Karoor | July | All Inverters | Feeder tripped | 18043 | 44764 | 0.54792 | 44764 | 0.55347 | 0.13333 | 33kv Transmission line tripped due to master trip realy Oparated | 0.0384 | 0.8236 | 570.6322 | Reset the fault and trail charge taken line has with stand
Karoor | July | Inverter 10 | IO fault | 1205.82 | 44767 | 0.46597 | 44767 | 0.46875 | 0.066667 | FO Cable Communication | 0.043 | 0.8534 | 44.2492 | Reset the fault and start the inverter
Karoor | July | Inverter 10 | IO fault | 1205.82 | 44767 | 0.47153 | 44767 | 0.47708 | 0.13333 | FO Cable Communication | 0.055 | 0.8534 | 56.5978 | Reset the fault and start the inverter
Karoor | August | Inverter 10 | Ground fault | 1205.82 | 44776 | 0.5 | 44776 | 0.50625 | 0.15 | EXT DI4 | 0.16258 | 0.83563 | 163.8203 | Reset the fault and back charge done-start the inverter
Karoor | August | All Inverters | Feeder tripped | 18043 | 44796 | 0.30972 | 44796 | 0.31597 | 0.15 | 33KV Line tripped on Master trip relay operated | 0.0334 | 0.81078 | 488.6035 | Trail Charge taken Line has withstand
Karoor | August | Inverter 13 | IO fault | 1206.15 | 44797 | 0.49306 | 44797 | 0.49375 | 0.016667 | Inverter tripped on IO Fault | 0.02 | 0.85157 | 20.5424 | Inverter Auto Started
Karoor | August | Inverter 13 | IO fault | 1206.15 | 44797 | 0.51181 | 44797 | 0.5125 | 0.016667 | Inverter tripped on IO Fault | 0.029 | 0.85157 | 29.7865 | Inverter Auto Started
Karoor | August | Inverter 13 | IO fault | 1206.15 | 44798 | 0.47639 | 44798 | 0.47708 | 0.016667 | Inverter tripped on IO Fault | 0.028 | 0.82156 | 27.746 | Inverter Auto Started
Karoor | August | Inverter 13 | IO fault | 1206.15 | 44798 | 0.50069 | 44798 | 0.50208 | 0.033333 | Inverter tripped on IO Fault | 0.022 | 0.82156 | 21.8004 | Inverter Auto Started
Karoor | August | Inverter 13 | IO fault | 1206.15 | 44798 | 0.56667 | 44798 | 0.56806 | 0.033333 | Inverter tripped on IO Fault | 0.04 | 0.82156 | 39.6372 | Inverter Auto Started
Karoor | September | All Inverters | Feeder tripped | 18043 | 44810 | 0.56667 | 44810 | 0.625 | 1.4 | 33kv 4 -Pole DP Yard B- phase jumper Failure | 1.0913 | 0.8287 | 16317.3731 | Replaced jumper connector and restord Plant
Karoor | September | Inverter 03 | IO fault | 1204.17 | 44815 | 0.33542 | 44815 | 0.34444 | 0.21667 | Battery failure alarm | 0.009 | 0.8287 | 8.9811 | Checked OFC cables and restarted the inverter
Kodangal | April | Inverter 08 | Unknown fault | 1206 | 44652 | 0.47917 | 44652 | 0.55556 | 1.8333 | Fault is not identified due to display is not working | 1.348 | 0.7646 | 1243.001 | Reset the fault and update the software for display
Kodangal | April | Inverter 03 | SMPS failure | 1193.4 | 44664 | 0.61806 | 44664 | 0.65833 | 0.96667 | SMPS G10 Card failure | 0.28 | 0.7945 | 265.4838 | asper service engineer instructions supply taken from inverter-2 and connected to Inverter -3.
Kodangal | April | All Inverters | Feeder tripped | 12008.7 | 44667 | 0.35972 | 44667 | 0.47708 | 2.8167 | pole no-77 Y-phase pin insulator is damaged | 1.855 | 0.7721 | 17199.4065 | New Pin insulator is replaced .Charged the line and kept under observation
Kodangal | April | Inverter 03 | Unbalance voltage | 1193.4 | 44667 | 0.48611 | 44667 | 0.57292 | 2.0833 | SMPS G10 unbalce voltage | 1.27 | 0.7721 | 1170.2087 | Service peson instructions follow to SMPS G10 votage increased after Inverter -3 charged . Inverter is normal condition kept under observation.
Kodangal | April | Inv-1,2,3,4 | Block 01 tripped | 4786.2 | 44681 | 0.58611 | 44681 | 0.60347 | 0.41667 | BLOCK-1 Tripped Due to Earth Leakage Relay Operated | 0.13415 | 0.768 | 493.1155 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | May | All Inverters | Feeder tripped | 12008.7 | 44683 | 0.52569 | 44683 | 0.53194 | 0.15 | Breaker tripped on EL R phase from gss end | 0.14346 | 0.7617 | 1312.2142 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | May | Inverter-5 | Ground fault | 1206 | 44686 | 0.28542 | 44686 | 0.29861 | 0.31667 | Ground leakage current | 0.01822 | 0.7767 | 17.0668 | reset the fault and charged the inverter
Kodangal | May | Inverter-6 | Ground fault | 1206 | 44686 | 0.28542 | 44686 | 0.30278 | 0.41667 | Ground leakage current | 0.023154 | 0.7767 | 21.688 | reset the fault and charged the inverter
Kodangal | May | Inverter-7 | Ground fault | 1206 | 44686 | 0.28542 | 44686 | 0.29792 | 0.3 | Ground leakage current | 0.018623 | 0.7767 | 17.4437 | reset the fault and charged the inverter
Kodangal | May | Inverter-3 | Ground fault | 1193.4 | 44686 | 0.2875 | 44686 | 0.28889 | 0.033333 | Ground leakage current | 0.0017832 | 0.7767 | 1.6529 | Inverter auto reset and charged
Kodangal | May | Inverter-5 | Ground fault | 1206 | 44688 | 0.32639 | 44688 | 0.35069 | 0.58333 | Ground leakage current | 0.17715 | 0.7731 | 165.171 | reset the fault and charged the inverter
Kodangal | May | INV-9,SCB-7,STR-3 | String fault | 9 | 44690 | 0.25486 | 44690 | 0.47222 | 5.2167 | +ve Cable failure | 2.33 | 0.7729 | 16.2077 | New string cable replaced
Kodangal | May | Inv-3 | Ground fault | 1193.4 | 44692 | 0.3375 | 44692 | 0.36875 | 0.75 | Ground leakage current | 0.088864 | 0.8107 | 85.9754 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | May | Inv-3 | Ground fault | 1193.4 | 44692 | 0.42292 | 44692 | 0.44583 | 0.55 | Ground leakage current | 0.06607 | 0.8107 | 63.9215 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | May | Inv-6 | Ground fault | 1206 | 44692 | 0.3375 | 44692 | 0.35903 | 0.51667 | Ground leakage current | 0.053186 | 0.8107 | 52.0004 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | May | Inv-6 | Ground fault | 1206 | 44692 | 0.42361 | 44692 | 0.44444 | 0.5 | Ground leakage current | 0.05826 | 0.8107 | 56.961 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | May | Inv-10 | Ground fault | 1224 | 44692 | 0.42292 | 44692 | 0.45208 | 0.7 | Ground leakage current | 0.0969 | 0.8107 | 96.1536 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | May | All Inverters | Feeder tripped | 12008.7 | 44694 | 0.69236 | 44694 | 0.69583 | 0.083333 | Breaker tripped on EL R phase from gss end | 0.003321 | 0.8022 | 31.9925 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | May | All Inverters | Grid failure | 12008.7 | 44698 | 0.64375 | 44698 | 0.68403 | 0.96667 | 33KV Bay Tripped From GSS End | 0.029583 | 0.793 | 281.7159 | Charged From GSS End.
Kodangal | May | Inverter-1 | Ground fault | 1193.4 | 44699 | 0.65278 | 44699 | 0.66944 | 0.4 | Ground leakage current due to String Fault | 0.064591 | 0.8194 | 63.1617 | Isolated the string and Inverter taken into load
Kodangal | May | INV-1,SCB-7,STR-16 | String fault | 9 | 44699 | 0.67014 | 44699 | 0.72917 | 1.4167 | String Cable Damage | 0.15385 | 0.8194 | 1.1346 | New string cable replaced
Kodangal | May | All Inverters | Feeder tripped | 12008.7 | 44702 | 0.26944 | 44702 | 0.42014 | 3.6167 | Pole no-85,91 Y-phase pin insulator is damaged | 0.6305 | 0.7725 | 5848.9724 | New Pin insulator is replaced .Charged the line and kept under observation
Kodangal | May | All Inverters | Feeder tripped | 12008.7 | 44708 | 0.42639 | 44708 | 0.42986 | 0.083333 | Bird flash our at P-181 | 0.0644 | 0.7841 | 606.3918 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | June | Inv-9 | Ground fault | 1188 | 44727 | 0.44236 | 44727 | 0.45903 | 0.4 | Ground leakage current due to Rainfall | 0.10817 | 0.8342 | 107.199 | reset the fault and charged the inverter
Kodangal | June | All Inverters | Feeder tripped | 12008.7 | 44733 | 0.49722 | 44733 | 0.52083 | 0.56667 | Main Outgoing Breaker Tripped due to OC | 0.3581 | 0.7661 | 3294.4717 | Reset the fault and charged the Breaker.
Kodangal | June | Block-3,IDT-5 | IDT 05 tripped | 2412 | 44733 | 0.52153 | 44733 | 0.6 | 1.8833 | IDT Tripped Due to Buccolz Relay & PRV Relay Operated. | 1.114 | 0.7661 | 2058.4862 | IDT all Air Release Valves Checked,HV & LV Side IR test Conducted & Charged.
Kodangal | June | Inverter-9 | Ground fault | 1188 | 44741 | 0.31042 | 44741 | 0.33056 | 0.48333 | Ground leakage current | 0.10159 | 0.8245 | 99.5051 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | June | Inverter-9 | Ground fault | 1188 | 44741 | 0.35 | 44741 | 0.35625 | 0.15 | Ground leakage current | 0.034774 | 0.8245 | 34.0613 | checked the Vtg at SCB level and found abnormality in one string, Isolated the string and Inverter taken into load
Kodangal | June | INV-9,SCB-4,STR-14 | String fault | 9 | 44741 | 0.35694 | 44741 | 0.45486 | 2.35 | String Cable Damage | 0.8318 | 0.8245 | 6.1724 | New string cable replaced
Kodangal | July | Inverter-10 | Ground fault | 1224 | 44744 | 0.26389 | 44744 | 0.29097 | 0.65 | Ground leakage current | 0.027071 | 0.8412 | 27.8733 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | July | Inverter-2 | Ground fault | 1193.4 | 44745 | 0.54722 | 44745 | 0.58333 | 0.86667 | Ground leakage current | 0.2508 | 0.8241 | 246.657 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | July | Inverter-3 | Ground fault | 1193.4 | 44745 | 0.54653 | 44745 | 0.57431 | 0.66667 | Ground leakage current | 0.2067 | 0.8241 | 203.2855 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | July | Inverter-2 | Ground fault | 1193.4 | 44747 | 0.51528 | 44747 | 0.53333 | 0.43333 | Ground leakage current | 0.1613 | 0.823 | 158.4237 | checked the Vtg at SCB level and found abnormality in few string, Isolated the string and Inverter taken into load
Kodangal | July | Inv-2,SCB-7,STR-11 | String fault | 9 | 44747 | 0.53403 | 44747 | 0.64583 | 2.6833 | String Cable Damage | 0.413 | 0.823 | 3.0591 | New string cable replaced
Kodangal | July | Inverter-5 | Ground fault | 1206 | 44747 | 0.59861 | 44747 | 0.62569 | 0.65 | Ground leakage current | 0.0339 | 0.823 | 33.647 | Checked the Voltage at inverter level, reset the fault and charged the inverter
Kodangal | July | All Inverters | Feeder tripped | 12008.7 | 44750 | 0.26944 | 44750 | 0.32847 | 1.4167 | Pole no-80, Y-phase pin insulator is damaged | 0.070261 | 0.807 | 680.8999 | New Pin insulator is replaced .Charged the line and kept under observation
Kodangal | July | Inv-1,2,3,4 | Block 01 tripped | 4772.7 | 44750 | 0.33333 | 44750 | 0.36458 | 0.75 | Moisture observed in Cable chamber | 0.1153 | 0.807 | 444.0859 | removed the moisture and charged the feeder
Kodangal | July | IDT-5 | IDT 05 tripped | 2412 | 44750 | 0.33333 | 44750 | 0.48611 | 3.65 | Moisture observed in Cable chamber | 0.7 | 0.807 | 1368 | removed the moisture and charged the feeder
Kodangal | July | IDT-2 | IDT 02 tripped | 2385.9 | 44750 | 0.48681 | 44750 | 0.74028 | 6.0833 | Moisture observed in Cable chamber | 1.0043 | 0.807 | 1933.7006 | removed the moisture and charged the feeder
Kodangal | July | IDT-5 | IDT 05 tripped | 2412 | 44750 | 0.60417 | 44750 | 0.66667 | 1.5 | Moisture observed in Cable chamber | 0.2413 | 0.807 | 469.6866 | removed the moisture and charged the feeder
Kodangal | July | All Inverters | Plant tripped on O/C fault | 12008.7 | 44751 | 0.41528 | 44751 | 0.41944 | 0.1 | Due to I/C-3 Feeder Feedback Main O/G Triiped on O/C. | 0.0086248 | 0.8214 | 85.0746 | Isolated the I/C-3 & O/G Feeder Taken into Load.
Kodangal | July | INV-9,10 | IDT 05 tripped | 2412 | 44751 | 0.42014 | 44751 | 0.43194 | 0.28333 | Due to Moisture Contained | 0.040565 | 0.8214 | 80.3691 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | July | Inverter-3 | Ground fault | 1193.4 | 44755 | 0.27778 | 44755 | 0.36875 | 2.1833 | Ground leakage current | 0.11974 | 0.8635 | 123.388 | checked the Vtg at SCB level and found abnormality in one string, Isolated the string and Inverter taken into load
Kodangal | July | INV-3,SCB-2,STR-17,18 | String fault | 18 | 44755 | 0.36944 | 44755 | 0.66319 | 7.05 | String Cable Damage due to Continuos Rain | 1.1331 | 0.8635 | 17.6118 | Replaced with a New String Cable.
Kodangal | July | INV-3,SCB-2,STR-14,15,16 | String fault | 27 | 44755 | 0.36944 | 44755 | 0.76042 | 9.3833 | String Cable Damage due to Continuos Rain | 1.2402 | 0.8635 | 28.9146 | due to continuous rain fall rectification is not happening
Kodangal | July | INV-3,SCB-2,STR-14 | String fault | 9 | 44756 | 0.25903 | 44756 | 0.29514 | 0.86667 | String Cable Damage due to Continuos Rain | 0.042924 | 0.8692 | 0.33579 | Replaced with a New String Cable.
Kodangal | July | INV-3,SCB-2,STR-15 | String fault | 9 | 44756 | 0.25903 | 44756 | 0.3125 | 1.2833 | String Cable Damage due to Continuos Rain | 0.089122 | 0.8692 | 0.69719 | Replaced with a New String Cable.
Kodangal | July | INV-3,SCB-2,STR-16 | String fault | 9 | 44756 | 0.25903 | 44756 | 0.32292 | 1.5333 | String Cable Damage due to Continuos Rain | 0.13286 | 0.8692 | 1.0393 | Replaced with a New String Cable.
Kodangal | July | INV-1,SCB-6,STR-11 sub string | String fault | 3 | 44764 | 0.52569 | 44764 | 0.6875 | 3.8833 | Damage module scanning | 0.75 | 0.8501 | 1.9127 | after damaged modules scanning string connected into load
Kodangal | July | Inverter-5 | Ground fault | 1206 | 44770 | 0.47292 | 44770 | 0.49653 | 0.56667 | Ground leakage current | 0.396 | 0.807 | 385.4038 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | July | All Inverters | Plant tripped on E/L fault | 12008.7 | 44770 | 0.66042 | 44770 | 0.75 | 2.15 | Pole no-189, Y-phase pin insulator was damaged | 0.491 | 0.807 | 4758.2913 | New Pin insulator is replaced , Charged the line and kept under observation
Kodangal | July | Inverter-5 | Ground fault | 1206 | 44771 | 0.41111 | 44771 | 0.43403 | 0.55 | Ground leakage current | 0.43 | 0.8041 | 416.9902 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | All Inverters | Feeder tripped | 12008.7 | 44774 | 0.46181 | 44774 | 0.47361 | 0.28333 | Due to I/C-3 Feeder Feedback Main O/G Triiped on O/C. | 0.269 | 0.8103 | 2617.5447 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | August | Inverter-1 | Ground fault | 1193.4 | 44774 | 0.47431 | 44774 | 0.49931 | 0.6 | Ground leakage current | 0.548 | 0.8103 | 529.9226 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | Inverter-3 | Ground fault | 1193.4 | 44774 | 0.47431 | 44774 | 0.50694 | 0.78333 | Ground leakage current | 0.695 | 0.8103 | 672.0734 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | All Inverters | Plant tripped on O/C fault | 12008.7 | 44776 | 0.36736 | 44776 | 0.37431 | 0.16667 | Due to I/C-3 Feeder Feedback Main O/G Triiped on O/C. | 0.065 | 0.8103 | 632.4922 | Isolated the IDT-5 and O/G Feeder charged.
Kodangal | August | INV-9,10 | IDT 05 tripped | 2412 | 44776 | 0.37431 | 44776 | 0.75556 | 9.15 | Due to Moisture Contained | 3.102 | 0.8103 | 6062.684 | As per Testing team suggesions Trafo tests compeleted, due to Low IR values IDT-5 is under breakdown.
Kodangal | August | Inverter-1 | Ground fault | 1193.4 | 44776 | 0.59375 | 44776 | 0.65694 | 1.5167 | Ground leakage current | 0.29 | 0.8103 | 280.4335 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | Inverter-8 | Ground fault | 1206 | 44776 | 0.59375 | 44776 | 0.63194 | 0.91667 | Ground leakage current | 0.19 | 0.8103 | 185.6721 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | Inveter-5 | Ground leakage current fault | 12060 | 44777 | 0.40972 | 44777 | 0.41667 | 0.16667 | Ground leakage current | 0.05 | 0.8103 | 488.6109 | Isolated the SCB-3 and charged the inverter
Kodangal | August | INV-5 | String fault | 162 | 44777 | 0.41667 | 44777 | 0.53889 | 2.9333 | Inv-5 SCB-3 Negative TBs melted. | 2.04 | 0.8103 | 267.7879 | Replaced the -ve TB'S
Kodangal | August | Inv-5 SCB-3 Str-7,12. | String fault | 18 | 44777 | 0.53958 | 44777 | 0.70833 | 4.05 | String Cable Damage due to Continuos Rain | 1.43 | 0.8103 | 20.8571 | String cable rectification completed
Kodangal | August | Inv-5 SCB-3 Str-17 | String fault | 9 | 44777 | 0.53958 | 44777 | 0.72014 | 4.3333 | String Cable Damage due to Continuos Rain | 5 | 0.8103 | 36.4635 | String cable rectification work in progress
Kodangal | August | INV-9,10 | IDT 05 tripped | 2412 | 44777 | 0.26319 | 44777 | 0.72014 | 10.9667 | Due to I/C-3 Feeder Triiped on O/C. | 5.306 | 0.8103 | 10370.2777 | As per Testing team suggesions Trafo tests compeleted, due to Low IR values IDT-5 is under breakdown.
Kodangal | August | Inv-8 | Ground fault | 1206 | 44778 | 0.59028 | 44778 | 0.59375 | 0.083333 | Ground leakage current | 0.04 | 0.8103 | 39.0889 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | Inv-9 ,10 | IDT 05 tripped | 2412 | 44778 | 0.26528 | 44779 | 0.66667 | 21.73 | Due to I/C-3 Feeder Triiped on O/C. | 8.49 | 0.8103 | 16583 | due to Low IR values IDT-5 is under breakdown. Suspecting HV bushings and replaced
Kodangal | August | Inverter-2 | Ground fault | 1193.4 | 44790 | 0.67778 | 44790 | 0.72847 | 1.2167 | Ground leakage current | 0.3225 | 0.8016 | 308.513 | Checked the Voltage at inverter level, no abnormality found. reset the fault and charged the inverter
Kodangal | August | Inverter-2 | Ground fault | 1193.4 | 44791 | 0.35556 | 44791 | 0.36736 | 0.28333 | Ground leakage current | 0.1455 | 0.7958 | 138.1825 | Isolated the Faulty strings & Inverter taken into load
Kodangal | August | Inverter-2 | Ground fault | 1193.4 | 44791 | 0.38403 | 44791 | 0.39167 | 0.18333 | Ground leakage current | 0.1101 | 0.7958 | 104.5628 | Isolated the Faulty strings & Inverter taken into load
Kodangal | August | Inv-2 SCB-1 Str-5,13,14 | String fault | 27 | 44791 | 0.39236 | 44791 | 0.57639 | 4.4167 | String Cable Damage and damage module | 3.5793 | 0.7958 | 76.907 | Replaced with a New String Cable.
Kodangal | August | Inv-2 SCB-6 Str-1,17,14 | String fault | 27 | 44791 | 0.39236 | 44791 | 0.60764 | 5.1667 | String Cable Damage and damage module | 4.144 | 0.7958 | 89.0405 | Replaced with a New String Cable.
Kodangal | August | Incomer-1 | Incomer 01 tripped | 4772.7 | 44804 | 0.50417 | 44804 | 0.50833 | 0.1 | Tripped on O/C in Y-Phase | 0.10412 | 0.7946 | 394.8748 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | September | Block-2 | Block 02 tripped | 4824 | 44807 | 0.54097 | 44807 | 0.55486 | 0.33333 | Transformer Tripped due to WTI Trip Alarm | 0.2 | 0.7634 | 736.5283 | Afternormalisation of temperature reset the fault and charged the IDT.(4 Inv tripped due to Aux supply fail, Aux trafo connected in IDT-4)
Kodangal | September | All Inverters | Plant tripped on E/L fault | 12008.7 | 44808 | 0.35208 | 44808 | 0.36528 | 0.31667 | Main Outgoing Breaker Tripped due to E/L | 0.168 | 0.8013 | 1616.592 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | September | Inverter-3 | Ground fault | 1193.4 | 44811 | 0.59444 | 44811 | 0.62222 | 0.66667 | Ground leakage current | 0.1987 | 0.8104 | 192.169 | Isolated the Faulty strings & Inverter taken into load, after that faulty string also taken into load within few minutes
Kodangal | September | All Inverters | Plant tripped on O/C fault | 12008.7 | 44815 | 0.38125 | 44815 | 0.39236 | 0.26667 | Breaker Tripped due to Over Current & Earth Faulit. | 0.0429 | 0.8516 | 438.7215 | Trail charge taken feeder withstand healthy, kept under observation
Kodangal | September | Incomer-1 | Incomer 01 tripped | 4772.7 | 44815 | 0.39306 | 44815 | 0.39583 | 0.066667 | Breaker Tripped due to Over Current. | 0.0121 | 0.8516 | 49.1796 | Trail charge taken feeder withstand healthy, kept under observation
Mahabubnagar | May | All INVs | LC taken | 11599 | 44695 | 0.27083 | 44695 | 0.34375 | 1.75 | FS DEVCO LC taken on 33KV line,End termination B-phase failure | 0.36656 | 0.49327 | 2097.2388 | FS DEVCO after rectification ,plant charged
Mahabubnagar | May | All INVs | LC taken | 11599 | 44695 | 0.41806 | 44695 | 0.52292 | 2.5167 | FS DEVCO LC taken on 33KV line,End termination B-phase failure | 2.1151 | 0.49327 | 12101.5409 | FS DEVCO after rectification ,LC returns
Mahabubnagar | May | All INVs | Grid failure | 11599 | 44703 | 0.48194 | 44703 | 0.48958 | 0.18333 | GSS end grid flatuation happened due to this our plant also tripped | 0.18738 | 0.68776 | 1494.8281 | Plant charged
Mahabubnagar | May | All INVs | LC taken | 11599 | 44703 | 0.56181 | 44703 | 0.62361 | 1.4833 | FS DEVCO LC taken on 33KV line, tower no-7 R-phase jumpher failure | 1.2052 | 0.68776 | 9614.3652 | FS DEVCO after rectification ,plant charged
Mahabubnagar | June | SCB.06.02 | String fault | 8.325 | 44730 | 0.26111 | 44730 | 0.51736 | 6.15 | Inv-6 SCB-2 ST-03 20A fuse blown | 3.2445 | 0.85681 | 23.1427 | Healthy Fuse replaced
Mahabubnagar | June | SCB.09.02 | String fault | 8.325 | 44730 | 0.26111 | 44730 | 0.47708 | 5.1833 | Inv-9 SCB-2 ST-10 20A fuse blown | 2.4499 | 0.85681 | 17.4749 | Healthy Fuse replaced
Mahabubnagar | June | All INVs | Feeder tripped | 11599 | 44732 | 0.54167 | 44732 | 0.63056 | 2.1333 | Transmission line pole-5 R-phase Pin Insulator blown | 0.85454 | 0.69333 | 6872.1616 | After Pin Insulator replced ,feeder charge by GSS tem
Mahabubnagar | June | All INVs | Feeder tripped | 11599 | 44733 | 0.6875 | 44733 | 0.69514 | 0.18333 | TL Tripped on O/C & E/F due to heavy wind | 0.0098037 | 0.86845 | 98.7534 | After decrease the wind speed, feeder Charged by GSS Team
Mahabubnagar | June | SCB.03.03 | String fault | 8.325 | 44741 | 0.27083 | 44741 | 0.33819 | 1.6167 | Inv-3 SCB-3 ST-5 20A fuse blown | 0.27979 | 0.8519 | 1.9843 | Healthy Fuse replaced
Mahabubnagar | July | SCB.11.06 | String fault | 8.325 | 44750 | 0.29792 | 44750 | 0.35 | 1.25 | Inv-11 SCB-6 ST-2 20A fuse blown | 0.08 | 0.92607 | 0.61676 | Healthy Fuse replaced
Mahabubnagar | July | Inverter 12 | Insulation fault | 966 | 44752 | 0.42847 | 44752 | 0.43333 | 0.11667 | Inv-12 tripped on isulation fault. | 0.02 | 0.91441 | 17.6664 | Checked all SMB's floating found good, then restore the inverter.
Mahabubnagar | July | Inverter 12 | Insulation fault | 966 | 44752 | 0.44028 | 44752 | 0.44236 | 0.05 | Inv-12 tripped on isulation fault. | 0.012 | 0.91441 | 10.5998 | Checked all SMB's floating found good, then restore the inverter.
Mahabubnagar | July | Inverter 12 | Insulation fault | 966 | 44752 | 0.49306 | 44752 | 0.50903 | 0.38333 | Inv-12 tripped on isulation fault. | 0.078 | 0.91441 | 68.899 | Checked all SMB's floating found abnormalitie strings, isolated faulty string go, then restore the inverter.
Mahabubnagar | July | SCB.12.07 | String fault | 8.325 | 44752 | 0.50972 | 44752 | 0.55556 | 1.1 | String-14 cable melted between SMB to String. | 0.23 | 0.91441 | 1.7509 | Rectified by using two pairs MC4 connectors and taken to load.
Mahabubnagar | July | SCB.12.07 | String fault | 8.325 | 44752 | 0.50972 | 44752 | 0.55556 | 1.1 | String-15 cable melted between SMB to String. | 0.23 | 0.91441 | 1.7509 | Rectified by using two pairs MC4 connectors and taken to load.
Mahabubnagar | July | SCB.10.06 | String fault | 8.325 | 44757 | 0.24444 | 44757 | 0.49861 | 6.1 | During string monitoring found 20A fuse were failure. ,string -13 floating ,MC4 connectors and modules checked found healthy | 2.33 | 0.85511 | 16.5868 | Checked the string floating found good, then restore the string by replaced 20A Fuse.
Mahabubnagar | July | All INVs | Feeder tripped | 11599 | 44760 | 0.56736 | 44760 | 0.575 | 0.18333 | TL Tripped on O/V | 0.057 | 0.88873 | 587.575 | Taken the trail charge after confirmation of Substation it is withstand the supply.
Mahabubnagar | July | Inverter 03 | Insulation fault | 966 | 44760 | 0.39931 | 44760 | 0.40208 | 0.066667 | Inv-3 tripped on isulation fault,due to CB-8,string-13 string cable ground | 0.026 | 0.88873 | 22.3212 | Checked all SMB's floating found abnormalitie strings, isolated faulty string, then restore the inverter.
Mahabubnagar | July | Inverter 03 | String fault | 8.325 | 44760 | 0.40278 | 44760 | 0.45833 | 1.3333 | String Cable Insulation failed inside trench due to cable grounded . | 0.033 | 0.88873 | 0.24416 | Rectified by using 4 pairs MC4 connectors and taken to load.
Mahabubnagar | July | All INVs | Grid failure | 11599 | 44762 | 0.29444 | 44762 | 0.31181 | 0.41667 | 33KV TL Tripped on O/V Due to Grid Fluctuations. | 0.074793 | 0.85399 | 740.8618 | Communicate with GSS Operator, GSS team changed the Tap Position of PTR at GSS. After that changes we charge the plant, Its withstand supply. .
Mahabubnagar | July | Inverter 03 | String fault | 8.325 | 44768 | 0.28889 | 44768 | 0.53125 | 5.8167 | During string monitoring found 20A fuse were failure. | 1.386 | 0.92027 | 10.6187 | Checked the string floating found good, then restore the string by replaced 20A Fuse.
Mahabubnagar | July | All INVs | Grid failure | 11599 | 44773 | 0.51042 | 44773 | 0.51736 | 0.16667 | TL Tripped on O/V Due to Grid Fluctuations. | 0.085897 | 0.86164 | 858.4665 | Communicate with GSS Operator, He chenged the Tap Position of PTR at GSS. After that changes we charge the plant, Its withstand supply.
Mahabubnagar | August | All INVs | Grid failure | 11599 | 44795 | 0.73264 | 44795 | 0.74028 | 0.18333 | Plant end O/G Breaker Tripped on O/V Due to Grid Fluctuations. | 0.018 | 0.87043 | 181.7308 | Communicate with GSS Operator, He chenged the Tap Position of PTR at GSS. After that changes we charge the plant, Its withstand supply.
Mahabubnagar | August | All INVs | Grid failure | 11599 | 44797 | 0.54861 | 44797 | 0.55556 | 0.16667 | I/C Breaker Tripped on O/V fault due to at GSS End Kondapur 33KV distribution feeder tripped at that time voltage fluctuated on grid. | 0.087 | 0.86512 | 873.004 | Communicate with GSS Operator, and charge plant after normalised the voltage level.
Mahabubnagar | August | All INVs | Grid failure | 11599 | 44799 | 0.42708 | 44799 | 0.43333 | 0.15 | I/C Breaker Tripped on O/V fault due to at GSS End tripped at that time voltage fluctuated on grid. | 0.16606 | 0.92092 | 1773.8541 | Communicate with GSS Operator, and charge plant after normalised the voltage level.
Mahabubnagar | August | All INVs | Feeder tripped | 11599 | 44800 | 0.49861 | 44800 | 0.50347 | 0.11667 | TL Tripped on O/C & E/F | 0.024151 | 0.83809 | 234.7735 | Taken the trail charge after confirmation of Substation it is withstand the supply.
Mahabubnagar | September | All INVs | Feeder tripped | 11599 | 44808 | 0.29931 | 44808 | 0.30208 | 0.066667 | TL Tripped on O/C & E/F | 0.0098424 | 0.86917 | 99.2266 | Taken the trail charge after confirmation of Substation it is withstand the supply. And checked fault hystory in GSS End found Instantaneuos O/C fault recorded. And line patroling also completed we suspected at pole-98 have bushes.
Malwa | April | Inverter 34 | IGBT stack faulty | 659.65 | 44652 | 0.375 | 44652 | 0.65972 | 6.8333 | Inv - 34 running on 50% Load due to IGBT stack failure of W2-Phase | 4.51 | 0.67424 | 2005.8684 | Inverter stopped at 5 Pm for Replaced Faulty IGBT Stack. After Replaced inv will be start on Full Load.
Malwa | April | Inverter 34 | IGBT SAT Trip | 1319.28 | 44653 | 0.27431 | 44653 | 0.31597 | 1 | Inv - 34 tripped due to IGBT SAT Trip | 0.11855 | 0.68076 | 106.4709 | After replaced Faulty IGBT stack, Inv tripped on IGBT SAT Trip. So we checked & Rectified
Malwa | April | Inverter 40 | Keypad card comm. failure | 1324.44 | 44653 | 0.38542 | 44653 | 0.39931 | 0.33333 | Inv - 40 tripped due to Keypad Card Communication Failure | 0.27457 | 0.68076 | 247.5549 | checked & rectified
Malwa | April | SCB.35.11 | String fault | 24 | 44653 | 0.27778 | 44653 | 0.46875 | 4.5833 | 4 nos. Strings Faulty | 2.444 | 0.68076 | 39.9304 | checked & rectified
Malwa | April | SCB.22.03 | String fault | 24 | 44655 | 0.27778 | 44655 | 0.52083 | 5.8333 | 4 nos. Strings Faulty | 3.95 | 0.68631 | 65.0623 | checked & rectified
Malwa | April | SCB.29.05 | String fault | 6 | 44656 | 0.28125 | 44656 | 0.4375 | 3.75 | 1 nos. Strings Faulty | 1.888 | 0.67935 | 7.6957 | checked & rectified
Malwa | April | SCB.32.07 | String fault | 18 | 44657 | 0.27778 | 44657 | 0.45833 | 4.3333 | 3 nos. Strings Faulty | 2.331 | 0.66767 | 28.0141 | checked & rectified
Malwa | April | All Inverters | Overvoltage fault | 26521 | 44657 | 0.54722 | 44657 | 0.55694 | 0.23333 | 33 Outgoing panel tripped due to Overvoltage (27) Fault | 0.2386 | 0.66767 | 4224.9613 | As per Instruction, Checked visual inspection of 132kV & 33kV Switchyard & VCB panel. After normalization of Voltage we started Feeder.
Malwa | April | Inverter 24 | DC CB ON failure | 1324.56 | 44657 | 0.55694 | 44657 | 0.56597 | 0.21667 | Inv - 34 tripped due to DC CB ON failure | 0.18 | 0.66767 | 159.1866 | checked & rectified
Malwa | April | Inverter 37 | 100V DC failure | 1321.2 | 44657 | 0.55694 | 44657 | 0.5625 | 0.13333 | Inv - 37 tripped due to 100V DC Failure | 0.1632 | 0.66767 | 143.9631 | checked & rectified
Malwa | April | Inverter 38 | 100V DC failure | 1320.6 | 44657 | 0.55694 | 44657 | 0.55903 | 0.05 | Inv - 38 tripped due to 100V DC Failure | 0.08229 | 0.66767 | 72.5572 | checked & rectified
Malwa | April | Inverter 39 | 100V DC failure | 1324.08 | 44657 | 0.55694 | 44657 | 0.5625 | 0.13333 | Inv - 39 tripped due to 100V DC Failure | 0.1632 | 0.66767 | 144.2769 | checked & rectified
Malwa | April | Inverter 40 | 100V DC failure | 1324.44 | 44657 | 0.55694 | 44657 | 0.56181 | 0.11667 | Inv - 40 tripped due to 100V DC Failure | 0.1632 | 0.66767 | 144.3161 | checked & rectified
Malwa | April | Inverter 30 | AC side CT issue | 1329.84 | 44658 | 0.5 | 44658 | 0.52083 | 0.5 | Inv - 30 running low as compare to other inv | 0.62 | 0.68359 | 563.6232 | we checked & Rectified fault
Malwa | April | SCB.02.07 | String fault | 18 | 44659 | 0.275 | 44659 | 0.45903 | 4.4167 | 3 nos. Strings Faulty | 2.371 | 0.66387 | 28.3326 | checked & rectified
Malwa | April | All Inverters | Overvoltage fault | 26491 | 44659 | 0.35625 | 44659 | 0.36042 | 0.1 | P1, 33 Outgoing panel tripped due to Overvoltage (27) Fault | 0.06646 | 0.66387 | 1168.8038 | As per Instruction, Checked visual inspection of 132kV & 33kV Switchyard & VCB panel. After normalization of Voltage we started Feeder.
Malwa | April | All Inverters | Overvoltage fault | 26521 | 44659 | 0.35625 | 44659 | 0.36042 | 0.1 | P2, 33 Outgoing panel tripped due to Overvoltage (27) Fault | 0.06646 | 0.66387 | 1170.1275 | As per Instruction, Checked visual inspection of 132kV & 33kV Switchyard & VCB panel. After normalization of Voltage we started Feeder.
Malwa | April | Inverter 05 | DC under voltage | 5310.8 | 44659 | 0.35625 | 44659 | 0.36528 | 0.21667 | Block - 2, LCR - 2 All Inverter stopped due to UPS tripped on DC Undervolted | 0.12941 | 0.66387 | 456.2582 | checked & rectified
Malwa | April | Inverter 13 | INT CONFIG fault | 1335.96 | 44659 | 0.35625 | 44659 | 0.36875 | 0.3 | Inv - 13 tripped due to INT CONFIG (5410) | 0.1762 | 0.66387 | 156.2724 | checked & rectified
Malwa | April | Inverter 21 | 100V DC failure | 5297.4 | 44659 | 0.35625 | 44659 | 0.375 | 0.45 | Block - 6, LCR - 1 All Inverter stopped due to 100V DC Failure | 0.2751 | 0.66387 | 967.4673 | checked & rectified
Malwa | April | Inverter 29 | DC under voltage | 5323.1 | 44659 | 0.35625 | 44659 | 0.375 | 0.45 | Block - 8, LCR - 3 All Inverter stopped due to UPS tripped on DC Undervolted | 0.2751 | 0.66387 | 972.1609 | checked & rectified
Malwa | April | Inverter 37 | 100V DC failure | 1321.2 | 44659 | 0.35625 | 44659 | 0.37153 | 0.36667 | Inv - 37 tripped due to 100V DC Failure | 0.22474 | 0.66387 | 197.1205 | checked & rectified
Malwa | April | Inverter 38 | 100V DC failure | 1320.6 | 44659 | 0.35625 | 44659 | 0.36458 | 0.2 | Inv - 38 tripped due to 100V DC Failure | 0.12941 | 0.66387 | 113.4546 | checked & rectified
Malwa | April | Inverter 40 | 100V DC failure | 1324.44 | 44659 | 0.35625 | 44659 | 0.36806 | 0.28333 | Inv - 40 tripped due to 100V DC Failure | 0.1762 | 0.66387 | 154.9249 | checked & rectified
Malwa | April | Inverter 39 | 100V DC failure | 1324.08 | 44659 | 0.35625 | 44659 | 0.37153 | 0.36667 | Inv - 39 tripped due to 100V DC Failure | 0.22474 | 0.66387 | 197.5502 | checked & rectified
Malwa | April | SCB.19.02 | String fault | 12 | 44659 | 0.50694 | 44659 | 0.77153 | 6.35 | SCB 512, String no. 23 & 24 Manually Open for new module Installation. String open as per instruct by VG Project Team | 3.98 | 0.66387 | 31.7064
Malwa | April | SCB.23.09 | String fault | 24 | 44660 | 0.26736 | 44660 | 0.48958 | 5.3333 | 4 nos. Strings Faulty | 2.9 | 0.68587 | 47.7367 | checked & rectified
Malwa | April | SCB.19.02 | String fault | 12 | 44660 | 0.26736 | 44660 | 0.77083 | 12.0833 | SCB 512, String no. 23 & 24 Manually Open for new module Installation. String open as per instruct by VG Project Team | 7.03 | 0.68587 | 57.8601
Malwa | April | SCB.19.02 | String fault | 12 | 44661 | 0.26528 | 44661 | 0.77431 | 12.2167 | SCB 512, String no. 23 & 24 Manually Open for new module Installation. String open as per instruct by VG Project Team | 7.01 | 0.68678 | 57.772
Malwa | April | SCB.30.08 | String fault | 30 | 44662 | 0.27083 | 44662 | 0.50347 | 5.5833 | 5 nos. Strings Faulty | 3.09 | 0.69414 | 64.3465 | checked & rectified
Malwa | April | SCB.19.02 | String fault | 12 | 44662 | 0.27083 | 44662 | 0.71181 | 10.5833 | SCB 512, String no. 23 & 24 Manually Open for new module Installation. String open as per instruct by VG Project Team | 6.44 | 0.69414 | 53.6429 | String no 23&24 load connected.
Malwa | April | Inverter 02 | No Comm. fault | 1331.4 | 44663 | 0.26458 | 44663 | 0.28889 | 0.58333 | Inv - 2 tripped due to NO COMMUCATION failure | 0.031692 | 0.69226 | 29.2097 | checked & rectified
Malwa | April | Inverter 05 | No Comm. fault | 1325.4 | 44665 | 0.4625 | 44665 | 0.46944 | 0.16667 | Inv - 5 tripped due to NO COMMUCATION failure | 0.2424 | 0.68108 | 218.8162 | checked & rectified
Malwa | April | SCB.11.08 | String fault | 18 | 44666 | 0.26111 | 44666 | 0.45903 | 4.75 | 3 nos. Strings Faulty | 2.381 | 0.68795 | 29.484 | checked & rectified
Malwa | April | Inverter 40 | AC Overcurrent fault | 1324.44 | 44668 | 0.46181 | 44668 | 0.57986 | 2.8333 | Inv - 40 tripped due to AC OVERCURRENT fault | 2.86 | 0.67791 | 2567.865 | checked & rectified
Malwa | April | Inverter 03 | INT CONFIG fault | 1323.6 | 44669 | 0.28889 | 44669 | 0.45208 | 3.9167 | Inv - 3 tripped due to INT CONFIG (5410) fault | 3.04 | 0.67601 | 2720.0998 | Inv started on 2 nos. ISU with 70% load at 10:51 am. We informed to ABB.
Malwa | April | Inverter 33 | AC side CT issue | 1332.72 | 44669 | 0.48611 | 44669 | 0.53472 | 1.1667 | Inv - 33 was running low as compare to other | 0.94 | 0.67601 | 846.8788 | checked & rectified
Malwa | April | Inverter 03 | Inv curtailed | 397.08 | 44670 | 0.41389 | 44670 | 0.61181 | 4.75 | Inv - 3 Running on 2 nos. ISU with 70% load | 3.02 | 0.67905 | 814.3072 | ABB Engineer Reached at site & started work.
Malwa | April | SCB.36.09 | String fault | 24 | 44671 | 0.26111 | 44671 | 0.47222 | 5.0667 | 4 nos. Strings Faulty | 2.7276 | 0.67632 | 44.2737 | checked & rectified
Malwa | April | Inverter 03 | Short circuit fault | 1323.6 | 44671 | 0.26111 | 44671 | 0.28194 | 0.5 | Inv - 3 tripped due to SC CKT Fault | 0.026958 | 0.67632 | 24.1323 | checked & rectified
Malwa | April | SCB.01.08 | String fault | 42 | 44672 | 0.28194 | 44672 | 0.48333 | 4.8333 | 7 nos. Strings Faulty | 1.24 | 0.73869 | 38.4707 | checked & rectified
Malwa | April | Inverter 03 | PPCC Link failure | 1323.6 | 44672 | 0.28194 | 44672 | 0.30625 | 0.58333 | Inv - 3 tripped due to PPCC Link Failure | 0.025248 | 0.73869 | 24.6856 | Replaced FO Cable
Malwa | April | SCB.08.01 | String fault | 42 | 44673 | 0.26111 | 44673 | 0.50069 | 5.75 | 7 nos. Strings Faulty | 3.1356 | 0.69981 | 92.1621 | checked & rectified
Malwa | April | SCB.14.05 | String fault | 12 | 44674 | 0.26111 | 44674 | 0.43819 | 4.25 | 2 nos. Strings Faulty | 1.9874 | 0.68132 | 16.2491 | checked & rectified
Malwa | April | SCB.24.02 | String fault | 12 | 44674 | 0.26042 | 44674 | 0.46875 | 5 | 2 nos. Strings Faulty | 2.702 | 0.68132 | 22.0908 | checked & rectified
Malwa | April | SCB.20.03 | String fault | 12 | 44676 | 0.25764 | 44676 | 0.44792 | 4.5667 | 2 nos. Strings Faulty | 2.23 | 0.67484 | 18.0588 | checked & rectified
Malwa | April | Inverter 40 | Fan failure | 1324.44 | 44677 | 0.47569 | 44677 | 0.48611 | 0.25 | Inv - 40 tripped due to Inverter Temp. Fin Failure | 0.327 | 0.6794 | 294.2433 | checked & rectified
Malwa | April | SCB.30.07 | String fault | 30 | 44677 | 0.25694 | 44677 | 0.46875 | 5.0833 | 5 nos. Strings Faulty | 2.608 | 0.6794 | 53.1564 | checked & rectified
Malwa | April | SCB.26.06 | String fault | 12 | 44680 | 0.26042 | 44680 | 0.45833 | 4.75 | 2 nos. Strings Faulty | 2.36 | 0.67894 | 19.2275 | checked & rectified
Malwa | May | Inverter 24 | DC CB ON failure | 1324.56 | 44685 | 0.29167 | 44685 | 0.30208 | 0.25 | Inv - 24 Tripped Due to DC CB ON failure | 0.0573 | 0.6717 | 50.9802 | checked & rectified
Malwa | May | Inverter 12 | INT CONFIG fault | 1323.84 | 44688 | 0.26875 | 44688 | 0.51181 | 5.8333 | Inv - 12 tripped due to INT CONFIG (5410) failure | 3.8 | 0.67885 | 3415.0115 | after checking found IGBT card faulty in ISU-1 than inverter started on 2 nos. ISU with 70% load at 12:18 pm. We Informed to ABB Service Engineer.
Malwa | May | Inverter 34 | DC CB ON failure | 1319.28 | 44689 | 0.36458 | 44689 | 0.43403 | 1.6667 | Inv - 34 tripped due to DC CB ON failure | 1.49 | 0.66893 | 1314.9262 | checked & rectified
Malwa | May | Inverter 38 | 100V DC failure | 3969.1 | 44689 | 0.57778 | 44689 | 0.58194 | 0.1 | Inv - 38,39 & 40 tripped due to 100V DC Failure | 0.074 | 0.66893 | 196.4725 | checked & rectified
Malwa | May | Inverter 37 | 100V DC failure | 1321.2 | 44689 | 0.57778 | 44689 | 0.5875 | 0.23333 | Inv - 37 tripped due to 100V DC Failure | 0.222 | 0.66893 | 196.2003 | checked & rectified
Malwa | May | Inverter 12 | Inv curtailed | 397.14 | 44689 | 0.38681 | 44689 | 0.63333 | 5.9167 | Inv - 12 Running on 2 nos. ISU with 70% Load | 3.6 | 0.66893 | 956.3663
Malwa | May | Inverter 12 | Inv curtailed | 397.14 | 44690 | 0.38333 | 44690 | 0.64028 | 6.1667 | Inv - 12 Running on 2 nos. ISU with 70% Load | 3.62 | 0.68107 | 979.1331
Malwa | May | Inverter 07 | GND CLOSE ERROR | 1331.88 | 44690 | 0.28611 | 44690 | 0.31042 | 0.58333 | Inv - 7 tripped due to GND CLOSE ERROR failure | 0.0878 | 0.68107 | 79.6433 | checked & rectified
Malwa | May | SCB.07.08 | String fault | 18 | 44690 | 0.31042 | 44690 | 0.47917 | 4.05 | 3 string Faulty | 2.64 | 0.68107 | 32.3643 | checked & rectified
Malwa | May | Inverter 12 | Inv curtailed | 397.14 | 44692 | 0.39722 | 44692 | 0.64722 | 6 | Inv - 12 Running on 2 nos. ISU with 70% Load | 3.97 | 0.67341 | 1061.7299
Malwa | May | SCB.32.07 | String fault | 18 | 44693 | 0.25 | 44693 | 0.45833 | 5 | Total - 3 nos. String Faulty | 2.23 | 0.67215 | 26.9802 | checked & rectified
Malwa | May | Inverter 17 | 100V DC failure | 1307.52 | 44694 | 0.35764 | 44694 | 0.37847 | 0.5 | Inv - 17 tripped due to 100V DC Failure | 0.3 | 0.67119 | 263.2771 | checked & rectified
Malwa | May | Inverter 18 | 100V DC failure | 3969 | 44694 | 0.35764 | 44694 | 0.36806 | 0.25 | Inv - 18,19&20 tripped due to 100V DC Failure | 0.161 | 0.67119 | 428.8945 | checked & rectified
Malwa | May | SCB.26.01 | String fault | 30 | 44696 | 0.25 | 44696 | 0.47917 | 5.5 | Total - 5 nos. String Faulty | 2.8 | 0.68457 | 57.5039 | checked & rectified
Malwa | May | Inverter 34 | DC CB ON failure | 1319.28 | 44697 | 0.48264 | 44697 | 0.49306 | 0.25 | Inv - 34 tripped due to DC CB ON failure | 0.33 | 0.67885 | 295.5469 | checked & rectified
Malwa | May | Inverter 36 | DC CB ON failure | 1325.52 | 44697 | 0.48264 | 44697 | 0.48958 | 0.16667 | Inv - 36 tripped due to DC CB ON failure | 0.25 | 0.67885 | 224.9582 | checked & rectified
Malwa | May | Inverter 05 | Ground fault | 1325.4 | 44698 | 0.33472 | 44698 | 0.33819 | 0.083333 | Inv-05 tripped due to GND leak current | 0.063 | 0.68147 | 56.9032 | checked & rectified
Malwa | May | SCB.01.07 | String fault | 36 | 44699 | 0.25 | 44699 | 0.47917 | 5.5 | Total - 6 nos. String Faulty | 2.694 | 0.67757 | 65.7135
Malwa | May | Inverter 21 | 100V DC failure | 5297.4 | 44699 | 0.73611 | 44699 | 0.73958 | 0.083333 | Inv no-21,22,23&24 tripped due to 100v Dc Failure | 0.021 | 0.67757 | 75.3766 | checked & rectified
Malwa | May | SCB.29.05 | String fault | 18 | 44701 | 0.25 | 44701 | 0.45833 | 5 | Total - 3 nos. String Faulty | 2.23 | 0.67732 | 27.1878
Malwa | May | Inverter 26 | AC CB ON failure | 1321.2 | 44702 | 0.625 | 44702 | 0.63264 | 0.18333 | Inv - 26 tripped due to AC CB ON failure | 0.173 | 0.69815 | 159.5735
Malwa | May | SCB.11.02 | String fault | 18 | 44702 | 0.25 | 44702 | 0.45833 | 5 | Total - 3 nos. String Faulty | 2.44 | 0.69815 | 30.6626
Malwa | May | Inverter 05 | Charging failure | 1325.4 | 44704 | 0.25 | 44704 | 0.28611 | 0.86667 | Inv - 5 tripped due to Charging Failure | 0.0633 | 0.69991 | 58.7207 | checked & rectified
Malwa | May | Inverter 08 | GND LEAK CUR | 1328.04 | 44704 | 0.33403 | 44704 | 0.33958 | 0.13333 | Inv - 8 tripped due to GND LEAK CUR | 0.0535 | 0.69991 | 49.7285 | checked & rectified
Malwa | May | Inverter 13 | Ground fault | 1335.96 | 44705 | 0.27917 | 44705 | 0.32361 | 1.0667 | Inv - 13 tripped due to Ground Fault | 0.2 | 0.71874 | 192.0424 | checked & rectified
Malwa | May | SCB.20.06 | String fault | 38 | 44705 | 0.32917 | 44705 | 0.47917 | 3.6 | Total - 5 String Faulty | 2.3 | 0.71874 | 62.8182 | checked & rectified
Malwa | May | Inverter 19 | Temp. fault | 1324.32 | 44705 | 0.47917 | 44705 | 0.48472 | 0.13333 | Inv - 19 tripped due to Temp. Fault | 0.0723 | 0.71874 | 68.8185 | checked & rectified
Malwa | May | SCB.10.02 | String fault | 6 | 44706 | 0.25 | 44706 | 0.47917 | 5.5 | Total - 1 String Faulty | 2.5 | 0.70944 | 10.6417 | checked & rectified
Malwa | May | SCB.30.01 | String fault | 18 | 44707 | 0.25 | 44707 | 0.45833 | 5 | Total - 3 String Faulty | 2.245 | 0.69817 | 28.2131 | checked & rectified
Malwa | May | Inverter 18 | GND LEAK CUR | 1319.16 | 44707 | 0.32986 | 44707 | 0.33333 | 0.083333 | Inv - 18 tripped due to GND LEAK CUR | 0.027 | 0.69817 | 24.867 | checked & rectified
Malwa | May | Inverter 25 | Ground fault | 1334.4 | 44711 | 0.63542 | 44711 | 0.64236 | 0.16667 | Inv - 25 tripped due to DC Earth Fault | 0.155 | 0.69209 | 143.1455 | checked & rectified
Malwa | June | Inverter 08 | INT CONFIG fault | 1328.04 | 44716 | 0.50347 | 44716 | 0.51042 | 0.16667 | Inv - 8 tripped due to INT CONFIG (5410) | 0.156 | 0.68218 | 141.3305 | checked & rectified
Malwa | June | Inverter 09 | GND LEAK CUR | 1329 | 44716 | 0.66944 | 44716 | 0.67292 | 0.083333 | Inv - 9 tripped due to GND LEAK CUR | 0.0444 | 0.68218 | 40.2539 | checked & rectified
Malwa | June | Inverter 04 | GND LEAK CUR | 1332.36 | 44718 | 0.40278 | 44718 | 0.40625 | 0.083333 | Inv - 4 tripped due to GND LEAK CUR | 0.05855 | 0.68679 | 53.5759 | checked & rectified
Malwa | June | Inverter 01 | Short circuit fault | 1313.4 | 44719 | 0.71806 | 44719 | 0.73542 | 0.41667 | Inv - 1 tripped due to SC CKT Fault | 0.06938 | 0.68876 | 62.7627 | checked & rectified
Malwa | June | Inverter 08 | AIR temp. failure | 1328.04 | 44720 | 0.53472 | 44720 | 0.54653 | 0.28333 | Inv - 8 tripped due to AIR Temp. failure | 0.311 | 0.69531 | 287.1776 | checked & rectified
Malwa | June | SCB.30.01 | String fault | 18 | 44720 | 0.25 | 44720 | 0.45833 | 5 | Total - 3 nos. String Faulty | 1.964 | 0.69531 | 24.5806 | checked & rectified
Malwa | June | Inverter 34 | IGBT stack faulty | 1319.28 | 44723 | 0.54514 | 44723 | 0.65278 | 2.5833 | Inv - 34 tripped due to Inverter Fuse failure | 1.52 | 0.69029 | 1384.2357 | after checking found IGBT Stack faulty in W-1 phase than Replaced faulty IGBT stack & Inverter started.
Malwa | June | Inverter 01 | Short circuit fault | 1313.4 | 44723 | 0.26875 | 44723 | 0.27917 | 0.25 | Inv - 1 tripped due to SC CKT Fault | 0.025 | 0.69029 | 22.6656
Malwa | June | Inverter 31 | Overcurrent restart lock | 1332 | 44724 | 0.28125 | 44724 | 0.29167 | 0.25 | Inv - 11 tripped due to Overcurrent Restart Lock | 0.017 | 0.7484 | 16.9468 | checked & rectified
Malwa | June | Inverter 08 | GND CLOSE ERROR | 1328.04 | 44725 | 0.61667 | 44725 | 0.62014 | 0.083333 | Inv 8 tripped due to GND CLOSE ERROR | 0.0126 | 0.71342 | 11.9378 | checked & rectified
Malwa | June | SCB.33.07 | String fault | 24 | 44725 | 0.25 | 44725 | 0.45833 | 5 | Total - 4 nos. String Faulty | 1.8 | 0.71342 | 30.8196 | checked & rectified
Malwa | June | SCB.05.10 | String fault | 24 | 44726 | 0.25 | 44726 | 0.40069 | 3.6167 | SCB 2110, String no. 7,8,9,10 Manually Open for new module Installation. String open as per instruct by VG Project Team | 1.17 | 0.70172 | 19.7044 | checked & rectified
Malwa | June | Inverter 19 | GND LEAK CUR | 1324.32 | 44727 | 0.46111 | 44727 | 0.46458 | 0.083333 | Inv - 19 tripped due to GND LEAK CUR (8197) | 0.0743 | 0.70825 | 69.6897 | checked & rectified
Malwa | June | Inverter 16 | Short circuit fault | 1325.88 | 44728 | 0.25486 | 44728 | 0.33819 | 2 | Inv - 16 tripped due to SC CKT Fault | 0.2834 | 0.71136 | 267.2952 | checked & rectified
Malwa | June | Inverter 21 | 100V DC failure | 5297.4 | 44728 | 0.44444 | 44728 | 0.45139 | 0.16667 | Inv - 1 to 4 tripped due to 100V DC Failure | 0.229 | 0.71136 | 862.9493 | checked & rectified
Malwa | June | Inverter 23 | Overcurrent restart lock | 1320 | 44729 | 0.60069 | 44729 | 0.60208 | 0.033333 | Inv - 23 tripped due to Overcurrent Restart Lock | 0.043 | 0.71961 | 40.8448 | checked & rectified
Malwa | June | Inverter 32 | DC CB ON failure | 1328.16 | 44730 | 0.3625 | 44730 | 0.36597 | 0.083333 | Inv - 12 tripped due to DC CB ON failure | 0.0453 | 0.70482 | 42.4059 | checked & rectified
Malwa | June | SCB.26.10 | String fault | 18 | 44731 | 0.25 | 44731 | 0.45833 | 5 | Total - 3 nos. String Faulty | 1.126 | 0.7287 | 14.7693 | checked & rectified
Malwa | June | Inverter 07 | GND LEAK CUR | 1331.88 | 44733 | 0.25139 | 44733 | 0.27222 | 0.5 | Inv - 7 tripped due to GND LEAK CUR (8197) | 0.026 | 0.71078 | 24.6134 | checked & rectified
Malwa | June | Inverter 13 | GND LEAK CUR | 1335.96 | 44733 | 0.25139 | 44733 | 0.27569 | 0.58333 | Inv - 13 tripped due to GND LEAK CUR (8197) | 0.032 | 0.71078 | 30.3862 | checked & rectified
Malwa | June | Inverter 20 | GND LEAK CUR | 1325.52 | 44733 | 0.25139 | 44733 | 0.27569 | 0.58333 | Inv - 20 tripped due to GND LEAK CUR (8197) | 0.032 | 0.71078 | 30.1488 | checked & rectified
Malwa | June | Inverter 17 | GND LEAK CUR | 1307.52 | 44733 | 0.69931 | 44733 | 0.70972 | 0.25 | Inv - 17 tripped due to GND LEAK CUR (8197) | 0.038 | 0.71078 | 35.3155 | checked & rectified
Malwa | June | Inverter 08 | GND LEAK CUR | 1328.04 | 44733 | 0.70278 | 44733 | 0.71319 | 0.25 | Inv - 8 tripped due to GND LEAK CUR (8197) | 0.036 | 0.71078 | 33.9819 | checked & rectified
Malwa | June | Inverter 25 | Negative fuse failure | 1334.4 | 44733 | 0.25 | 44733 | 0.28819 | 0.91667 | Inv - 25 tripped due to Negative Fuse Failure | 0.0602 | 0.71078 | 57.0974 | checked & rectified
Malwa | June | SCB.12.02 | String fault | 12 | 44733 | 0.25 | 44733 | 0.44931 | 4.7833 | Total - 2 nos. String Faulty | 1.8144 | 0.71078 | 15.4756 | checked & rectified
Malwa | June | Inverter 05 | TEMP DIF 2 V fault | 1325.4 | 44733 | 0.41111 | 44733 | 0.46319 | 1.25 | Inv - 5 tripped due to TEMP DIF 2 V (44B5) | 0.9 | 0.71078 | 847.858 | after checking found AFIN card not working. So we replaced AFIN card & fault resolved
Malwa | June | SCB.15.04 | String fault | 24 | 44734 | 0.25 | 44734 | 0.48056 | 5.5333 | Total - 4 nos. String Faulty | 2.6 | 0.72388 | 45.1701 | checked & rectified
Malwa | June | SCB.23.06 | String fault | 30 | 44735 | 0.25 | 44735 | 0.49097 | 5.7833 | Total - 5 nos. String Faulty | 2.5 | 0.72533 | 54.3998 | checked & rectified
Malwa | June | SCB.07.06 | String fault | 12 | 44736 | 0.25 | 44736 | 0.43889 | 4.5333 | Total - 2 nos. String Faulty | 1.42 | 0.72862 | 12.4156 | checked & rectified
Malwa | June | Inverter 16 | GND LEAK CUR | 1325.88 | 44736 | 0.33125 | 44736 | 0.33333 | 0.05 | Inv - 16 tripped due to GND LEAK CUR (8197) | 0.02424 | 0.72862 | 23.4172 | checked & rectified
Malwa | June | Inverter 11 | GND LEAK CUR | 1327.08 | 44736 | 0.45417 | 44736 | 0.45694 | 0.066667 | Inv - 11 tripped due to GND LEAK CUR (8197) | 0.07 | 0.72862 | 67.6852 | checked & rectified
Malwa | June | Inverter 32 | Overcurrent restart lock | 1328.16 | 44737 | 0.34375 | 44737 | 0.36111 | 0.41667 | Inv - 32 tripped due to Overcurrent Restart Lock | 0.206 | 0.71944 | 196.8386 | checked & rectified
Malwa | June | Inverter 07 | INT CONFIG fault | 1331.88 | 44737 | 0.62986 | 44737 | 0.63681 | 0.16667 | Inv - 7 tripped due to INT CONFIG (5410) | 0.219 | 0.71944 | 209.8466 | checked & rectified
Malwa | June | SCB.16.02 | String fault | 18 | 44737 | 0.25 | 44737 | 0.47917 | 5.5 | Total - 3 nos. String Faulty | 2.52 | 0.71944 | 32.6337 | checked & rectified
Malwa | June | SCB.12.02 | String fault | 12 | 44740 | 0.25 | 44740 | 0.44792 | 4.75 | Total - 2 nos. String Faulty | 1.823 | 0.72799 | 15.9254 | checked & rectified
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44743 | 0.42153 | 44743 | 0.425 | 0.083333 | Inv - 10 tripped due to GND LEAK CUR (8197) | 0.144 | 0.74354 | 142.5536 | checked & rectified
Malwa | July | Inverter 11 | GND LEAK CUR | 1327.08 | 44743 | 0.42153 | 44743 | 0.425 | 0.083333 | Inv - 11 tripped due to GND LEAK CUR (8197) | 0.144 | 0.74354 | 142.0911 | checked & rectified
Malwa | July | Inverter 30 | Negative fuse failure | 1329.84 | 44743 | 0.54514 | 44743 | 0.54861 | 0.083333 | Inv - 30 tripped due to Negative Fuse Failure | 0.06 | 0.74354 | 59.3277 | checked & rectified
Malwa | July | Inverter 12 | GND LEAK CUR | 1323.84 | 44744 | 0.46111 | 44744 | 0.46458 | 0.083333 | Inv - 12 tripped due to GND LEAK CUR (8197) | 0.0363 | 0.74161 | 35.6386 | checked & rectified
Malwa | July | Inverter 30 | DC CB ON failure | 1329.84 | 44744 | 0.51528 | 44744 | 0.51875 | 0.083333 | Inv - 30 tripped due to DC CB ON failure | 0.0424 | 0.74161 | 41.8161 | checked & rectified
Malwa | July | Inverter 31 | Negative fuse failure | 1332 | 44745 | 0.25 | 44745 | 0.26944 | 0.46667 | Inv - 31 tripped due to Negative Fuse Failure | 0.02 | 0.72938 | 19.4308 | checked & rectified
Malwa | July | Inverter 12 | GND LEAK CUR | 1323.84 | 44745 | 0.29236 | 44745 | 0.29861 | 0.15 | Inv - 12 tripped due to GND LEAK CUR (8197) | 0.023 | 0.72938 | 22.2085 | checked & rectified
Malwa | July | Inverter 30 | IGBT SAT Trip | 1329.84 | 44745 | 0.47222 | 44745 | 0.5 | 0.66667 | Inv - 30 tripped 4-5 times on IGBT SAT TRIP in W1- Phase | 0.72 | 0.72938 | 698.3739 | We will checking tonight.
Malwa | July | Inverter 08 | Short circuit fault | 1328.04 | 44745 | 0.66736 | 44745 | 0.67361 | 0.15 | Inv - 8 tripped due to SC CKT Fault | 0.011 | 0.72938 | 10.6552 | checked & rectified
Malwa | July | Inverter 11 | GND LEAK CUR | 1327.08 | 44746 | 0.31389 | 44746 | 0.33125 | 0.41667 | Inv - 11 tripped due to GND LEAK CUR (8197) | 0.0631 | 0.72313 | 60.5538 | checked & rectified
Malwa | July | Inverter 17 | GND LEAK CUR | 1307.52 | 44746 | 0.27222 | 44746 | 0.32778 | 1.3333 | Inv - 17 tripped due to GND LEAK CUR (8197) | 0.08 | 0.72313 | 75.6403 | checked & rectified
Malwa | July | Inverter 12 | Ground fault | 1323.84 | 44746 | 0.44236 | 44746 | 0.45278 | 0.25 | Inv - 12 tripped due to DI4 fault | 0.144 | 0.72313 | 137.852 | checked & rectified
Malwa | July | Inverter 01 | MAIN CNT FLT | 1313.4 | 44746 | 0.55694 | 44746 | 0.62986 | 1.75 | Inv - 1 tripped due to MAIN CNT FLT | 1.374 | 0.72313 | 1304.9648 | checked & rectified
Malwa | July | Inverter 33 | DC Output Detection fault | 1332.72 | 44746 | 0.28819 | 44746 | 0.32986 | 1 | Inv - 33 tripped due to DC Output Detection fault | 0.075 | 0.72313 | 72.2795 | checked & rectified
Malwa | July | Inverter 30 | IGBT SAT Trip | 1329.84 | 44746 | 0.38542 | 44746 | 0.38889 | 0.083333 | Inv - 30 tripped due to IGBT SAT TRIP in W2- Phase | 0.058 | 0.72313 | 55.7754 | checked & rectified
Malwa | July | Inverter 31 | IGBT SAT Trip | 1332 | 44746 | 0.53819 | 44746 | 0.54514 | 0.16667 | Inv - 31 tripped times on IGBT SAT TRIP in V2- Phase | 0.198 | 0.72313 | 190.7148 | checked & rectified
Malwa | July | Inverter 21 | DC CB ON failure | 1325.88 | 44746 | 0.6125 | 44746 | 0.61597 | 0.083333 | Inv - 21 tripped due to DC CB ON failure | 0.031 | 0.72313 | 29.7222 | checked & rectified
Malwa | July | Inverter 01 | Ground fault | 1313.4 | 44747 | 0.39722 | 44747 | 0.40417 | 0.16667 | Inv - 1 tripped due to DI4 fault | 0.39 | 0.73666 | 377.3386 | checked & rectified
Malwa | July | Inverter 20 | GND LEAK CUR | 1325.52 | 44747 | 0.58125 | 44747 | 0.60556 | 0.58333 | Inv - 20 tripped due to GND LEAK CUR (8197) | 0.0383 | 0.73666 | 37.3985 | checked & rectified
Malwa | July | Inverter 17 | Ground fault | 1307.52 | 44747 | 0.6125 | 44747 | 0.64375 | 0.75 | Inv - 17 tripped due to DI4 fault | 0.12 | 0.73666 | 115.5844 | checked & rectified
Malwa | July | Inverter 12 | GND LEAK CUR | 1323.84 | 44747 | 0.68889 | 44747 | 0.70625 | 0.41667 | Inv - 12 tripped due to GND LEAK CUR (8197) | 0.0841 | 0.73666 | 82.0165 | checked & rectified
Malwa | July | Inverter 21 | IGBT SAT Trip | 1325.88 | 44747 | 0.68542 | 44747 | 0.68889 | 0.083333 | Inv - 21 tripped due to IGBT SAT TRIP in W2- Phase | 0.0286 | 0.73666 | 27.9344 | checked & rectified
Malwa | July | SCB.01.05 | String fault | 54 | 44748 | 0.27222 | 44748 | 0.54306 | 6.5 | Total - 9 nos. String Faulty | 3.21 | 0.70842 | 122.7974 | checked & rectified
Malwa | July | Inverter 25 | Negative fuse failure | 1334.4 | 44748 | 0.26042 | 44748 | 0.3125 | 1.25 | Inv - 25 tripped due to Negative Fuse Failure | 0.4 | 0.70842 | 378.126 | checked & rectified
Malwa | July | Inverter 34 | Negative fuse failure | 1319.28 | 44748 | 0.26042 | 44748 | 0.29514 | 0.83333 | Inv - 34 tripped due to Negative Fuse Failure | 0.14 | 0.70842 | 130.8445 | checked & rectified
Malwa | July | Inverter 01 | Ground fault | 1313.4 | 44748 | 0.31389 | 44748 | 0.32083 | 0.16667 | Inv - 1 tripped due to DI4 fault | 0.17 | 0.70842 | 158.1745 | checked & rectified
Malwa | July | Inverter 11 | Ground fault | 1327.08 | 44748 | 0.38333 | 44748 | 0.39028 | 0.16667 | Inv - 11 tripped due to DI4 fault | 0.14 | 0.70842 | 131.6181 | checked & rectified
Malwa | July | Inverter 13 | Ground fault | 1335.96 | 44748 | 0.45139 | 44748 | 0.45486 | 0.083333 | Inv - 13 tripped due to DI4 fault | 0.0256 | 0.70842 | 24.2284 | checked & rectified
Malwa | July | Inverter 03 | Ground fault | 1323.6 | 44748 | 0.45625 | 44748 | 0.46667 | 0.25 | Inv - 3 tripped due to DC GND FLT | 0.56 | 0.70842 | 525.0919 | checked & rectified
Malwa | July | SCB.02.10 | String fault | 24 | 44749 | 0.27222 | 44749 | 0.45972 | 4.5 | Total - 4 nos. String Faulty | 0.504 | 0.7589 | 9.1797 | checked & rectified
Malwa | July | Inverter 01 | GND LEAK CUR | 1313.4 | 44749 | 0.34167 | 44749 | 0.35556 | 0.33333 | Inv - 1 tripped due to GND LEAK CUR (8197) | 0.0168 | 0.7589 | 16.7453 | checked & rectified
Malwa | July | Inverter 11 | GND LEAK CUR | 1327.08 | 44749 | 0.37292 | 44749 | 0.37986 | 0.16667 | Inv - 11 tripped due to GND LEAK CUR (8197) | 0.0193 | 0.7589 | 19.4375 | checked & rectified
Malwa | July | Inverter 21 | IGBT SAT Trip | 1325.88 | 44749 | 0.39931 | 44749 | 0.40972 | 0.25 | Inv - 21 tripped due to IGBT SAT TRIP in Y2- Phase | 0.0485 | 0.7589 | 48.8014 | checked & rectified
Malwa | July | SCB.01.10 | String fault | 60 | 44750 | 0.26528 | 44750 | 0.52222 | 6.1667 | Total - 10 nos. String Faulty | 2.08 | 0.74636 | 93.1455 | checked & rectified
Malwa | July | Inverter 25 | Ground fault | 1334.4 | 44750 | 0.28125 | 44750 | 0.30208 | 0.5 | Inv - 25 tripped due to Earth Fault | 0.03 | 0.74636 | 29.8782 | checked & rectified
Malwa | July | Inverter 33 | DC Output Detection fault | 1332.72 | 44750 | 0.42361 | 44750 | 0.42708 | 0.083333 | Inv - 33 tripped due to DC Output Detection fault | 0.06 | 0.74636 | 59.6812 | checked & rectified
Malwa | July | Inverter 01 | GND LEAK CUR | 1313.4 | 44750 | 0.47361 | 44750 | 0.47708 | 0.083333 | Inv - 1 tripped due to GND LEAK CUR (8197) | 0.08 | 0.74636 | 78.4213 | checked & rectified
Malwa | July | SCB.15.06 | String fault | 24 | 44751 | 0.28264 | 44751 | 0.45972 | 4.25 | Total - 4 nos. String Faulty | 0.602 | 0.76162 | 11.0039 | checked & rectified
Malwa | July | Inverter 30 | DC CB ON failure | 1329.84 | 44751 | 0.62639 | 44751 | 0.63056 | 0.1 | Inv - 30 tripped due to DC CB ON failure | 0.037 | 0.76162 | 37.4748 | checked & rectified
Malwa | July | SCB.02.05 | String fault | 12 | 44752 | 0.33472 | 44752 | 0.44931 | 2.75 | Total - 2 nos. String Faulty | 0.86 | 0.75187 | 7.7593 | checked & rectified
Malwa | July | Inverter 18 | GND LEAK CUR | 1319.16 | 44752 | 0.33472 | 44752 | 0.35208 | 0.41667 | Inv - 18 tripped due to GND LEAK CUR (8197) | 0.031 | 0.75187 | 30.7471 | checked & rectified
Malwa | July | Inverter 24 | Ground fault | 1324.56 | 44752 | 0.33681 | 44752 | 0.35417 | 0.41667 | Inv - 24 Tripped Due to DC Earth Fault | 0.0342 | 0.75187 | 34.0599 | checked & rectified
Malwa | July | Inverter 23 | Ground fault | 1320 | 44752 | 0.33681 | 44752 | 0.38889 | 1.25 | Inv - 23 Tripped Due to DC Earth Fault | 0.43 | 0.75187 | 426.764 | checked & rectified
Malwa | July | Inverter 19 | GND LEAK CUR | 1324.32 | 44752 | 0.37292 | 44752 | 0.42153 | 1.1667 | Inv - 19 tripped due to GND LEAK CUR (8197) | 0.51 | 0.75187 | 507.8185 | checked & rectified
Malwa | July | Inverter 02 | Ground fault | 1331.4 | 44752 | 0.49792 | 44752 | 0.53681 | 0.93333 | Inv - 02 tripped due to DI4 fault | 0.61 | 0.75187 | 610.6379 | checked & rectified
Malwa | July | Inverter 03 | GND LEAK CUR | 1323.6 | 44752 | 0.53264 | 44752 | 0.53611 | 0.083333 | Inv - 3 tripped due to GND LEAK CUR (8197) | 0.06 | 0.75187 | 59.7109 | checked & rectified
Malwa | July | SCB.18.09 | String fault | 60 | 44753 | 0.27917 | 44753 | 0.53958 | 6.25 | Total - 10 nos. String Faulty | 1.762 | 0.7766 | 82.1019 | checked & rectified
Malwa | July | Inverter 30 | IGBT SAT Trip | 1329.84 | 44753 | 0.48264 | 44753 | 0.50347 | 0.5 | Inv - 30 tripped due to IGBT SAT TRIP in W2- Phase | 0.29 | 0.7766 | 299.4977 | We will checking tonight.
Malwa | July | Inverter 22 | DC CB ON failure | 1329.84 | 44754 | 0.47917 | 44754 | 0.48264 | 0.083333 | Inv - 22 tripped due to DCCB ON Failure | 0.17 | 0.71458 | 161.547 | We will checking tonight.
Malwa | July | Inverter 30 | IGBT SAT Trip | 1329.84 | 44754 | 0.375 | 44754 | 0.38542 | 0.25 | Inv - 30 tripped due to IGBT SAT TRIP in V1- Phase | 0.144 | 0.71458 | 136.8398 | We will checking tonight.
Malwa | July | Inverter 34 | DC Output Detection fault | 1329.84 | 44754 | 0.48264 | 44754 | 0.52431 | 1 | Inv - 34 tripped due to DC Output Detection fault | 0.456 | 0.71458 | 433.3262 | We will checking tonight.
Malwa | July | Inverter 02 | Ground fault | 1331.4 | 44755 | 0.45694 | 44755 | 0.48125 | 0.58333 | Inv - 2 tripped due to DI4 Fault | 0.295 | 0.70256 | 275.9386 | checked & rectified
Malwa | July | Inverter 03 | Ground fault | 1323.6 | 44755 | 0.40486 | 44755 | 0.42917 | 0.58333 | Inv - 3 tripped due to DI4 Fault | 0.026 | 0.70256 | 24.1775 | checked & rectified
Malwa | July | Inverter 04 | Ground fault | 1332.36 | 44755 | 0.40486 | 44755 | 0.46042 | 1.3333 | Inv - 4 tripped due to DI4 Fault | 0.173 | 0.70256 | 161.9383 | checked & rectified
Malwa | July | Inverter 06 | Ground fault | 1325.52 | 44755 | 0.40486 | 44755 | 0.43958 | 0.83333 | Inv - 6 tripped due to DI4 Fault | 0.038 | 0.70256 | 35.3877 | checked & rectified
Malwa | July | Inverter 08 | Ground fault | 1328.04 | 44755 | 0.40486 | 44755 | 0.44653 | 1 | Inv - 8 tripped due to DI4 Fault | 0.064 | 0.70256 | 59.7136 | checked & rectified
Malwa | July | Inverter 13 | GND LEAK CUR | 1335.96 | 44755 | 0.47639 | 44755 | 0.47986 | 0.083333 | Inv - 13 tripped due GND LEAK CUR (8197) | 0.046 | 0.70256 | 43.1751 | checked & rectified
Malwa | July | Inverter 14 | Ground fault | 1322.52 | 44755 | 0.40486 | 44755 | 0.44653 | 1 | Inv - 14 tripped due to DI4 Fault | 0.064 | 0.70256 | 59.4654 | checked & rectified
Malwa | July | Inverter 15 | Ground fault | 1321.8 | 44755 | 0.40486 | 44755 | 0.45347 | 1.1667 | Inv - 15 tripped due to DI4 Fault | 0.0975 | 0.70256 | 90.5425 | checked & rectified
Malwa | July | Inverter 17 | Ground fault | 1307.52 | 44755 | 0.40486 | 44755 | 0.47778 | 1.75 | Inv - 17 tripped due to DI4 Fault | 0.41 | 0.70256 | 376.6293 | checked & rectified
Malwa | July | Inverter 19 | Ground fault | 1324.32 | 44755 | 0.40486 | 44755 | 0.48472 | 1.9167 | Inv - 19 tripped due to DI4 Fault | 0.78 | 0.70256 | 725.7206 | checked & rectified
Malwa | July | Inverter 22 | IGBT SAT Trip | 1326.96 | 44755 | 0.60903 | 44755 | 0.61319 | 0.1 | Inv - 22 tripped due to IGBT SAT Trip | 0.05 | 0.70256 | 46.6133 | checked & rectified
Malwa | July | Inverter 24 | Ground fault | 1324.56 | 44755 | 0.41319 | 44755 | 0.43403 | 0.5 | Inv - 24 Tripped Due to DC Earth Fault | 0.026 | 0.70256 | 24.1951 | checked & rectified
Malwa | July | Inverter 29 | Ground fault | 1333.08 | 44755 | 0.41319 | 44755 | 0.47917 | 1.5833 | Inv - 29 Tripped Due to DC Earth Fault | 0.43 | 0.70256 | 402.7231 | checked & rectified
Malwa | July | Inverter 33 | Overcurrent restart lock | 1332.72 | 44755 | 0.41319 | 44755 | 0.46181 | 1.1667 | Inv - 33 tripped due to Overcurrent Restart Lock | 0.183 | 0.70256 | 171.3452 | checked & rectified
Malwa | July | Inverter 36 | DC Output Detection fault | 1325.52 | 44755 | 0.50694 | 44755 | 0.51042 | 0.083333 | Inv - 36 tripped due to DC Output Detection fault | 0.1 | 0.70256 | 93.1254 | checked & rectified
Malwa | July | Inverter 40 | Negative fuse failure | 1324.44 | 44755 | 0.41319 | 44755 | 0.46181 | 1.1667 | Inv - 40 tripped due to Negative Fuse Failure | 0.183 | 0.70256 | 170.2807 | checked & rectified
Malwa | July | All Inverters | Overcurrent fault | 26491 | 44756 | 0.48681 | 44756 | 0.64583 | 3.8167 | P1, 33kv Outgoing & Incomer -1 feeder tripped due to Overcurrent Fault | 2.56 | 0.72709 | 49308.9779 | According to fault, Taken immediately action & one by one checked all necessary process. Now P1, LCR - 1, TR-2 Under breakdown & Rctification WIP.
Malwa | July | IDT 02 | Overcurrent fault | 2656 | 44756 | 0.64583 | 44756 | 0.78403 | 3.3167 | P1, LCR - 1, TR-2 tripped due to Overcurrent Fault | 0.83 | 0.72709 | 1602.8536 | Rectification WIP.
Malwa | July | Inverter 05 | Ground fault | 1325.4 | 44756 | 0.27083 | 44756 | 0.35417 | 2 | Inv - 5 tripped due to DI4 fault | 0.32 | 0.72709 | 308.3789 | checked & rectified
Malwa | July | Inverter 31 | Overcurrent fault | 1332 | 44756 | 0.51389 | 44756 | 0.54514 | 0.75 | Inv - 11 tripped due to Overcurrent, IGBT SAT Trip & Inverter Fan failure | 0.7714 | 0.72709 | 747.0876 | checked & rectified
Malwa | July | IDT 02 | Overcurrent fault | 2656 | 44757 | 0.25 | 44757 | 0.79167 | 13 | P1, LCR - 1, TR-2 tripped due to Overcurrent Fault | 3.27 | 0.66962 | 5815.7715 | Rectification done & transformer chearged on 6:30 pm.
Malwa | July | Inverter 31 | IGBT SAT Trip | 1332 | 44757 | 0.52778 | 44757 | 0.57292 | 1.0833 | Inv - 11 tripped due to IGBT SAT Trip, Inverter Fan failure & DC Earth fault | 0.71 | 0.66962 | 633.2775 | checked & rectified
Malwa | July | Inverter 09 | Ground fault | 1329 | 44757 | 0.71667 | 44757 | 0.77569 | 1.4167 | Inv - 9 tripped due to DI4 fault | 0.14 | 0.66962 | 124.5904 | checked & rectified
Malwa | July | Inverter 07 | Short circuit fault | 1331.88 | 44757 | 0.72361 | 44757 | 0.77222 | 1.1667 | Inv - 7 tripped due to SC CKT Fault | 0.12 | 0.66962 | 107.0232 | checked & rectified
Malwa | July | Inverter 31 | Ground fault | 1332 | 44758 | 0.26736 | 44758 | 0.30903 | 1 | Inverter 31 tripped due to DC Earth Fault | 0.07 | 0.7073 | 65.9486 | checked & rectified
Malwa | July | Inverter 30 | Ground fault | 1329.84 | 44758 | 0.26736 | 44758 | 0.32639 | 1.4167 | Inverter 30 tripped due to DC Earth Fault | 0.11 | 0.7073 | 103.4655 | checked & rectified
Malwa | July | Inverter 25 | Ground fault | 1334.4 | 44758 | 0.48611 | 44758 | 0.48958 | 0.083333 | Inverter 25 tripped due to DC Earth Fault | 0.1795 | 0.7073 | 169.4159 | checked & rectified
Malwa | July | Inverter 16 | Ground fault | 1325.88 | 44758 | 0.47361 | 44758 | 0.48403 | 0.25 | Inverter 16 tripped due to DI4 fault | 0.2688 | 0.7073 | 252.0792 | checked & rectified
Malwa | July | Inverter 15 | GND LEAK CUR | 1321.8 | 44758 | 0.53819 | 44758 | 0.54028 | 0.05 | Inverter 15 tripped due to GND LEAK CUR (8197) | 0.03552 | 0.7073 | 33.208 | checked & rectified
Malwa | July | Inverter 09 | GND LEAK CUR | 1329 | 44759 | 0.44514 | 44759 | 0.44861 | 0.083333 | Inverter 9 tripped due to GND LEAK CUR (8197) | 0.066 | 0.71074 | 62.3418 | checked & rectified
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44759 | 0.57222 | 44759 | 0.57569 | 0.083333 | Inverter 10 tripped due to GND LEAK CUR (8197) | 0.068 | 0.71074 | 64.3469 | checked & rectified
Malwa | July | Inverter 19 | GND LEAK CUR | 1324.32 | 44759 | 0.60764 | 44759 | 0.61111 | 0.083333 | Inverter 19 tripped due to GND LEAK CUR (8197) | 0.053 | 0.71074 | 49.8861 | checked & rectified
Malwa | July | Inverter 23 | Ground fault | 1320 | 44759 | 0.26042 | 44759 | 0.34028 | 1.9167 | Inverter 23 tripped due to DC Earth Fault | 0.373 | 0.71074 | 349.9397 | checked & rectified
Malwa | July | Inverter 25 | Ground fault | 1334.4 | 44759 | 0.48958 | 44759 | 0.49306 | 0.083333 | Inverter 25 tripped due to DC Earth Fault | 0.107 | 0.71074 | 101.48 | checked & rectified
Malwa | July | Inverter 30 | Ground fault | 1329.84 | 44759 | 0.26042 | 44759 | 0.28819 | 0.66667 | Inverter 30 tripped due to DC Earth Fault | 0.049 | 0.71074 | 46.3133 | checked & rectified
Malwa | July | Inverter 22 | Temp. fault | 1326.96 | 44760 | 0.40972 | 44760 | 0.49306 | 2 | Inv - 22 tripped due to Temp. Failure of Fin for IGBT | 1.34 | 0.73276 | 1302.9452 | Inv started on 50% load on 11:55.
Malwa | July | Inverter 25 | Ground fault | 1334.4 | 44760 | 0.36111 | 44760 | 0.36458 | 0.083333 | Inverter 25 tripped due to DC Earth Fault | 0.0281 | 0.73276 | 27.4761 | checked & rectified
Malwa | July | Inverter 30 | Ground fault | 1329.84 | 44760 | 0.52083 | 44760 | 0.56597 | 1.0833 | Inverter 30 tripped due to DC Earth Fault | 0.1773 | 0.73276 | 172.7713 | checked & rectified
Malwa | July | Inverter 33 | Ground fault | 1332.72 | 44760 | 0.55208 | 44760 | 0.56806 | 0.38333 | Inverter 33 tripped due to DC Earth Fault | 0.2 | 0.73276 | 195.3136 | checked & rectified
Malwa | July | Inverter 03 | GND LEAK CUR | 1323.6 | 44760 | 0.54722 | 44760 | 0.56806 | 0.5 | Inverter 03 tripped due to GND LEAK CUR (8197) | 0.157 | 0.73276 | 152.272 | checked & rectified
Malwa | July | Inverter 04 | GND LEAK CUR | 1332.36 | 44760 | 0.54375 | 44760 | 0.56458 | 0.5 | Inverter 4 tripped due to GND LEAK CUR (8197) | 0.157 | 0.73276 | 153.2797 | checked & rectified
Malwa | July | Inverter 17 | GND LEAK CUR | 1307.52 | 44760 | 0.54375 | 44760 | 0.55764 | 0.33333 | Inverter 17 tripped due to GND LEAK CUR (8197) | 0.121 | 0.73276 | 115.9304 | checked & rectified
Malwa | July | Inverter 19 | GND LEAK CUR | 1324.32 | 44760 | 0.55208 | 44760 | 0.58333 | 0.75 | Inverter 19 tripped due to GND LEAK CUR (8197) | 0.3 | 0.73276 | 291.1238 | checked & rectified
Malwa | July | Inverter 05 | GND LEAK CUR | 1325.4 | 44761 | 0.26944 | 44761 | 0.30069 | 0.75 | Inverter 05 tripped due to GND LEAK CUR (8197) | 0.021 | 0.71206 | 19.8191 | checked & rectified
Malwa | July | Inverter 07 | GND LEAK CUR | 1331.88 | 44761 | 0.40139 | 44761 | 0.40486 | 0.083333 | Inverter 07 tripped due to GND LEAK CUR (8197) | 0.09 | 0.71206 | 85.3542 | checked & rectified
Malwa | July | Inverter 12 | GND LEAK CUR | 1323.84 | 44761 | 0.49514 | 44761 | 0.49861 | 0.083333 | Inverter 12 tripped due to GND LEAK CUR (8197) | 0.125 | 0.71206 | 117.8319 | checked & rectified
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44761 | 0.5625 | 44761 | 0.56597 | 0.083333 | Inverter 10 tripped due to GND LEAK CUR (8197) | 0.0335 | 0.71206 | 31.7593 | checked & rectified
Malwa | July | Inverter 39 | IGBT SAT Trip | 1324.08 | 44761 | 0.43056 | 44761 | 0.48264 | 1.25 | Inv - 39 Multiple times tripped due to IGBT SAT TRIP in U1- Phase | 0.87 | 0.71206 | 820.2586 | We will checking tonight.
Malwa | July | Inverter 34 | IGBT SAT Trip | 1319.28 | 44761 | 0.47917 | 44761 | 0.48264 | 0.083333 | Inv - 34 tripped due to IGBT SAT TRIP in W1- Phase | 0.1354 | 0.71206 | 127.1958 | checked & rectified
Malwa | July | SCB.02.04 | String fault | 39.95 | 44761 | 0.27083 | 44761 | 0.5 | 5.5 | Total - 5 nos. String Faulty | 1.7 | 0.71206 | 48.3596 | checked & rectified
Malwa | July | SCB.05.06 | String fault | 87.89 | 44762 | 0.27292 | 44762 | 0.62361 | 8.4167 | Total - 11 nos. String Faulty | 1.747 | 0.73281 | 112.5181 | checked & rectified
Malwa | July | Inverter 34 | IGBT SAT Trip | 1319.28 | 44762 | 0.59444 | 44762 | 0.59792 | 0.083333 | Inv - 34 tripped due to IGBT SAT TRIP in W1- Phase | 0.0231 | 0.73281 | 22.3326 | We will checking tonight.
Malwa | July | Inverter 07 | GND LEAK CUR | 1331.88 | 44763 | 0.45694 | 44763 | 0.46042 | 0.083333 | Inverter 7 tripped due to GND LEAK CUR (8197) | 0.0252 | 0.73485 | 24.6642 | checked & rectified
Malwa | July | Inverter 32 | IGBT SAT Trip | 1328.16 | 44763 | 0.51458 | 44763 | 0.51806 | 0.083333 | Inv - 32 tripped due to IGBT SAT TRIP in W1- Phase | 0.0582 | 0.73485 | 56.8034 | We will checking tonight.
Malwa | July | SCB.07.05 | String fault | 12 | 44764 | 0.2625 | 44764 | 0.43958 | 4.25 | Total - 2 nos. String Faulty | 0.782 | 0.71893 | 6.7464 | checked & rectified
Malwa | July | SCB.05.04 | String fault | 119.85 | 44765 | 0.26944 | 44765 | 0.54028 | 6.5 | Total - 15 nos. String Faulty | 1.573 | 0.74392 | 140.2474 | checked & rectified
Malwa | July | Inverter 21 | Ground fault | 1325.88 | 44765 | 0.27083 | 44765 | 0.30903 | 0.91667 | Inv - 21 tripped due to DC Earth Fault | 0.081 | 0.74392 | 79.8946 | checked & rectified
Malwa | July | Inverter 32 | DC CB ON failure | 1328.16 | 44765 | 0.44583 | 44765 | 0.44931 | 0.083333 | Inv - 32 tripped due to DC CB ON failure | 0.031 | 0.74392 | 30.6295 | checked & rectified
Malwa | July | Inverter 03 | GND LEAK CUR | 1323.6 | 44765 | 0.56111 | 44765 | 0.58194 | 0.5 | Inverter 3 tripped due to GND LEAK CUR (8197) | 0.0222 | 0.74392 | 21.8594 | checked & rectified
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44765 | 0.65 | 44765 | 0.65347 | 0.083333 | Inverter 10 tripped due to GND LEAK CUR (8197) | 0.01 | 0.74392 | 9.9046 | checked & rectified
Malwa | July | SCB.02.02 | String fault | 48 | 44766 | 0.29028 | 44766 | 0.49861 | 5 | Total - 8 nos. String Faulty | 1.414 | 0.74262 | 50.4032 | checked & rectified
Malwa | July | Inverter 07 | GND LEAK CUR | 1331.88 | 44766 | 0.46875 | 44766 | 0.47569 | 0.16667 | Inverter 7 tripped due to GND LEAK CUR (8197) | 0.12 | 0.74262 | 118.6899 | checked & rectified
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44766 | 0.48333 | 44766 | 0.48681 | 0.083333 | Inverter 10 tripped due to GND LEAK CUR (8197) | 0.06 | 0.74262 | 59.3236 | checked & rectified
Malwa | July | Inverter 32 | IGBT SAT Trip | 1328.16 | 44766 | 0.46528 | 44766 | 0.49306 | 0.66667 | Inv - 32 tripped due to IGBT SAT TRIP in V2- Phase | 0.71 | 0.74262 | 700.2874 | We will checking tonight.
Malwa | July | SCB.06.09 | String fault | 42 | 44767 | 0.30764 | 44767 | 0.51944 | 5.0833 | Total - 8 nos. String Faulty | 0.652 | 0.77076 | 21.1064 | checked & rectified
Malwa | July | Inverter 32 | IGBT SAT Trip | 1328.16 | 44767 | 0.53125 | 44767 | 0.55903 | 0.66667 | Inv - 32 tripped due to IGBT SAT TRIP in U1- Phase | 0.1023 | 0.77076 | 104.7234 | We will checking tonight.
Malwa | July | Inverter 24 | Ground fault | 1324.56 | 44767 | 0.64931 | 44767 | 0.65625 | 0.16667 | Inv - 24 tripped due to DC Earth Fault | 0.051 | 0.77076 | 52.0666 | checked & rectified
Malwa | July | SCB.09.03 | String fault | 60 | 44768 | 0.26944 | 44768 | 0.50208 | 5.5833 | Total - 10 nos. String Faulty | 1.23 | 0.75428 | 55.6657 | checked & rectified
Malwa | July | SCB.27.07 | String fault | 30 | 44768 | 0.26736 | 44768 | 0.46875 | 4.8333 | Total - 5 nos. String Faulty | 0.883 | 0.75428 | 19.9808 | checked & rectified
Malwa | July | Inverter 24 | IGBT SAT Trip | 1324.56 | 44768 | 0.41319 | 44768 | 0.43403 | 0.5 | Inv - 24 tripped due to IGBT SAT TRIP in V2- Phase | 0.143 | 0.75428 | 142.8692 | We will checking tonight.
Malwa | July | SCB.14.02 | String fault | 72 | 44769 | 0.29722 | 44769 | 0.52292 | 5.4167 | Total - 12 nos. String Faulty | 1.834 | 0.75454 | 99.6355 | checked & rectified
Malwa | July | Inverter 40 | DC CB OFF failure | 1324.44 | 44769 | 0.29861 | 44769 | 0.31597 | 0.41667 | Inv - 40 tripped due to DC CB OFF failure | 0.0256 | 0.75454 | 25.5832 | checked & rectified
Malwa | July | Inverter 15 | GND LEAK CUR | 1321.8 | 44769 | 0.45556 | 44769 | 0.45903 | 0.083333 | Inverter 15 tripped due to GND LEAK CUR (8197) | 0.0376 | 0.75454 | 37.5004 | checked & rectified
Malwa | July | Inverter 01 | GND LEAK CUR | 1313.4 | 44770 | 0.56597 | 44770 | 0.56944 | 0.083333 | Inverter 1 tripped due to GND LEAK CUR (8197) | 0.0382 | 0.73799 | 37.0262 | checked & rectified
Malwa | July | Inverter 16 | GND LEAK CUR | 1325.88 | 44770 | 0.69236 | 44770 | 0.69583 | 0.083333 | Inverter 16 tripped due to GND LEAK CUR (8197) | 0.029 | 0.73799 | 28.376 | checked & rectified
Malwa | July | Inverter 34 | IGBT stack faulty | 1319.28 | 44770 | 0.28819 | 44770 | 0.49306 | 4.9167 | Inverter 34 tripped due to Inverter Fuse Failure | 2.23 | 0.73799 | 2171.1533 | Inv started on half at 11:50 am after replaced IGBT satck. Inv running on half load from 11:51 to 15:40. after than inv manually stop at 15:41 for replaced faulty material of IGBT Satck. Inv running on full load at 16:50.
Malwa | July | SCB.15.05 | String fault | 30 | 44771 | 0.26597 | 44771 | 0.48125 | 5.1667 | Total - 5 nos. String Faulty | 1.193 | 0.72656 | 26.0035 | checked & rectified
Malwa | July | SCB.32.07 | String fault | 30 | 44771 | 0.26736 | 44771 | 0.48958 | 5.3333 | Total - 5 nos. String Faulty | 1.213 | 0.72656 | 26.4395 | checked & rectified
Malwa | July | Inverter 16 | GND LEAK CUR | 1325.88 | 44771 | 0.41319 | 44771 | 0.41667 | 0.083333 | Inverter 16 tripped due to GND LEAK CUR (8197) | 0.02326 | 0.72656 | 22.407 | checked & rectified
Malwa | July | Inverter 33 | DC Output Detection fault | 1332.72 | 44771 | 0.48264 | 44771 | 0.51111 | 0.68333 | Inverter 33 tripped due to DC Output Detection fault | 0.38 | 0.72656 | 367.9537 | checked & rectified
Malwa | July | Inverter 01 | GND LEAK CUR | 1313.4 | 44772 | 0.37292 | 44772 | 0.37986 | 0.16667 | Inverter 1 tripped due to GND LEAK CUR (8197) | 0.1058 | 0.7243 | 100.6471 | checked & rectified
Malwa | July | Inverter 12 | GND LEAK CUR | 1323.84 | 44772 | 0.52569 | 44772 | 0.52917 | 0.083333 | Inverter 12 tripped due to GND LEAK CUR (8197) | 0.08152 | 0.7243 | 78.166 | checked & rectified
Malwa | July | SCB.34.07 | String fault | 42 | 44772 | 0.25486 | 44772 | 0.52083 | 6.3833 | Total - 7 nos. String Faulty | 2.587 | 0.7243 | 78.6981 | checked & rectified
Malwa | July | All Inverters | Under Voltage Relay | 26521 | 44773 | 0.40278 | 44773 | 0.41042 | 0.18333 | P2, 33kV Ougoing Feeder tripped on Under Voltage Relay (59) fault | 0.095 | 0.7129 | 1796.1429 | Pysically checked all Feeder, 132kV Switchyard, 33kV Switchyard, All LCR after than we taken trial & feeder Charged.
Malwa | July | Inverter 39 | Precharge failure | 1324.08 | 44773 | 0.41042 | 44773 | 0.41736 | 0.16667 | Inverter 39 tripped due to Precharge Failure | 0.125 | 0.7129 | 117.9917 | checked & rectified
Malwa | July | Inverter 40 | DC CB OFF failure | 1324.44 | 44773 | 0.41042 | 44773 | 0.41736 | 0.16667 | Inverter 40 tripped due to DC CB Off Failure | 0.125 | 0.7129 | 118.0238 | checked & rectified
Malwa | July | Inverter 28 | DC Output Detection fault | 1329.96 | 44773 | 0.42708 | 44773 | 0.46528 | 0.91667 | Inverter 28 tripped due to DC Output Detection fault | 0.64 | 0.7129 | 606.8005 | checked & rectified
Malwa | July | Inverter 35 | IGBT stack faulty | 1324.56 | 44773 | 0.55556 | 44773 | 0.65417 | 2.3667 | Inverter 35 tripped due to Inverter Fuse Failure | 2.1 | 0.7129 | 1982.9799 | Checked than found W1 - Phase IGBT Stack faulty than inv started on half load at 15:42.
Malwa | July | Inverter 10 | GND LEAK CUR | 1331.4 | 44773 | 0.44861 | 44773 | 0.45417 | 0.13333 | Inverter 10 tripped due to GND LEAK CUR (8197) | 0.126 | 0.7129 | 119.5932 | checked & rectified
Malwa | August | Inverter 35 | Inverter drive failure | 1324.56 | 44774 | 0.26389 | 44774 | 0.36458 | 2.4167 | Inverter 35 tripped due to Inverte Drive Failure | 3.63 | 0.71153 | 3421.145 | after repalced faulty IGBT Stack & Inverter started at morning but inv tripped due to inverter Drive failure than Inv started on half load at 8:45. inv mannually stopped at 16:07 for replacement of faulty gate driver card & Inv started on full load at 18:30.
Malwa | August | SCB.35.10 | String fault | 132 | 44775 | 0.28125 | 44775 | 0.52083 | 5.75 | Total -22 nos. String Faulty | 3.19 | 0.72818 | 306.6207 | checked & rectified
Malwa | August | Inverter 33 | DC CB OFF failure | 1332.72 | 44775 | 0.47222 | 44775 | 0.47917 | 0.16667 | Inverter 33 tripped due to DC CB Off Failure | 0.242 | 0.72818 | 234.8503 | checked & rectified
Malwa | August | SCB.29.04 | String fault | 24 | 44776 | 0.27431 | 44776 | 0.52083 | 5.9167 | Total -04 nos. String Faulty | 2.27 | 0.72864 | 39.6963 | checked & rectified
Malwa | August | Inverter 01 | GND LEAK CUR | 1313.4 | 44776 | 0.55069 | 44776 | 0.57153 | 0.5 | Inverter 01 tripped due to GND LEAK CUR (8197) | 0.06 | 0.72864 | 57.4197 | checked & rectified
Malwa | August | Inverter 13 | GND LEAK CUR | 1335.96 | 44776 | 0.55764 | 44776 | 0.57153 | 0.33333 | Inverter 13 tripped due to GND LEAK CUR (8197) | 0.054 | 0.72864 | 52.5654 | checked & rectified
Malwa | August | SCB.35.04 | String fault | 24 | 44777 | 0.27083 | 44777 | 0.47917 | 5 | Total - 4 nos. String Faulty | 1.611 | 0.71333 | 27.5801 | checked & rectified
Malwa | August | SCB.20.10 | String fault | 31.96 | 44777 | 0.25278 | 44777 | 0.78056 | 12.6667 | SCB 5210, Manually remove as per instruct by VG Project Team | 4.63 | 0.71333 | 105.5546
Malwa | August | SCB.35.10 | String fault | 180 | 44778 | 0.26389 | 44778 | 0.67014 | 9.75 | Total - 30 nos. String Rectified | 4.9 | 0.70573 | 622.4518 | checked & rectified
Malwa | August | SCB.22.02 | String fault | 330 | 44778 | 0.26389 | 44778 | 0.78125 | 12.4167 | Total - 55 nos. String Rectification Pending | 5.26 | 0.70573 | 1225.002 | Rectification Pending
Malwa | August | SCB.29.01 | String fault | 282 | 44779 | 0.25139 | 44779 | 0.70833 | 10.9667 | Total - 47 nos. String Rectified | 4.836 | 0.70366 | 959.6173 | checked & rectified
Malwa | August | SCB.21.06 | String fault | 48 | 44779 | 0.25139 | 44779 | 0.77778 | 12.6333 | Total - 8 nos. String Rectification Pending | 4.96 | 0.70366 | 167.5273 | Rectification Pending
Malwa | August | Inverter 32 | Ground fault | 1328.16 | 44779 | 0.66875 | 44779 | 0.67222 | 0.083333 | Inv - 32 tripped due to DC Earth Fault | 0.0255 | 0.70366 | 23.8316 | checked & rectified
Malwa | August | SCB.21.07 | String fault | 60 | 44780 | 0.27083 | 44780 | 0.52083 | 6 | Total - 10 nos. String Rectified | 1.774 | 0.75886 | 80.773 | checked & rectified
Malwa | August | SCB.12.10 | String fault | 168 | 44780 | 0.27083 | 44780 | 0.70833 | 10.5 | Total - 28 nos. String Rectified | 3.278 | 0.75886 | 417.9069 | checked & rectified
Malwa | August | Inverter 32 | Ground fault | 1328.16 | 44780 | 0.53819 | 44780 | 0.54444 | 0.15 | Inv - 32 tripped due to DC Earth Fault | 0.074 | 0.75886 | 74.5836 | checked & rectified
Malwa | August | Inverter 27 | Ground fault | 1322.76 | 44781 | 0.69444 | 44781 | 0.69792 | 0.083333 | Inv - 27 tripped due to DC Earth Fault | 0.08 | 0.71316 | 75.4668 | checked & rectified
Malwa | August | Inverter 32 | Ground fault | 1328.16 | 44781 | 0.34167 | 44781 | 0.34583 | 0.1 | Inv - 32 tripped on DC earth fault and was running low as compare to other due to low efficiency | 0.88 | 0.71316 | 833.5241 | checked & rectified
Malwa | August | Inverter 33 | IGBT SAT Trip | 1332.72 | 44781 | 0.50833 | 44781 | 0.5125 | 0.1 | Inv - 33 tripped due to IGBT SAT TRIP | 0.081 | 0.71316 | 76.9855 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44781 | 0.46528 | 44781 | 0.47569 | 0.25 | Inv - 37 tripped due to DC Earth Fault | 0.27 | 0.71316 | 254.4002 | checked & rectified
Malwa | August | SCB.21.06 | String fault | 36 | 44781 | 0.27083 | 44781 | 0.77778 | 12.1667 | Total - 6 nos. String Rectification Pending | 6.41 | 0.71316 | 164.5681 | Rectification Pending
Malwa | August | SCB.05.06 | String fault | 198 | 44781 | 0.27083 | 44781 | 0.72917 | 11 | Total - 33 nos. String Rectified | 6.3 | 0.71316 | 889.5919 | checked & rectified
Malwa | August | SCB.06.10 | String fault | 48 | 44782 | 0.27431 | 44782 | 0.54097 | 6.4 | Total - 8 nos. String Rectified | 2.635 | 0.72551 | 91.7621 | checked & rectified
Malwa | August | Inverter 08 | Ground fault | 1328.04 | 44782 | 0.47222 | 44782 | 0.47917 | 0.16667 | Inv - 8 tripped due to DI4 fault | 0.2277 | 0.72551 | 219.3894 | checked & rectified
Malwa | August | SCB.04.10 | String fault | 72 | 44783 | 0.27361 | 44783 | 0.5375 | 6.3333 | Total - 12 nos. String Rectified | 2.264 | 0.74089 | 120.7712 | checked & rectified
Malwa | August | SCB.38.09 | String fault | 72 | 44783 | 0.26181 | 44783 | 0.73681 | 11.4 | Total - 12 nos. String Rectification Pending | 3.69 | 0.74089 | 196.84 | Rectification Pending due to Rain from 13:42.
Malwa | August | Inverter 08 | GND LEAK CUR | 1328.04 | 44783 | 0.28403 | 44783 | 0.31528 | 0.75 | Inverter 8 tripped due to GND LEAK CUR (8197) | 0.0352 | 0.74089 | 34.6345 | checked & rectified
Malwa | August | Inverter 20 | Ground fault | 1325.52 | 44783 | 0.27014 | 44783 | 0.30486 | 0.83333 | Inv - 20 tripped due to DI4 fault | 0.0236 | 0.74089 | 23.1768 | checked & rectified
Malwa | August | Inverter 19 | GND LEAK CUR | 1324.32 | 44783 | 0.58194 | 44783 | 0.58542 | 0.083333 | Inverter 19 tripped due to GND LEAK CUR (8197) | 0.0451 | 0.74089 | 44.2511 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44783 | 0.28472 | 44783 | 0.3125 | 0.66667 | Inv - 37 tripped due to DC Earth Fault | 0.02886 | 0.74089 | 28.2501 | checked & rectified
Malwa | August | Inverter 39 | Ground fault | 1324.08 | 44783 | 0.38194 | 44783 | 0.39583 | 0.33333 | Inv - 39 tripped due to DC Earth Fault | 0.217 | 0.74089 | 212.8769 | checked & rectified
Malwa | August | Inverter 38 | Ground fault | 1320.6 | 44783 | 0.38542 | 44783 | 0.42014 | 0.83333 | Inv - 38 tripped due to DC Earth Fault | 0.44 | 0.74089 | 430.5054 | checked & rectified
Malwa | August | Inverter 33 | DC Output Detection fault | 1332.72 | 44783 | 0.375 | 44783 | 0.37847 | 0.083333 | Inverter 33 tripped due to DC Output Detection fault | 0.2 | 0.74089 | 197.4802 | checked & rectified
Malwa | August | SCB.38.09 | String fault | 72 | 44784 | 0.26667 | 44784 | 0.76597 | 11.9833 | Total - 12 nos. String Rectification Pending | 1.57 | 0.75513 | 85.3603 | Rectification Pending due to Whole day rainy
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44784 | 0.31597 | 44784 | 0.32986 | 0.33333 | Inv - 37 tripped due to DC Earth Fault | 0.017 | 0.75513 | 16.9606 | checked & rectified
Malwa | August | SCB.38.09 | String fault | 132 | 44785 | 0.29167 | 44785 | 0.52083 | 5.5 | Total - 22 nos. String Rectified | 0.9 | 0.7933 | 94.2435 | checked & rectified
Malwa | August | IDT 09 | Overcurrent fault | 2626.7 | 44785 | 0.73542 | 44785 | 0.76736 | 0.76667 | P1, LCR - 5, TR- 1 tripped on Overcurrent fault | 0.07 | 0.7933 | 145.8624 | After checked found LCR Filter capacitor blown in Inv - 18. than reset ASHIDA Relay & Transformer charged. Now Inv started on 2 nos. ISU with 70% Load.
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44785 | 0.44792 | 44785 | 0.45139 | 0.083333 | Inv - 37 tripped due to DC Earth Fault | 0.0475 | 0.7933 | 49.7848 | checked & rectified
Malwa | August | SCB.18.09 | String fault | 36 | 44786 | 0.27708 | 44786 | 0.46806 | 4.5833 | Total - 6 nos. String Rectified | 1.41 | 0.73401 | 37.2583 | checked & rectified
Malwa | August | SCB.18.08 | String fault | 30 | 44786 | 0.27014 | 44786 | 0.78819 | 12.4333 | Total - 5 nos. String Rectification Pending | 4.76 | 0.73401 | 104.8165 | Rectification Pending
Malwa | August | SCB.37.06 | String fault | 60 | 44786 | 0.27014 | 44786 | 0.78819 | 12.4333 | Total - 10 nos. String Rectification Pending | 4.71 | 0.73401 | 207.431 | Rectification Pending
Malwa | August | Inverter 17 | GND LEAK CUR | 1307.52 | 44786 | 0.27014 | 44786 | 0.29792 | 0.66667 | Inverter 17 tripped due to GND LEAK CUR (8197) | 0.0333 | 0.73401 | 31.9591 | checked & rectified
Malwa | August | Inverter 18 | INT CONFIG fault | 1319.16 | 44786 | 0.27014 | 44786 | 0.40208 | 3.1667 | Inv - 18 tripped due to INT CONFIG (5410) fault & Running 2 nos. ISU with 60% load due to Yesterday LCR filter blown | 1.52 | 0.73401 | 1471.7785 | ABB Enginner informed & arrange material asap.
Malwa | August | Inverter 26 | AC Overcurrent fault | 1321.2 | 44786 | 0.44097 | 44786 | 0.44444 | 0.083333 | Inv - 26 tripped due to AC Overcurrent Fault | 0.1325 | 0.73401 | 128.4949 | checked & rectified
Malwa | August | Inverter 38 | AC Overcurrent fault | 1320.6 | 44786 | 0.50694 | 44786 | 0.51042 | 0.083333 | Inv - 38 tripped due to AC Overcurrent Fault | 0.0704 | 0.73401 | 68.241 | checked & rectified
Malwa | August | Inverter 23 | AC Overcurrent fault | 1320 | 44786 | 0.54167 | 44786 | 0.54861 | 0.16667 | Inv - 23 tripped due to AC Overcurrent Fault | 0.1482 | 0.73401 | 143.5898 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44786 | 0.63542 | 44786 | 0.64236 | 0.16667 | Inv - 37 tripped due to DC Earth Fault | 0.1034 | 0.73401 | 100.2745 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44787 | 0.53125 | 44787 | 0.53819 | 0.16667 | Inv - 37 tripped due to DC Earth Fault | 0.179 | 0.74622 | 176.4768 | checked & rectified
Malwa | August | SCB.38.09 | String fault | 120 | 44787 | 0.25417 | 44787 | 0.52083 | 6.4 | Total - 20 nos. String Rectified | 2.803 | 0.74622 | 250.998 | checked & rectified
Malwa | August | Inverter 18 | INT CONFIG fault | 1319.16 | 44787 | 0.25417 | 44787 | 0.77431 | 12.4833 | Inv - 18 tripped due to INT CONFIG (5410) fault & Running 2 nos. ISU with 60% load due to LCR filter blown | 0.45 | 0.74622 | 442.9716 | ABB Enginner informed & arrange material asap.
Malwa | August | Inverter 18 | INT CONFIG fault | 1319.16 | 44788 | 0.26319 | 44788 | 0.70833 | 10.6833 | Inv - 18 tripped due to INT CONFIG (5410) fault & Running 2 nos. ISU with 60% load due to LCR filter blown | 0.06 | 0.76464 | 60.5206 | ABB Enginner informed & arrange material asap.
Malwa | August | Inverter 03 | DC CB OFF failure | 1320 | 44788 | 0.62153 | 44788 | 0.625 | 0.083333 | Inverter 23 tripped due to DC CB Off Failure | 0.07 | 0.76464 | 70.6523 | checked & rectified
Malwa | August | Inverter 06 | AC Overcurrent fault | 1320 | 44788 | 0.61806 | 44788 | 0.62014 | 0.05 | Inv - 26 tripped due to AC Overcurrent Fault | 0.06 | 0.76464 | 60.5591 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44788 | 0.54861 | 44788 | 0.55208 | 0.083333 | Inv - 37 tripped due to DC Earth Fault | 0.05 | 0.76464 | 50.5118 | checked & rectified
Malwa | August | Inverter 19 | GND LEAK CUR | 1324.3 | 44788 | 0.56875 | 44788 | 0.57222 | 0.083333 | Inverter 19 tripped due to GND LEAK CUR (8197) | 0.09 | 0.76464 | 91.1346 | checked & rectified
Malwa | August | Inverter 01 | Ground fault | 1313.4 | 44789 | 0.31875 | 44789 | 0.34653 | 0.66667 | Inv - 1 tripped due to DI4 fault | 0.026 | 0.62775 | 21.4367
Malwa | August | Inverter 06 | Ground fault | 1325.52 | 44789 | 0.37778 | 44789 | 0.38472 | 0.16667 | Inv - 6 tripped due to DI4 fault | 0.012 | 0.62775 | 9.9852
Malwa | August | Inverter 14 | Ground fault | 1322.52 | 44789 | 0.4125 | 44789 | 0.42292 | 0.25 | Inv - 14 tripped due to DI4 fault | 0.0141 | 0.62775 | 11.706
Malwa | August | Inverter 15 | Ground fault | 1321.8 | 44789 | 0.45069 | 44789 | 0.46458 | 0.33333 | Inv - 15 tripped due to DI4 fault | 0.0144 | 0.62775 | 11.9486
Malwa | August | Inverter 19 | Ground fault | 1324.32 | 44789 | 0.5375 | 44789 | 0.55139 | 0.33333 | Inv - 19 tripped due to DI4 fault | 0.0311 | 0.62775 | 25.8548
Malwa | August | Inverter 35 | Ground fault | 1324.56 | 44789 | 0.3125 | 44789 | 0.35764 | 1.0833 | Inv - 35 tripped due to DC Earth Fault | 0.042 | 0.62775 | 34.9228
Malwa | August | Inverter 28 | Ground fault | 1329.96 | 44789 | 0.32292 | 44789 | 0.375 | 1.25 | Inv - 28 tripped due to DC Earth Fault | 0.0512 | 0.62775 | 42.7461
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44789 | 0.53472 | 44789 | 0.57986 | 1.0833 | Inv - 37 tripped due to DC Earth Fault | 0.075 | 0.62775 | 62.204
Malwa | August | SCB.37.07 | String fault | 114 | 44790 | 0.28125 | 44790 | 0.58681 | 7.3333 | Total - 18 nos. String Rectified | 2.5688 | 0.71138 | 208.3227 | checked & rectified
Malwa | August | Inverter 19 | GND LEAK CUR | 1324.32 | 44790 | 0.27708 | 44790 | 0.2875 | 0.25 | Inverter 19 tripped due to GND LEAK CUR (8197) | 0.0125 | 0.71138 | 11.7762 | checked & rectified
Malwa | August | Inverter 40 | IGBT SAT Trip | 1324.44 | 44790 | 0.28472 | 44790 | 0.29861 | 0.33333 | Inv - 40 tripped due to IGBT SAT TRIP in U1- phase | 0.024 | 0.71138 | 22.6123 | checked & rectified
Malwa | August | Inverter 34 | IGBT SAT Trip | 1319.28 | 44790 | 0.28472 | 44790 | 0.30556 | 0.5 | Inv - 34 tripped due to IGBT SAT TRIP in U1- phase | 0.0383 | 0.71138 | 35.9449 | checked & rectified
Malwa | August | Inverter 29 | IGBT SAT Trip | 1333.08 | 44790 | 0.28472 | 44790 | 0.33333 | 1.1667 | Inv - 29 tripped due to IGBT SAT TRIP in W1- phase | 0.077 | 0.71138 | 73.0211 | checked & rectified
Malwa | August | Inverter 33 | IGBT SAT Trip | 1332.72 | 44790 | 0.28472 | 44790 | 0.34722 | 1.5 | Inv - 33 tripped due to IGBT SAT TRIP in U1- phase | 0.12 | 0.71138 | 113.7684 | checked & rectified
Malwa | August | Inverter 35 | IGBT SAT Trip | 1324.56 | 44790 | 0.35764 | 44790 | 0.40625 | 1.1667 | Inv - 35 tripped due to IGBT SAT TRIP in U1- phase | 0.374 | 0.71138 | 352.4071 | checked & rectified
Malwa | August | Inverter 26 | AC Overcurrent fault | 1321.2 | 44790 | 0.50347 | 44790 | 0.51389 | 0.25 | Inv - 26 tripped due to AC Overcurrent Fault | 0.22 | 0.71138 | 206.7724 | checked & rectified
Malwa | August | Inverter 38 | IGBT SAT Trip | 1320.6 | 44790 | 0.53472 | 44790 | 0.59028 | 1.3333 | Inv - 38 tripped due to IGBT SAT TRIP in U2- phase | 0.97 | 0.71138 | 911.2645 | We will checking tonight.
Malwa | August | Inverter 39 | IGBT SAT Trip | 1324.08 | 44790 | 0.56944 | 44790 | 0.57639 | 0.16667 | Inv - 39 tripped due to IGBT SAT TRIP in U2- phase | 0.211 | 0.71138 | 198.7459 | We will checking tonight.
Malwa | August | Inverter 23 | AC Overcurrent fault | 1320 | 44790 | 0.64236 | 44790 | 0.65278 | 0.25 | Inv - 23 tripped due to AC Overcurrent Fault | 0.24 | 0.71138 | 225.3651 | checked & rectified
Malwa | August | SCB.31.07 | String fault | 132 | 44791 | 0.28125 | 44791 | 0.58333 | 7.25 | Total - 22 nos. String Rectified | 3.126 | 0.73249 | 302.2501 | checked & rectified
Malwa | August | Inverter 31 | Negative fuse failure | 1332 | 44791 | 0.35764 | 44791 | 0.37847 | 0.5 | Inv - 31 tripped due to Negative Fuse Failure & DC earth fault | 0.1531 | 0.73249 | 149.3767 | checked & rectified
Malwa | August | Inverter 39 | 24V DC operation & Emergency Stop | 1324.08 | 44791 | 0.42361 | 44791 | 0.47222 | 1.1667 | Inv - 39 tripped due to 24V DC operation & Emergency Stop | 0.85 | 0.73249 | 824.3975 | Replaced Feedback card & Rectified
Malwa | August | Inverter 35 | IGBT SAT Trip | 1324.56 | 44791 | 0.52083 | 44791 | 0.54861 | 0.66667 | Inv - 35 tripped due to IGBT SAT TRIP in U1- phase | 0.41 | 0.73249 | 397.7947 | We will checking tonight.
Malwa | August | SCB.12.05 | String fault | 78 | 44792 | 0.27083 | 44792 | 0.54236 | 6.5167 | Total - 13 nos. String Rectified | 2.18 | 0.73216 | 124.497 | checked & rectified
Malwa | August | SCB.28.02 | String fault | 24 | 44792 | 0.27083 | 44792 | 0.52083 | 6 | Total - 4 nos. String Rectified | 1.97 | 0.73216 | 34.6167 | checked & rectified
Malwa | August | SCB.16.05 | String fault | 66 | 44793 | 0.27083 | 44793 | 0.52083 | 6 | Total - 11 nos. String Rectified | 3.1 | 0.74687 | 152.8091 | checked & rectified
Malwa | August | SCB.34.07 | String fault | 18 | 44794 | 0.27083 | 44794 | 0.52083 | 6 | Total - 3 nos. String Rectified | 0.513 | 0.78201 | 7.2211 | checked & rectified
Malwa | August | Inverter 37 | Ground fault | 1321.2 | 44795 | 0.42014 | 44795 | 0.44792 | 0.66667 | Inv - 37 tripped due to DC Earth Fault | 0.035 | 0.68172 | 31.5241
Malwa | August | Inverter 35 | Ground fault | 1324.56 | 44795 | 0.5 | 44795 | 0.54861 | 1.1667 | Inv - 35 tripped due to DC Earth Fault | 0.1454 | 0.68172 | 131.293
Malwa | August | Inverter 17 | GND LEAK CUR | 1307.52 | 44795 | 0.65 | 44795 | 0.65347 | 0.083333 | Inverter 17 tripped due to GND LEAK CUR (8197) | 0.0134 | 0.68172 | 11.9442
Malwa | August | Inverter 25 | Ground fault | 1334.4 | 44795 | 0.6875 | 44795 | 0.69792 | 0.25 | Inv - 25 tripped due to DC Earth Fault | 0.01 | 0.68172 | 9.0969
Malwa | August | Inverter 40 | IGBT SAT Trip | 1324.44 | 44796 | 0.31597 | 44796 | 0.38194 | 1.5833 | Inv - 40 tripped due to IGBT SAT TRIP in U2- phase | 0.09834 | 0.75136 | 97.8611 | We will checking tonight.
Malwa | August | Inverter 33 | IGBT SAT Trip | 1332.72 | 44796 | 0.31597 | 44796 | 0.4 | 2.0167 | Inv - 33 tripped due to IGBT SAT TRIP in V1- phase | 0.144 | 0.75136 | 144.1946 | checked & rectified
Malwa | August | Inverter 28 | System abnormal fault | 1329.96 | 44796 | 0.44792 | 44796 | 0.46875 | 0.5 | Inv - 28 tripped due to System Abnormal | 0.115 | 0.75136 | 114.9169 | checked & rectified
Malwa | August | Inverter 39 | IGBT SAT Trip | 1324.08 | 44797 | 0.27431 | 44797 | 0.29861 | 0.58333 | Inv - 39 tripped due to IGBT SAT TRIP in V2- phase | 0.05644 | 0.78223 | 58.4571 | checked & rectified
Malwa | August | Inverter 29 | DC CB OFF failure | 1333.08 | 44797 | 0.27431 | 44797 | 0.30208 | 0.66667 | Inv - 29 tripped due to DC CB Off Failure | 0.069 | 0.78223 | 71.9517 | checked & rectified
Malwa | August | Inverter 33 | IGBT SAT Trip | 1332.72 | 44797 | 0.27083 | 44797 | 0.29167 | 0.5 | Inv - 33 tripped due to IGBT SAT TRIP in V1- phase | 0.04 | 0.78223 | 41.6999 | checked & rectified
Malwa | August | Inverter 34 | Ground fault | 1319.28 | 44797 | 0.27083 | 44797 | 0.28819 | 0.41667 | Inv - 34 tripped due to DC Earth Fault | 0.03 | 0.78223 | 30.9595 | checked & rectified
Malwa | August | SCB.04.07 | String fault | 96 | 44798 | 0.28542 | 44798 | 0.5875 | 7.25 | Total - 16 nos. String Rectified | 3.22 | 0.76726 | 237.1746 | checked & rectified
Malwa | August | SCB.31.04 | String fault | 54 | 44798 | 0.28472 | 44798 | 0.48264 | 4.75 | Total - 9 nos. String Rectified | 1.66 | 0.76726 | 68.7769 | checked & rectified
Malwa | August | Inverter 27 | Negative fuse failure | 1322.76 | 44798 | 0.28472 | 44798 | 0.34722 | 1.5 | Inv - 27 tripped due to Negative Fuse failure | 0.32 | 0.76726 | 324.7671 | checked & rectified
Malwa | August | Inverter 39 | IGBT SAT Trip | 1324.08 | 44798 | 0.52917 | 44798 | 0.53611 | 0.16667 | Inv - 39 tripped due to IGBT SAT TRIP in V2- phase | 0.1022 | 0.76726 | 103.826 | We will checking tonight.
Malwa | August | SCB.09.08 | String fault | 150 | 44799 | 0.27847 | 44799 | 0.59097 | 7.5 | Total - 25 nos. String Rectified | 4.5 | 0.69669 | 470.2639 | checked & rectified
Malwa | August | SCB.14.03 | String fault | 108 | 44799 | 0.27778 | 44799 | 0.54514 | 6.4167 | Total - 18 nos. String Rectified | 3.7 | 0.69669 | 278.3962 | checked & rectified
Malwa | August | All Inverters | Overvoltage fault | 26491 | 44800 | 0.39167 | 44800 | 0.40764 | 0.38333 | P1, Outgoing feeder tripped due to Overvoltage (27) Fault | 0.2768 | 0.72043 | 5282.7012 | As per Instruction, Checked visual inspection of 132kV & 33kV Switchyard & VCB panel. After normalization of Voltage we started Feeder.
Malwa | August | All Inverters | Overvoltage fault | 26521 | 44800 | 0.39167 | 44800 | 0.40764 | 0.38333 | P2, Outgoing feeder tripped due to Overvoltage (27) Fault | 0.2768 | 0.72043 | 5288.6837 | As per Instruction, Checked visual inspection of 132kV & 33kV Switchyard & VCB panel. After normalization of Voltage we started Feeder.
Malwa | August | Inverter 26 | 100V DC failure | 1321.2 | 44800 | 0.40764 | 44800 | 0.4125 | 0.11667 | Inv - 26 tripped due to 100V DC Failure | 0.087 | 0.72043 | 82.8094 | checked & rectified
Malwa | August | Inverter 27 | 100V DC failure | 1322.76 | 44800 | 0.40764 | 44800 | 0.4125 | 0.11667 | Inv - 27 tripped due to 100V DC Failure | 0.087 | 0.72043 | 82.9071 | checked & rectified
Malwa | August | Inverter 04 | Ground fault | 1332.36 | 44800 | 0.40764 | 44800 | 0.41389 | 0.15 | Inv - 4 tripped due to DI4 fault | 0.1111 | 0.72043 | 106.6417 | checked & rectified
Malwa | August | Inverter 37 | DC CB OFF failure | 1321.2 | 44800 | 0.40764 | 44800 | 0.41944 | 0.28333 | Inv - 37 tripped due to DC CB Off Failure | 0.2156 | 0.72043 | 205.2149 | checked & rectified
Malwa | August | Inverter 39 | Fan power failure | 1324.08 | 44800 | 0.40764 | 44800 | 0.42708 | 0.46667 | Inv - 39 tripped due to fan Power failure | 0.363 | 0.72043 | 346.2681 | checked & rectified
Malwa | August | Inverter 07 | Short circuit fault | 1331.88 | 44801 | 0.28611 | 44801 | 0.29444 | 0.2 | Inv - 7 tripped due to SC CKT Fault | 0.034 | 0.7322 | 33.1571 | checked & rectified
Malwa | August | Inverter 11 | Ground fault | 1327.08 | 44802 | 0.27222 | 44802 | 0.31875 | 1.1167 | Inv - 11 tripped due to DI4 fault | 0.081 | 0.71975 | 77.3683 | checked & rectified
Malwa | August | Inverter 14 | MAIN CNT FLT | 1322.52 | 44802 | 0.27222 | 44802 | 0.47431 | 4.85 | Inv - 14 tripped due to MAIN CNT FLT | 2.31 | 0.71975 | 2198.8478 | After checked found ISU 3 AC contactor not pick UP due to 24V operating coil so Inverter started on 2 nos. ISU with 60% Load at 11:23 am.
Malwa | August | Inverter 39 | Fan power failure | 1324.08 | 44802 | 0.27431 | 44802 | 0.33819 | 1.5333 | Inv - 39 tripped due to fan Power failure | 0.16 | 0.71975 | 152.4808 | checked & rectified
Malwa | August | SCB.30.07 | String fault | 72 | 44803 | 0.27431 | 44803 | 0.53819 | 6.3333 | Total - 12 nos. String Rectified | 2.97 | 0.73079 | 156.2723 | checked & rectified
Malwa | August | Inverter 14 | Inv curtailed | 793.5 | 44803 | 0.39236 | 44803 | 0.64028 | 5.95 | Inv - 14 running on 2 nos. ISU with 60% load due to AC contactor operating coil failure | 0.94 | 0.73079 | 545.0894 | Material Dispathed .
Malwa | August | Inverter 14 | Inv curtailed | 793.5 | 44804 | 0.39375 | 44804 | 0.64722 | 6.0833 | Inv - 14 running on 2 nos. ISU with 60% load due to AC contactor operating coil failure | 0.92 | 0.7248 | 529.1149 | Material Dispathed .
Malwa | September | Inverter 07 | Short circuit fault | 1331.88 | 44805 | 0.57083 | 44805 | 0.58125 | 0.25 | Inv - 7 tripped due to SC CKT Fault | 0.043 | 0.71143 | 40.7442 | checked & rectified
Malwa | September | Inverter 12 | Ground fault | 1323.84 | 44805 | 0.6125 | 44805 | 0.63681 | 0.58333 | Inv - 12 tripped due to DI4 fault | 0.0144 | 0.71143 | 13.5622 | checked & rectified
Malwa | September | Inverter 17 | Ground fault | 1307.52 | 44805 | 0.63333 | 44805 | 0.64722 | 0.33333 | Inv - 17 tripped due to DI4 fault | 0.01155 | 0.71143 | 10.7439 | checked & rectified
Malwa | September | SCB.19.01 | String fault | 31.96 | 44805 | 0.25486 | 44805 | 0.77153 | 12.4 | SCB 5210, Manually remove as per instruct by VG Project Team at last night | 3.74 | 0.71143 | 85.0375
Malwa | September | SCB.16.01 | String fault | 48 | 44806 | 0.28125 | 44806 | 0.53125 | 6 | Total - 8 nos. String Rectified | 2.94 | 0.71713 | 101.2012 | checked & rectified
Malwa | September | SCB.24.05 | String fault | 66 | 44806 | 0.27778 | 44806 | 0.53819 | 6.25 | Total - 11 nos. String Rectified | 3.263 | 0.71713 | 154.4394 | checked & rectified
Malwa | September | Inverter 25 | Negative fuse failure | 1334.4 | 44806 | 0.28472 | 44806 | 0.30556 | 0.5 | Inv - 25 tripped due to Negative Fuse Failure | 0.066 | 0.71713 | 63.1578 | checked & rectified
Malwa | September | Inverter 10 | Ground fault | 1331.4 | 44806 | 0.49861 | 44806 | 0.50556 | 0.16667 | Inv - 10 tripped due to DI4 fault | 0.14 | 0.71713 | 133.6699 | checked & rectified
Malwa | September | SCB.18.05 | String fault | 102 | 44807 | 0.28125 | 44807 | 0.5625 | 6.75 | Total - 17 nos. String Rectified | 4.043 | 0.68728 | 283.4248 | checked & rectified
Malwa | September | Inverter 23 | AC Overcurrent fault | 1320 | 44807 | 0.52778 | 44807 | 0.53819 | 0.25 | Inv - 23 tripped due to AC Overcurrent Fault | 0.354 | 0.68728 | 321.1524 | checked & rectified
Malwa | September | Inverter 10 | Ground fault | 1331.4 | 44807 | 0.51389 | 44807 | 0.51736 | 0.083333 | Inv - 10 tripped due to DI4 fault | 0.09 | 0.68728 | 82.3541 | checked & rectified
Malwa | September | SCB.11.03 | String fault | 30 | 44808 | 0.26042 | 44808 | 0.52083 | 6.25 | Total - 5 nos. String Rectified | 3.36 | 0.73104 | 73.6893 | checked & rectified
Malwa | September | SCB.22.05 | String fault | 84 | 44809 | 0.26389 | 44809 | 0.52431 | 6.25 | Total - 14 nos. String Rectified | 3.55 | 0.73135 | 218.0896 | checked & rectified
Malwa | September | Inverter 26 | Ground fault | 1321.2 | 44810 | 0.40903 | 44810 | 0.41458 | 0.13333 | Inv - 26 tripped due to DC Earth Fault | 0.13 | 0.70463 | 121.025 | checked & rectified
Malwa | September | Inverter 23 | AC Overcurrent fault | 1320 | 44810 | 0.54167 | 44810 | 0.55208 | 0.25 | Inv - 23 tripped due to AC Overcurrent Fault | 0.32 | 0.70463 | 297.637 | checked & rectified
Malwa | September | SCB.15.07 | String fault | 24 | 44810 | 0.27083 | 44810 | 0.46528 | 4.6667 | Total - 4 nos. String Rectified | 2.3 | 0.70463 | 38.8957 | checked & rectified
Malwa | September | SCB.05.06 | String fault | 24 | 44811 | 0.27431 | 44811 | 0.46181 | 4.5 | Total - 4 nos. String Rectified | 2.24 | 0.70963 | 38.1498 | checked & rectified
Malwa | September | Inverter 23 | AC Overcurrent fault | 1320 | 44811 | 0.49653 | 44811 | 0.50347 | 0.16667 | Inv - 23 tripped due to AC Overcurrent Fault | 0.216 | 0.70963 | 202.3299 | checked & rectified
Malwa | September | Inverter 12 | Ground fault | 1323.84 | 44811 | 0.62917 | 44811 | 0.63889 | 0.23333 | Inv - 12 tripped due to DI4 fault | 0.0885 | 0.70963 | 83.1402 | checked & rectified
Malwa | September | SCB.05.06 | String fault | 36 | 44812 | 0.27431 | 44812 | 0.48264 | 5 | Total - 6 nos. String Rectified | 2.73 | 0.70979 | 69.7581 | checked & rectified
Malwa | September | Inverter 23 | AC Overcurrent fault | 1320 | 44813 | 0.53472 | 44813 | 0.54861 | 0.33333 | Inv - 23 tripped due to AC Overcurrent Fault | 0.37 | 0.69819 | 340.9965 | checked & rectified
Malwa | September | Inverter 22 | DC Output Detection fault | 1328.16 | 44813 | 0.48264 | 44813 | 0.48611 | 0.083333 | Inverter 22 tripped due to DC Output Detection fault | 0.17 | 0.69819 | 157.6426 | checked & rectified
Malwa | September | SCB.25.06 | String fault | 30 | 44813 | 0.2625 | 44813 | 0.47917 | 5.2 | Total - 5 nos. String Rectified | 2.11 | 0.69819 | 44.1955 | checked & rectified
Malwa | September | Inverter 34 | Feedback circuit abnormal | 1319.28 | 44814 | 0.35972 | 44814 | 0.36667 | 0.16667 | Inv - 34 tripped due to Feedback circuit Abnormal | 0.0755 | 0.69135 | 68.8621 | checked & rectified
Malwa | September | SCB.05.04 | String fault | 48 | 44815 | 0.26042 | 44815 | 0.50347 | 5.8333 | Total - 6 nos. String Rectified | 2.75 | 0.70559 | 93.138 | checked & rectified
Malwa | September | SCB.22.09 | String fault | 78 | 44817 | 0.28125 | 44817 | 0.53472 | 6.0833 | Total - 13 nos. String Rectified | 2.6 | 0.75825 | 153.7724 | checked & rectified
Malwa | September | Inverter 05 | No Comm. fault | 1325.4 | 44817 | 0.27292 | 44817 | 0.29375 | 0.5 | Inv - 5 tripped due to NO COMMUCATION failure | 0.012 | 0.75825 | 12.0598 | checked & rectified
Malwa | September | Inverter 07 | Short circuit fault | 1331.88 | 44817 | 0.60903 | 44817 | 0.61806 | 0.21667 | Inv - 7 tripped due to SC CKT Fault | 0.2 | 0.75825 | 201.9787 | checked & rectified
Malwa | September | Inverter 36 | FRC cable faulty | 1325.52 | 44818 | 0.65625 | 44818 | 0.71875 | 1.5 | Inv - 36 tripped due to Inverter Fuse Failure | 0.0614 | 0.77331 | 62.9376 | Replaced FRC cable of U1- Phase & Inv started.
Pavagada | April | Inverter-14 | RISO fault | 3503.5 | 44652 | 0.25972 | 44652 | 0.27708 | 0.41667 | Inverter did not start due to Riso fault | 0.00625 | 0.72347 | 15.8416 | Reset and Restart
Pavagada | April | Inverter-18 | RISO fault | 3536 | 44652 | 0.25972 | 44652 | 0.27778 | 0.43333 | Inverter did not start due to Riso fault | 0.0052867 | 0.72347 | 13.5242 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3510 | 44655 | 0.25625 | 44655 | 0.27153 | 0.36667 | Inverter did not start due to Riso fault | 0.0031057 | 0.72596 | 7.9136 | Reset and Restart
Pavagada | April | Inverter-17 | Ground fault | 3477.5 | 44663 | 0.48125 | 44663 | 0.49306 | 0.28333 | Cable Insulation damaged | 0.27231 | 0.71654 | 678.528 | we are found the fault smb 9A2-3
Pavagada | April | Inverter-10 | RISO fault | 3529.5 | 44664 | 0.25556 | 44664 | 0.275 | 0.46667 | Inverter did not start due to Riso fault | 0.009086 | 0.71837 | 23.0373 | Reset and Restart
Pavagada | April | Inverter-15 | RISO fault | 3542.5 | 44664 | 0.25556 | 44664 | 0.27083 | 0.36667 | Inverter did not start due to Riso fault | 0.0047483 | 0.71837 | 12.0836 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44666 | 0.25486 | 44666 | 0.26944 | 0.35 | Inverter did not start due to Riso fault | 0.0022225 | 0.72395 | 5.6789 | Reset and Restart
Pavagada | April | Inverter 15 | RISO fault | 3542.5 | 44666 | 0.25486 | 44666 | 0.27153 | 0.4 | Inverter did not start due to Riso fault | 0.002896 | 0.72395 | 7.427 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44669 | 0.25278 | 44669 | 0.26944 | 0.4 | Inverter did not start due to Riso fault | 0.004124 | 0.74979 | 10.9137 | Reset and Restart
Pavagada | April | Inverter 1, | Grid failure | 3484 | 44670 | 0.58958 | 44670 | 0.60208 | 0.3 | Inverters tripped due to grid frequency fluctuation | 0.15878 | 0.74019 | 409.4613 | Reset and Restart
Pavagada | April | Inverter 2 | Grid failure | 3510 | 44670 | 0.58958 | 44670 | 0.59861 | 0.21667 | Inverters tripped due to grid frequency fluctuation | 0.10482 | 0.74019 | 272.3219 | Reset and Restart
Pavagada | April | Inverter 3, | Grid failure | 3526.6 | 44670 | 0.58958 | 44670 | 0.59792 | 0.2 | Inverters tripped due to grid frequency fluctuation | 0.095524 | 0.74019 | 249.3521 | Reset and Restart
Pavagada | April | Inverter 4 | Grid failure | 3488 | 44670 | 0.58958 | 44670 | 0.59931 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.11379 | 0.74019 | 293.787 | Reset and Restart
Pavagada | April | Inverter 5 | Grid failure | 3523 | 44670 | 0.58958 | 44670 | 0.6 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.12249 | 0.74019 | 319.4102 | Reset and Restart
Pavagada | April | Inverter 6 | Grid failure | 3510 | 44670 | 0.58958 | 44670 | 0.6 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.12249 | 0.74019 | 318.2316 | Reset and Restart
Pavagada | April | Inverter 7 | Grid failure | 3479.5 | 44670 | 0.58958 | 44670 | 0.60278 | 0.31667 | Inverters tripped due to grid frequency fluctuation | 0.17085 | 0.74019 | 440.035 | Reset and Restart
Pavagada | April | Inverter 8 | Grid failure | 3516.5 | 44670 | 0.58958 | 44670 | 0.60625 | 0.4 | Inverters tripped due to grid frequency fluctuation | 0.23208 | 0.74019 | 604.0672 | Reset and Restart
Pavagada | April | Inverter 9 | Grid failure | 3477.5 | 44670 | 0.58958 | 44670 | 0.59722 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.086572 | 0.74019 | 222.8374 | Reset and Restart
Pavagada | April | Inverter 10 | Grid failure | 3529.5 | 44670 | 0.58958 | 44670 | 0.59722 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.086572 | 0.74019 | 226.1696 | Reset and Restart
Pavagada | April | Inverter 11 | Grid failure | 3497 | 44670 | 0.58958 | 44670 | 0.60139 | 0.28333 | Inverters tripped due to grid frequency fluctuation | 0.14594 | 0.74019 | 377.7495 | Reset and Restart
Pavagada | April | Inverter 12 | Grid failure | 3490.5 | 44670 | 0.58958 | 44670 | 0.60139 | 0.28333 | Inverters tripped due to grid frequency fluctuation | 0.14594 | 0.74019 | 377.0474 | Reset and Restart
Pavagada | April | Inverter13 | Grid failure | 3555.5 | 44670 | 0.58958 | 44670 | 0.60069 | 0.26667 | Inverters tripped due to grid frequency fluctuation | 0.13223 | 0.74019 | 347.9879 | Reset and Restart
Pavagada | April | Inverter 14 | Grid failure | 3503.5 | 44670 | 0.58958 | 44670 | 0.60069 | 0.26667 | Inverters tripped due to grid frequency fluctuation | 0.13223 | 0.74019 | 342.8985 | Reset and Restart
Pavagada | April | Inverter 15 | Grid failure | 3542.5 | 44670 | 0.58958 | 44670 | 0.59722 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.086572 | 0.74019 | 227.0026 | Reset and Restart
Pavagada | April | Inverter 16 | Grid failure | 3497 | 44670 | 0.58958 | 44670 | 0.59722 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.086572 | 0.74019 | 224.087 | Reset and Restart
Pavagada | April | Inverter 17 | Grid failure | 3477.5 | 44670 | 0.58958 | 44670 | 0.60486 | 0.36667 | Inverters tripped due to grid frequency fluctuation | 0.20747 | 0.74019 | 534.034 | Reset and Restart
Pavagada | April | Inverter 18 | Grid failure | 3536 | 44670 | 0.58958 | 44670 | 0.60486 | 0.36667 | Inverters tripped due to grid frequency fluctuation | 0.20747 | 0.74019 | 543.0177 | Reset and Restart
Pavagada | April | Inverter 19 | Grid failure | 3507.2 | 44670 | 0.58958 | 44670 | 0.59861 | 0.21667 | Inverters tripped due to grid frequency fluctuation | 0.10698 | 0.74019 | 277.7293 | Reset and Restart
Pavagada | April | Inverter 20 | Grid failure | 3545.6 | 44670 | 0.58958 | 44670 | 0.59861 | 0.21667 | Inverters tripped due to grid frequency fluctuation | 0.10698 | 0.74019 | 280.7701 | Reset and Restart
Pavagada | April | Inverter 1, | Grid failure | 3484 | 44671 | 0.59792 | 44671 | 0.60556 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.14021 | 0.75013 | 366.4308 | Reset and Restart
Pavagada | April | Inverter 2 | Grid failure | 3510 | 44671 | 0.59792 | 44671 | 0.60903 | 0.26667 | Inverters tripped due to grid frequency fluctuation | 0.20269 | 0.75013 | 533.6749 | Reset and Restart
Pavagada | April | Inverter 3, | Grid failure | 3526.6 | 44671 | 0.59792 | 44671 | 0.61042 | 0.3 | Inverters tripped due to grid frequency fluctuation | 0.22752 | 0.75013 | 601.8745 | Reset and Restart
Pavagada | April | Inverter 4 | Grid failure | 3488 | 44671 | 0.59792 | 44671 | 0.60556 | 0.18333 | Inverters tripped due to grid frequency fluctuation | 0.14021 | 0.75013 | 366.8515 | Reset and Restart
Pavagada | April | Inverter 5 | Grid failure | 3523 | 44671 | 0.59792 | 44671 | 0.61458 | 0.4 | Inverters tripped due to grid frequency fluctuation | 0.30113 | 0.75013 | 795.7922 | Reset and Restart
Pavagada | April | Inverter 6 | Grid failure | 3510 | 44671 | 0.59792 | 44671 | 0.61458 | 0.4 | Inverters tripped due to grid frequency fluctuation | 0.30113 | 0.75013 | 792.8557 | Reset and Restart
Pavagada | April | Inverter 7 | Grid failure | 3479.5 | 44671 | 0.59792 | 44671 | 0.60486 | 0.16667 | Inverters tripped due to grid frequency fluctuation | 0.12748 | 0.75013 | 332.7409 | Reset and Restart
Pavagada | April | Inverter 8 | Grid failure | 3516.5 | 44671 | 0.59792 | 44671 | 0.60625 | 0.2 | Inverters tripped due to grid frequency fluctuation | 0.15287 | 0.75013 | 403.2501 | Reset and Restart
Pavagada | April | Inverter 9 | Grid failure | 3477.5 | 44671 | 0.59792 | 44671 | 0.60625 | 0.2 | Inverters tripped due to grid frequency fluctuation | 0.15287 | 0.75013 | 398.7778 | Reset and Restart
Pavagada | April | Inverter 10 | Grid failure | 3529.5 | 44671 | 0.59792 | 44671 | 0.60486 | 0.16667 | Inverters tripped due to grid frequency fluctuation | 0.12748 | 0.75013 | 337.5223 | Reset and Restart
Pavagada | April | Inverter 11 | Grid failure | 3497 | 44671 | 0.59792 | 44671 | 0.61389 | 0.38333 | Inverters tripped due to grid frequency fluctuation | 0.28894 | 0.75013 | 757.941 | Reset and Restart
Pavagada | April | Inverter 12 | Grid failure | 3490.5 | 44671 | 0.59792 | 44671 | 0.6125 | 0.35 | Inverters tripped due to grid frequency fluctuation | 0.26463 | 0.75013 | 692.8912 | Reset and Restart
Pavagada | April | Inverter13 | Grid failure | 3555.5 | 44671 | 0.59792 | 44671 | 0.61389 | 0.38333 | Inverters tripped due to grid frequency fluctuation | 0.28894 | 0.75013 | 770.6203 | Reset and Restart
Pavagada | April | Inverter 14 | Grid failure | 3503.5 | 44671 | 0.59792 | 44671 | 0.61528 | 0.41667 | Inverters tripped due to grid frequency fluctuation | 0.31323 | 0.75013 | 823.1793 | Reset and Restart
Pavagada | April | Inverter 15 | Grid failure | 3542.5 | 44671 | 0.59792 | 44671 | 0.61875 | 0.5 | Inverters tripped due to grid frequency fluctuation | 0.37272 | 0.75013 | 990.4406 | Reset and Restart
Pavagada | April | Inverter 16 | Grid failure | 3497 | 44671 | 0.59792 | 44671 | 0.61875 | 0.5 | Inverters tripped due to grid frequency fluctuation | 0.37287 | 0.75013 | 978.1128 | Reset and Restart
Pavagada | April | Inverter 17 | Grid failure | 3477.5 | 44671 | 0.59792 | 44671 | 0.61528 | 0.41667 | Inverters tripped due to grid frequency fluctuation | 0.31323 | 0.75013 | 817.0703 | Reset and Restart
Pavagada | April | Inverter 18 | Grid failure | 3536 | 44671 | 0.59792 | 44671 | 0.61111 | 0.31667 | Inverters tripped due to grid frequency fluctuation | 0.24 | 0.75013 | 636.577 | Reset and Restart
Pavagada | April | Inverter 19 | Grid failure | 3507.2 | 44671 | 0.59792 | 44671 | 0.66042 | 1.5 | Inverters tripped due to grid frequency fluctuation | 1.1182 | 0.75013 | 2941.7134 | Reset and Restart
Pavagada | April | Inverter 20 | Grid failure | 3545.6 | 44671 | 0.59792 | 44671 | 0.61875 | 0.5 | Inverters tripped due to grid frequency fluctuation | 0.37272 | 0.75013 | 991.3073 | Reset and Restart
Pavagada | April | Inverter 1, | Grid failure | 3484 | 44671 | 0.67847 | 44671 | 0.69653 | 0.43333 | Inverters tripped due to grid frequency fluctuation | 0.14266 | 0.75013 | 372.8399 | Reset and Restart
Pavagada | April | Inverter 2 | Grid failure | 3510 | 44671 | 0.67847 | 44671 | 0.69375 | 0.36667 | Inverters tripped due to grid frequency fluctuation | 0.1226 | 0.75013 | 322.8061 | Reset and Restart
Pavagada | April | Inverter 3, | Grid failure | 3526.6 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085508 | 0.75013 | 226.2019 | Reset and Restart
Pavagada | April | Inverter 4 | Grid failure | 3488 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 209.5436 | Reset and Restart
Pavagada | April | Inverter 5 | Grid failure | 3523 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085508 | 0.75013 | 225.971 | Reset and Restart
Pavagada | April | Inverter 6 | Grid failure | 3510 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085508 | 0.75013 | 225.1372 | Reset and Restart
Pavagada | April | Inverter 7 | Grid failure | 3479.5 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085758 | 0.75013 | 223.8334 | Reset and Restart
Pavagada | April | Inverter 8 | Grid failure | 3516.5 | 44671 | 0.67847 | 44671 | 0.68958 | 0.26667 | Inverters tripped due to grid frequency fluctuation | 0.090779 | 0.75013 | 239.4585 | Reset and Restart
Pavagada | April | Inverter 9 | Grid failure | 3477.5 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085508 | 0.75013 | 223.0526 | Reset and Restart
Pavagada | April | Inverter 10 | Grid failure | 3529.5 | 44671 | 0.67847 | 44671 | 0.68889 | 0.25 | Inverters tripped due to grid frequency fluctuation | 0.085508 | 0.75013 | 226.3879 | Reset and Restart
Pavagada | April | Inverter 11 | Grid failure | 3497 | 44671 | 0.67847 | 44671 | 0.68681 | 0.2 | Inverters tripped due to grid frequency fluctuation | 0.069334 | 0.75013 | 181.877 | Reset and Restart
Pavagada | April | Inverter 12 | Grid failure | 3490.5 | 44671 | 0.67847 | 44671 | 0.68681 | 0.2 | Inverters tripped due to grid frequency fluctuation | 0.069334 | 0.75013 | 181.5389 | Reset and Restart
Pavagada | April | Inverter13 | Grid failure | 3555.5 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 213.5987 | Reset and Restart
Pavagada | April | Inverter 14 | Grid failure | 3503.5 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 210.4748 | Reset and Restart
Pavagada | April | Inverter 15 | Grid failure | 3542.5 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 212.8177 | Reset and Restart
Pavagada | April | Inverter 16 | Grid failure | 3497 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 210.0843 | Reset and Restart
Pavagada | April | Inverter 17 | Grid failure | 3477.5 | 44671 | 0.67847 | 44671 | 0.69167 | 0.31667 | Inverters tripped due to grid frequency fluctuation | 0.1071 | 0.75013 | 279.3695 | Reset and Restart
Pavagada | April | Inverter 18 | Grid failure | 3536 | 44671 | 0.67847 | 44671 | 0.69167 | 0.31667 | Inverters tripped due to grid frequency fluctuation | 0.1071 | 0.75013 | 284.0692 | Reset and Restart
Pavagada | April | Inverter 19 | Grid failure | 3507.2 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 210.697 | Reset and Restart
Pavagada | April | Inverter 20 | Grid failure | 3545.6 | 44671 | 0.67847 | 44671 | 0.68819 | 0.23333 | Inverters tripped due to grid frequency fluctuation | 0.080087 | 0.75013 | 213.0039 | Reset and Restart
Pavagada | April | Inverter 17 | Grid failure | 3477.5 | 44671 | 0.58403 | 44671 | 0.59792 | 0.33333 | Inverters tripped due to grid frequency fluctuation | 0.27058 | 0.75013 | 705.8277 | Rectified
Pavagada | April | Inverter,3 | RISO fault | 3526.6 | 44672 | 0.25069 | 44672 | 0.27153 | 0.5 | Cable Insulation damaged | 0.00629 | 0.70031 | 15.5344 | Reset and Restart
Pavagada | April | Inverter 4 | Ground fault | 3488 | 44675 | 0.4125 | 44675 | 0.41875 | 0.15 | Inverter due to ground fault on 2B2-2 | 0.10728 | 0.70415 | 263.4983 | Rectified
Pavagada | April | Inverter 4 | RISO fault | 3526.6 | 44676 | 0.24375 | 44676 | 0.26181 | 0.43333 | Inverter did not start due to Riso fault | 0.0024007 | 0.71368 | 6.0422 | Reset and Restart
Pavagada | April | Inverter 5 | RISO fault | 3523 | 44677 | 0.24792 | 44677 | 0.26458 | 0.4 | Inverter did not start due to Riso fault | 0.003448 | 0.72218 | 8.7726 | Reset and Restart
Pavagada | April | Inverter 8 | RISO fault | 3516.5 | 44677 | 0.24792 | 44677 | 0.26458 | 0.4 | Inverter did not start due to Riso fault | 0.003448 | 0.72218 | 8.7564 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44677 | 0.24792 | 44677 | 0.27083 | 0.55 | Inverter did not start due to Riso fault | 0.0081455 | 0.72218 | 20.7625 | Reset and Restart
Pavagada | April | Inverter 19 | RISO fault | 3507.2 | 44677 | 0.24792 | 44677 | 0.27778 | 0.71667 | Inverter did not start due to Riso fault | 0.017293 | 0.72218 | 43.8009 | Reset and Restart
Pavagada | April | Inverter 20 | RISO fault | 3545.6 | 44677 | 0.24792 | 44677 | 0.27778 | 0.71667 | Inverter did not start due to Riso fault | 0.017293 | 0.72218 | 44.2805 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44678 | 0.24931 | 44678 | 0.26528 | 0.38333 | Inverter did not start due to Riso fault | 0.0041783 | 0.72436 | 10.6825 | Rectified
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44679 | 0.24722 | 44679 | 0.26111 | 0.33333 | Inverter did not start due to Riso fault | 0.00253 | 0.72344 | 6.4601 | Rectified
Pavagada | April | Inverter 16 | RISO fault | 3497 | 44680 | 0.24722 | 44680 | 0.26667 | 0.46667 | Inverter started late due to Riso fault | 0.005656 | 0.72089 | 14.2585 | Reset and Restart
Pavagada | April | Inverter 10 | RISO fault | 3529.5 | 44681 | 0.24722 | 44681 | 0.2625 | 0.36667 | Inverter started late due to Riso fault | 0.0033257 | 0.7194 | 8.4442 | Reset and Restart
Pavagada | April | 5B4-4 st 1,2,3,4 | String fault | 52 | 44681 | 0.34375 | 44681 | 0.39306 | 1.1833 | Inside conduit cables are short circuit | 0.61839 | 0.7194 | 23.133 | Rectifird
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44683 | 0.24931 | 44683 | 0.26528 | 0.38333 | Inverter started late due to Riso fault | 0.0040787 | 0.734 | 10.5665 | Rectified
Pavagada | May | Inverter 1 | RISO fault | 3484 | 44685 | 0.24653 | 44685 | 0.2625 | 0.38333 | Inverter started late due to Riso fault | 0.0050485 | 0.74127 | 13.0382 | Reset and Restart
Pavagada | May | Inverter 8 | RISO fault | 3516.5 | 44685 | 0.24653 | 44685 | 0.26944 | 0.55 | Inverter started late due to Riso fault | 0.01216 | 0.74127 | 31.6985 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44685 | 0.24653 | 44685 | 0.27014 | 0.56667 | Inverter started late due to Riso fault | 0.013135 | 0.74127 | 34.3662 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44685 | 0.24653 | 44685 | 0.26944 | 0.55 | Inverter started late due to Riso fault | 0.01216 | 0.74127 | 31.4642 | Reset and Restart
Pavagada | May | Inverter 19 | RISO fault | 3507.2 | 44685 | 0.24653 | 44685 | 0.27153 | 0.6 | Inverter started late due to Riso fault | 0.015228 | 0.74127 | 39.5896 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44685 | 0.24653 | 44685 | 0.27292 | 0.63333 | Inverter started late due to Riso fault | 0.01741 | 0.74127 | 45.7588 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44687 | 0.24653 | 44687 | 0.26458 | 0.43333 | Inverter started late due to Riso fault | 0.0069377 | 0.72209 | 17.6815 | Reset and Restart
Pavagada | May | 7B4-5 st 11 | String fault | 13 | 44688 | 0.39167 | 44688 | 0.40764 | 0.38333 | MC4 connector melted | 0.25477 | 0.73648 | 2.4392 | Replaced new MC4 connected
Pavagada | May | 4A3-2 st 10,11,12 | String fault | 39 | 44688 | 0.42708 | 44688 | 0.44167 | 0.35 | string cable short circuit | 0.28296 | 0.73648 | 8.1273 | Replace with cable and Mc4
Pavagada | May | 9B2-3 st 2 | String fault | 13 | 44688 | 0.45903 | 44688 | 0.47431 | 0.36667 | string cable short circuit | 0.33249 | 0.73648 | 3.1833 | Replace with cable and Mc4
Pavagada | May | Inverter 8 | RISO fault | 3516.5 | 44688 | 0.24375 | 44688 | 0.26389 | 0.48333 | Inverter started late due to Riso fault | 0.0054085 | 0.73648 | 14.0071 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44688 | 0.24375 | 44688 | 0.26389 | 0.48333 | Inverter started late due to Riso fault | 0.0054085 | 0.73648 | 14.0589 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44688 | 0.24375 | 44688 | 0.26944 | 0.61667 | Inverter started late due to Riso fault | 0.009879 | 0.73648 | 25.4431 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44688 | 0.24375 | 44688 | 0.26944 | 0.61667 | Inverter started late due to Riso fault | 0.009879 | 0.73648 | 25.3958 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44688 | 0.24375 | 44688 | 0.27014 | 0.63333 | Inverter started late due to Riso fault | 0.010513 | 0.73648 | 27.4291 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3477.5 | 44688 | 0.24375 | 44688 | 0.26319 | 0.46667 | Inverter started late due to Riso fault | 0.0049467 | 0.73648 | 12.669 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44689 | 0.24722 | 44689 | 0.26458 | 0.41667 | Inverter started late due to Riso fault | 0.0092917 | 0.74367 | 24.3885 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44689 | 0.24722 | 44689 | 0.27083 | 0.56667 | Inverter started late due to Riso fault | 0.018711 | 0.74367 | 48.6607 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44689 | 0.24722 | 44689 | 0.27222 | 0.6 | Inverter started late due to Riso fault | 0.021282 | 0.74367 | 55.2432 | Reset and Restart
Pavagada | May | Inverter 14 | RISO fault | 3503.5 | 44689 | 0.24722 | 44689 | 0.27083 | 0.56667 | Inverter started late due to Riso fault | 0.018711 | 0.74367 | 48.7512 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44689 | 0.24722 | 44689 | 0.26667 | 0.46667 | Inverter started late due to Riso fault | 0.012082 | 0.74367 | 31.8293 | Reset and Restart
Pavagada | May | Inverter 17 | RISO fault | 3477.5 | 44689 | 0.24722 | 44689 | 0.26458 | 0.41667 | Inverter started late due to Riso fault | 0.0092917 | 0.74367 | 24.0292 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44690 | 0.24375 | 44690 | 0.2625 | 0.45 | Inverter started late due to Riso fault | 0.004095 | 0.76649 | 11.0783 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44690 | 0.24375 | 44690 | 0.26597 | 0.53333 | Inverter started late due to Riso fault | 0.006528 | 0.76649 | 17.4653 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44690 | 0.24375 | 44690 | 0.26597 | 0.53333 | Inverter started late due to Riso fault | 0.006528 | 0.76649 | 17.741 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44691 | 0.24722 | 44691 | 0.26806 | 0.5 | Inverter started late due to Riso fault | 0.004635 | 0.87637 | 14.3368 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44691 | 0.24722 | 44691 | 0.26736 | 0.48333 | Inverter started late due to Riso fault | 0.0042775 | 0.87637 | 13.1092 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44691 | 0.24722 | 44691 | 0.26667 | 0.46667 | Inverter started late due to Riso fault | 0.003906 | 0.87637 | 11.9484 | Reset and Restart
Pavagada | May | Inverter 14 | RISO fault | 3503.5 | 44691 | 0.24722 | 44691 | 0.27083 | 0.56667 | Inverter started late due to Riso fault | 0.0063467 | 0.87637 | 19.4866 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44691 | 0.24722 | 44691 | 0.27361 | 0.63333 | Inverter started late due to Riso fault | 0.0083853 | 0.87637 | 26.0327 | Reset and Restart
Pavagada | May | Inverter 5 | RISO fault | 3523 | 44692 | 0.25347 | 44692 | 0.26944 | 0.38333 | Inverter started late due to Riso fault | 0.0032583 | 0.80526 | 9.2437 | Reset and Restart
Pavagada | May | Inverter 6 | RISO fault | 3510 | 44692 | 0.25347 | 44692 | 0.27014 | 0.4 | Inverter started late due to Riso fault | 0.003336 | 0.80526 | 9.4291 | Reset and Restart
Pavagada | May | Inverter 8 | RISO fault | 3516.5 | 44692 | 0.25347 | 44692 | 0.26944 | 0.38333 | Inverter started late due to Riso fault | 0.0030858 | 0.80526 | 8.7382 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44692 | 0.25347 | 44692 | 0.27083 | 0.41667 | Inverter started late due to Riso fault | 0.0035125 | 0.80526 | 9.9832 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44692 | 0.25347 | 44692 | 0.27639 | 0.55 | Inverter started late due to Riso fault | 0.0059895 | 0.80526 | 16.8665 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44692 | 0.25347 | 44692 | 0.27917 | 0.61667 | Inverter started late due to Riso fault | 0.0076282 | 0.80526 | 21.4411 | Reset and Restart
Pavagada | May | INVERTER-01 | RISO fault | 3484 | 44693 | 0.25556 | 44693 | 0.28403 | 0.68333 | Inverter started late due to Riso fault | 0.0048722 | 0.80962 | 13.7431 | Reset and Restart
Pavagada | May | INVERTER-03 | RISO fault | 3526.6 | 44693 | 0.25556 | 44693 | 0.28056 | 0.6 | Inverter started late due to Riso fault | 0.003822 | 0.80962 | 10.9127 | Reset and Restart
Pavagada | May | INVERTER-04 | RISO fault | 3488 | 44693 | 0.25556 | 44693 | 0.27361 | 0.43333 | Inverter started late due to Riso fault | 0.002262 | 0.80962 | 6.3878 | Reset and Restart
Pavagada | May | INVERTER-11 | RISO fault | 3497 | 44693 | 0.25556 | 44693 | 0.28264 | 0.65 | Inverter started late due to Riso fault | 0.004381 | 0.80962 | 12.4037 | Reset and Restart
Pavagada | May | INVERTER-12 | RISO fault | 3490.5 | 44693 | 0.25556 | 44693 | 0.28125 | 0.61667 | Inverter started late due to Riso fault | 0.0039898 | 0.80962 | 11.2752 | Reset and Restart
Pavagada | May | INVERTER-14 | RISO fault | 3503.5 | 44693 | 0.25556 | 44693 | 0.275 | 0.46667 | Inverter started late due to Riso fault | 0.00252 | 0.80962 | 7.148 | Reset and Restart
Pavagada | May | INVERTER-15 | RISO fault | 3542.5 | 44693 | 0.25556 | 44693 | 0.28681 | 0.75 | Inverter started late due to Riso fault | 0.0058575 | 0.80962 | 16.7999 | Reset and Restart
Pavagada | May | INVERTER-19 | RISO fault | 3507.2 | 44693 | 0.25556 | 44693 | 0.29375 | 0.91667 | Inverter started late due to Riso fault | 0.007975 | 0.80962 | 22.6451 | Reset and Restart
Pavagada | May | INVERTER-20 | RISO fault | 3545.6 | 44693 | 0.25556 | 44693 | 0.29097 | 0.85 | Inverter started late due to Riso fault | 0.0070125 | 0.80962 | 20.1301 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44694 | 0.24583 | 44694 | 0.26458 | 0.45 | Inverter started late due to Riso fault | 0.0025425 | 0.7363 | 6.5343 | Reset and Restart
Pavagada | May | Inverter 14 | RISO fault | 3503.5 | 44694 | 0.24583 | 44694 | 0.26528 | 0.46667 | Inverter started late due to Riso fault | 0.002716 | 0.7363 | 7.0062 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44694 | 0.24583 | 44694 | 0.27014 | 0.58333 | Inverter started late due to Riso fault | 0.0040308 | 0.7363 | 10.5137 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3497 | 44694 | 0.24583 | 44694 | 0.26181 | 0.38333 | Inverter started late due to Riso fault | 0.0019818 | 0.7363 | 5.1029 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44694 | 0.24583 | 44694 | 0.26181 | 0.38333 | Inverter started late due to Riso fault | 0.0019818 | 0.7363 | 5.1598 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44695 | 0.23958 | 44695 | 0.25486 | 0.36667 | Inverter started late due to Riso fault | 0.0014337 | 0.74695 | 3.7379 | Reset and Restart
Pavagada | May | Inverter 14 | RISO fault | 3503.5 | 44695 | 0.23958 | 44695 | 0.25556 | 0.38333 | Inverter started late due to Riso fault | 0.0015947 | 0.74695 | 4.1731 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44695 | 0.23958 | 44695 | 0.26111 | 0.51667 | Inverter started late due to Riso fault | 0.0033583 | 0.74695 | 8.8864 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3497 | 44695 | 0.29514 | 44695 | 0.29792 | 0.066667 | Inverter started late due to Riso fault | 0.0076267 | 0.74695 | 19.9215 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44696 | 0.23611 | 44696 | 0.25764 | 0.51667 | Inverter started late due to Riso fault | 0.0046655 | 0.78943 | 12.9995 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44696 | 0.23611 | 44696 | 0.26389 | 0.66667 | Inverter started late due to Riso fault | 0.00846 | 0.78943 | 23.6589 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44697 | 0.23611 | 44697 | 0.25417 | 0.43333 | Inverter started late due to Riso fault | 0.002067 | 0.7365 | 5.3731 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44697 | 0.23611 | 44697 | 0.25903 | 0.55 | Inverter started late due to Riso fault | 0.0037015 | 0.7365 | 9.6574 | Reset and Restart
Pavagada | May | 1A1-6 st 9 | String fault | 13 | 44697 | 0.30208 | 44697 | 0.70625 | 9.7 | string cable is damaged in side conduit | 5.977 | 0.7365 | 57.2272 | Replaced new MC4 connectors
Pavagada | May | 1A3-1 st 1,13 | String fault | 26 | 44697 | 0.30208 | 44697 | 0.35 | 1.15 | string cable is damaged | 0.3048 | 0.7365 | 5.8365 | Replaced new MC4 connectors
Pavagada | May | 9B2-1 st 13 | String fault | 13 | 44697 | 0.30208 | 44697 | 0.36528 | 1.5167 | Cable short circuit | 0.48354 | 0.7365 | 4.6297 | Replaced new cable and 30A
Pavagada | May | 4A3-2 st 11 | String fault | 13 | 44697 | 0.30208 | 44697 | 0.38194 | 1.9167 | Cable insulation damaged | 0.72047 | 0.7365 | 6.8982 | Replaced new MC4 connectors
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44698 | 0.23889 | 44698 | 0.26042 | 0.51667 | Inverter started late due to Riso fault | 0.0044537 | 0.73883 | 11.6139 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44698 | 0.23889 | 44698 | 0.26597 | 0.65 | Inverter started late due to Riso fault | 0.0071175 | 0.73883 | 18.3895 | Reset and Restart
Pavagada | May | Inverter 14 | RISO fault | 3503.5 | 44698 | 0.23889 | 44698 | 0.26667 | 0.66667 | Inverter started late due to Riso fault | 0.00748 | 0.73883 | 19.362 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44698 | 0.23889 | 44698 | 0.27222 | 0.8 | Inverter started late due to Riso fault | 0.010712 | 0.73883 | 28.0367 | Reset and Restart
Pavagada | May | Inverter 17 | RISO fault | 3477.5 | 44698 | 0.23889 | 44698 | 0.25486 | 0.38333 | Inverter started late due to Riso fault | 0.0021198 | 0.73883 | 5.4465 | Reset and Restart
Pavagada | May | 7A4-4 st 13 | String fault | 13 | 44698 | 0.31389 | 44698 | 0.32847 | 0.35 | String cable is damaged | 0.043208 | 0.73883 | 0.415 | Rectified
Pavagada | May | 7B3-1 st 3 | String fault | 13 | 44698 | 0.35833 | 44698 | 0.36736 | 0.21667 | mc4 melt due to over heat | 0.043656 | 0.73883 | 0.41931 | Rectified
Pavagada | May | Inverter 3 | RISO fault | 3526.6 | 44699 | 0.24861 | 44699 | 0.26319 | 0.35 | Inverter started late due to Riso fault | 0.000651 | 0.81334 | 1.8673 | Reset and Restart
Pavagada | May | Inverter 9 | RISO fault | 3477.5 | 44699 | 0.24861 | 44699 | 0.27292 | 0.58333 | Inverter started late due to Riso fault | 0.0022458 | 0.81334 | 6.3521 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44699 | 0.24861 | 44699 | 0.27222 | 0.56667 | Inverter started late due to Riso fault | 0.0020853 | 0.81334 | 5.9864 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44699 | 0.24861 | 44699 | 0.26736 | 0.45 | Inverter started late due to Riso fault | 0.001188 | 0.81334 | 3.379 | Reset and Restart
Pavagada | May | Inverter 13 | RISO fault | 3555.5 | 44699 | 0.24861 | 44699 | 0.27083 | 0.53333 | Inverter started late due to Riso fault | 0.0018027 | 0.81334 | 5.213 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44699 | 0.24861 | 44699 | 0.27778 | 0.7 | Inverter started late due to Riso fault | 0.003808 | 0.81334 | 10.9719 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3497 | 44699 | 0.24861 | 44699 | 0.27778 | 0.7 | Inverter started late due to Riso fault | 0.003808 | 0.81334 | 10.831 | Reset and Restart
Pavagada | May | Inverter 17 | RISO fault | 3477.5 | 44699 | 0.24861 | 44699 | 0.28194 | 0.8 | Inverter started late due to Riso fault | 0.005264 | 0.81334 | 14.8887 | Reset and Restart
Pavagada | May | Inverter 14 | Ground fault | 3503.5 | 44699 | 0.4875 | 44699 | 0.50139 | 0.33333 | Inverter tripped due to Ground fault | 0.14382 | 0.81334 | 409.8227 | we found fault strings and rectified
Pavagada | May | 2B2-1 st 6 | String fault | 13 | 44699 | 0.24861 | 44699 | 0.35069 | 2.45 | String Cable damaged | 0.030625 | 0.81334 | 0.32381 | Rectified
Pavagada | May | 2B1-2 st 14 | String fault | 13 | 44699 | 0.24861 | 44699 | 0.38958 | 3.3833 | String cable damaged inside conduit | 0.088508 | 0.81334 | 0.93584 | Rectified
Pavagada | May | 2B4-4 st 9 | String fault | 13 | 44699 | 0.24861 | 44699 | 0.40903 | 3.85 | String cable damaged inside conduit | 0.17005 | 0.81334 | 1.7981 | Rectified
Pavagada | May | 6A2-2 st 1 | String fault | 13 | 44699 | 0.24861 | 44699 | 0.42847 | 4.3167 | String cable damaged inside conduit | 0.29953 | 0.81334 | 3.1671 | Rectified
Pavagada | May | 7A1-3 st 7 | String fault | 13 | 44699 | 0.24861 | 44699 | 0.77153 | 12.55 | We found 11 diode failure models in this string | 2.51 | 0.81334 | 26.5394 | Plan to replace JB for diode failure modules
Pavagada | May | 7A3-1 st 1,4,8 | String fault | 39 | 44699 | 0.24861 | 44699 | 0.77153 | 12.55 | We found 87 diode failure models in this string | 2.51 | 0.81334 | 79.6183 | Plan to replace JB for diode failure modules
Pavagada | May | Inverter-8 | RISO fault | 3516.5 | 44700 | 0.24375 | 44700 | 0.25833 | 0.35 | Inverter started late due to Riso fault | 0.001568 | 0.80404 | 4.4334 | Reset and Restart
Pavagada | May | Inverter-9 | RISO fault | 3477.5 | 44700 | 0.24375 | 44700 | 0.26458 | 0.5 | Inverter started late due to Riso fault | 0.00392 | 0.80404 | 10.9605 | Reset and Restart
Pavagada | May | Inverter-18 | RISO fault | 3536 | 44700 | 0.24375 | 44700 | 0.26389 | 0.48333 | Inverter started late due to Riso fault | 0.0035573 | 0.80404 | 10.1138 | Reset and Restart
Pavagada | May | Inverter-5 | Ground fault | 3523 | 44700 | 0.28125 | 44700 | 0.28958 | 0.2 | Inverter tripped due to Ground fault | 0.013842 | 0.80404 | 39.2094 | we found fault strings and rectified
Pavagada | May | 3B4-6 S5,7,9 | String fault | 39 | 44700 | 0.28125 | 44700 | 0.35417 | 1.75 | String cable damaged inside conduit | 0.27037 | 0.80404 | 8.4783 | Rectified
Pavagada | May | 3B3-3 S1,2,4 | String fault | 39 | 44700 | 0.28125 | 44700 | 0.39583 | 2.75 | String cable damaged inside conduit | 0.53625 | 0.80404 | 16.8155 | Rectified
Pavagada | May | 3B2-5 S10 | String fault | 13 | 44700 | 0.28125 | 44700 | 0.41667 | 3.25 | String cable damaged inside conduit | 0.6955 | 0.80404 | 7.2697 | Rectified
Pavagada | May | 7B3-2S11,13 | String fault | 26 | 44700 | 0.24375 | 44700 | 0.4375 | 4.65 | String cable damaged inside conduit | 1.0044 | 0.80404 | 20.9971 | Rectified
Pavagada | May | 7B4-5S2 | String fault | 13 | 44700 | 0.24375 | 44700 | 0.45833 | 5.15 | String cable damaged inside conduit | 1.2824 | 0.80404 | 13.4038 | Rectified
Pavagada | May | 10A2-5S10 | String fault | 13 | 44700 | 0.24375 | 44700 | 0.46875 | 5.4 | String cable damaged inside conduit | 1.4256 | 0.80404 | 14.9012 | Rectified
Pavagada | May | 7A1-3 st 7 | String fault | 13 | 44700 | 0.24861 | 44700 | 0.77153 | 12.55 | We found 11 diode failure models in this string | 4.0004 | 0.80404 | 41.8146 | Plan to replace JB for diode failure modules
Pavagada | May | 7A3-1 st 1,4,8 | String fault | 39 | 44700 | 0.24861 | 44700 | 0.77153 | 12.55 | We found 87 diode failure models in this string | 4.0004 | 0.80404 | 125.4437 | Plan to replace JB for diode failure modules
Pavagada | May | Inverter-9 | RISO fault | 3477.5 | 44701 | 0.25278 | 44701 | 0.26806 | 0.36667 | Inverter started late due to Riso fault | 0.000451 | 0.84693 | 1.3283 | Reset and Restart
Pavagada | May | Inverter-10 | RISO fault | 3529.5 | 44701 | 0.25278 | 44701 | 0.26806 | 0.36667 | Inverter started late due to Riso fault | 0.000451 | 0.84693 | 1.3482 | Reset and Restart
Pavagada | May | Inverter-11 | RISO fault | 3497 | 44701 | 0.25278 | 44701 | 0.27569 | 0.55 | Inverter started late due to Riso fault | 0.0006435 | 0.84693 | 1.9059 | Reset and Restart
Pavagada | May | Inverter-12 | RISO fault | 3490.5 | 44701 | 0.25278 | 44701 | 0.27431 | 0.51667 | Inverter started late due to Riso fault | 0.00061483 | 0.84693 | 1.8176 | Reset and Restart
Pavagada | May | Inverter-15 | RISO fault | 3542.5 | 44701 | 0.25278 | 44701 | 0.27361 | 0.5 | Inverter started late due to Riso fault | 0.0006 | 0.84693 | 1.8002 | Reset and Restart
Pavagada | May | Inverter-16 | RISO fault | 3497 | 44701 | 0.25278 | 44701 | 0.27431 | 0.51667 | Inverter started late due to Riso fault | 0.00061483 | 0.84693 | 1.821 | Reset and Restart
Pavagada | May | 7A1-3 st,6 | String fault | 13 | 44701 | 0.40972 | 44701 | 0.42569 | 0.38333 | String cable damaged inside conduit | 0.055698 | 0.84693 | 0.61325 | Rectified
Pavagada | May | 5B3-1 st,5,2 | String fault | 26 | 44701 | 0.45 | 44701 | 0.47083 | 0.5 | String cable damaged inside conduit | 0.16545 | 0.84693 | 3.6431 | Rectified
Pavagada | May | 9A3-5 st,2 | String fault | 13 | 44701 | 0.52083 | 44701 | 0.52847 | 0.18333 | String cable damaged inside conduit | 0.095924 | 0.84693 | 1.0561 | Rectified
Pavagada | May | 7A1-3 st,7 | String fault | 13 | 44701 | 0.25278 | 44701 | 0.78333 | 12.7333 | We found 11 diode failure modules in this string | 2.2055 | 0.84693 | 24.2833 | Plan to replace JB for diode failure modules
Pavagada | May | 7A3-1 st 1,4,8 | String fault | 39 | 44701 | 0.25278 | 44701 | 0.78333 | 12.7333 | We found 87 diode failure modules in this string | 2.2055 | 0.84693 | 72.8499 | Plan to replace JB for diode failure modules
Pavagada | May | Inverter-9 | RISO fault | 3477.5 | 44702 | 0.2375 | 44702 | 0.26042 | 0.55 | Inverter started late due to Riso fault | 0.0022605 | 0.82637 | 6.496 | Reset and Restart
Pavagada | May | Inverter-10 | RISO fault | 3529.5 | 44702 | 0.2375 | 44702 | 0.26181 | 0.58333 | Inverter started late due to Riso fault | 0.0024908 | 0.82637 | 7.265 | Reset and Restart
Pavagada | May | Inverter-11 | RISO fault | 3497 | 44702 | 0.2375 | 44702 | 0.27083 | 0.8 | Inverter started late due to Riso fault | 0.006952 | 0.82637 | 20.0901 | Reset and Restart
Pavagada | May | Inverter-12 | RISO fault | 3490.5 | 44702 | 0.2375 | 44702 | 0.27153 | 0.81667 | Inverter started late due to Riso fault | 0.007448 | 0.82637 | 21.4834 | Reset and Restart
Pavagada | May | Inverter-17 | RISO fault | 3477.5 | 44702 | 0.2375 | 44702 | 0.2625 | 0.6 | Inverter started late due to Riso fault | 0.002622 | 0.82637 | 7.5349 | Reset and Restart
Pavagada | May | Inverter-18 | RISO fault | 3536 | 44702 | 0.2375 | 44702 | 0.26319 | 0.61667 | Inverter started late due to Riso fault | 0.0027812 | 0.82637 | 8.1267 | Reset and Restart
Pavagada | May | Inverter 1 | RISO fault | 3484 | 44703 | 0.23958 | 44703 | 0.26944 | 0.71667 | Inverter started late due to Riso fault | 0.0089583 | 0.74444 | 23.2346 | Reset and Restart
Pavagada | May | Inverter 2 | RISO fault | 3510 | 44703 | 0.23958 | 44703 | 0.25972 | 0.48333 | Inverter started late due to Riso fault | 0.0026728 | 0.74444 | 6.9841 | Reset and Restart
Pavagada | May | Inverter 3 | RISO fault | 3526.6 | 44703 | 0.23958 | 44703 | 0.27083 | 0.75 | Inverter started late due to Riso fault | 0.009975 | 0.74444 | 26.1877 | Reset and Restart
Pavagada | May | Inverter 9 | RISO fault | 3477.5 | 44703 | 0.23958 | 44703 | 0.26458 | 0.6 | Inverter started late due to Riso fault | 0.005232 | 0.74444 | 13.5445 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44703 | 0.23958 | 44703 | 0.26458 | 0.6 | Inverter started late due to Riso fault | 0.005232 | 0.74444 | 13.7471 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44703 | 0.23958 | 44703 | 0.25625 | 0.4 | Inverter started late due to Riso fault | 0.001472 | 0.74444 | 3.8321 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44703 | 0.23958 | 44703 | 0.25625 | 0.4 | Inverter started late due to Riso fault | 0.001472 | 0.74444 | 3.8249 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44703 | 0.23958 | 44703 | 0.25833 | 0.45 | Inverter started late due to Riso fault | 0.002133 | 0.74444 | 5.6251 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3497 | 44703 | 0.23958 | 44703 | 0.25833 | 0.45 | Inverter started late due to Riso fault | 0.002133 | 0.74444 | 5.5528 | Reset and Restart
Pavagada | May | Inverter 19 Unit 3 | Island fault | 845 | 44703 | 0.47153 | 44703 | 0.48333 | 0.28333 | Inverter tripped on Island fault due to AC Breaker tripped | 0.24456 | 0.74444 | 153.8437 | Inform to Service Engineer
Pavagada | May | Inverter 19 Unit 3 | Island fault | 845 | 44703 | 0.59792 | 44703 | 0.60556 | 0.18333 | Inverter tripped on Island fault due to AC Breaker tripped | 0.16264 | 0.74444 | 102.3103 | Inform to Service Engineer
Pavagada | May | Inverter 3 | RISO fault | 3526.6 | 44704 | 0.24306 | 44704 | 0.25903 | 0.38333 | Inverter started late due to Riso fault | 0.0050983 | 0.71796 | 12.9087 | Reset and Restart
Pavagada | May | Inverter 4 | RISO fault | 3488 | 44704 | 0.24306 | 44704 | 0.25694 | 0.33333 | Inverter started late due to Riso fault | 0.0035867 | 0.71796 | 8.9818 | Reset and Restart
Pavagada | May | Inverter 19 Unit 3 | Island fault | 845 | 44704 | 0.51458 | 44704 | 0.52083 | 0.15 | Inverter tripped on Island fault due to AC Breaker tripped | 0.15356 | 0.71796 | 93.1603 | Inform to Service Engineer
Pavagada | May | Inverter 19 Unit 3 | Island fault | 845 | 44704 | 0.53472 | 44704 | 0.55 | 0.36667 | Inverter tripped on Island fault due to AC Breaker tripped | 0.30259 | 0.71796 | 183.5718 | Inform to Service Engineer
Pavagada | May | Inverter 1 | RISO fault | 3484 | 44705 | 0.23681 | 44705 | 0.26736 | 0.73333 | Inverter started late due to Riso fault | 0.014388 | 0.73174 | 36.6805 | Reset and Restart
Pavagada | May | Inverter 2 | RISO fault | 3510 | 44705 | 0.23681 | 44705 | 0.26736 | 0.73333 | Inverter started late due to Riso fault | 0.014388 | 0.73174 | 36.9542 | Reset and Restart
Pavagada | May | Inverter 3 | RISO fault | 3526.6 | 44705 | 0.23681 | 44705 | 0.25139 | 0.35 | Inverter started late due to Riso fault | 0.0012565 | 0.73174 | 3.2425 | Reset and Restart
Pavagada | May | Inverter 5 | RISO fault | 3523 | 44705 | 0.23681 | 44705 | 0.25417 | 0.41667 | Inverter started late due to Riso fault | 0.0023958 | 0.73174 | 6.1763 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44705 | 0.23681 | 44705 | 0.26111 | 0.58333 | Inverter started late due to Riso fault | 0.0072917 | 0.73174 | 18.6586 | Reset and Restart
Pavagada | May | Inverter 12 | RISO fault | 3490.5 | 44705 | 0.23681 | 44705 | 0.25972 | 0.55 | Inverter started late due to Riso fault | 0.006094 | 0.73174 | 15.5649 | Reset and Restart
Pavagada | May | Inverter 17 | RISO fault | 3477.5 | 44705 | 0.23681 | 44705 | 0.25972 | 0.55 | Inverter started late due to Riso fault | 0.006094 | 0.73174 | 15.5069 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44705 | 0.23681 | 44705 | 0.26111 | 0.58333 | Inverter started late due to Riso fault | 0.0072917 | 0.73174 | 18.8667 | Reset and Restart
Pavagada | May | Inverter 3 | RISO fault | 3526.6 | 44706 | 0.23958 | 44706 | 0.25556 | 0.38333 | Inverter started late due to Riso fault | 0.0021467 | 0.74138 | 5.6125 | Reset and Restart
Pavagada | May | Inverter 5 | RISO fault | 3523 | 44706 | 0.23958 | 44706 | 0.25486 | 0.36667 | Inverter started late due to Riso fault | 0.0018553 | 0.74138 | 4.8459 | Reset and Restart
Pavagada | May | Inverter 10 | RISO fault | 3529.5 | 44706 | 0.23958 | 44706 | 0.25556 | 0.38333 | Inverter started late due to Riso fault | 0.0021467 | 0.74138 | 5.6171 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44706 | 0.23958 | 44706 | 0.26181 | 0.53333 | Inverter started late due to Riso fault | 0.0061067 | 0.74138 | 15.8321 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44706 | 0.23958 | 44706 | 0.26667 | 0.65 | Inverter started late due to Riso fault | 0.011329 | 0.74138 | 29.7003 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44706 | 0.23958 | 44706 | 0.27222 | 0.78333 | Inverter started late due to Riso fault | 0.020155 | 0.74138 | 52.9803 | Reset and Restart
Pavagada | May | Inverter 4 | Ground fault | 3488 | 44706 | 0.25139 | 44706 | 0.28056 | 0.7 | Inverter tripped due to Ground fault | 0.037352 | 0.74138 | 96.5892 | Fault identification in 2B4-4 ,2B2-1 SMB
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44707 | 0.24167 | 44707 | 0.25833 | 0.4 | Inverter started late due to Riso fault | 0.004596 | 0.74011 | 11.8952 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44708 | 0.24167 | 44708 | 0.26181 | 0.48333 | Inverter started late due to Riso fault | 0.0061238 | 0.73112 | 15.8315 | Reset and Restart
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44709 | 0.24097 | 44709 | 0.27014 | 0.7 | Inverter started late due to Riso fault | 0.018662 | 0.73843 | 48.1907 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44709 | 0.24097 | 44709 | 0.25764 | 0.4 | Inverter started late due to Riso fault | 0.004068 | 0.73843 | 10.6414 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44709 | 0.24097 | 44709 | 0.2625 | 0.51667 | Inverter started late due to Riso fault | 0.0081323 | 0.73843 | 21.2343 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44709 | 0.24097 | 44709 | 0.26389 | 0.55 | Inverter started late due to Riso fault | 0.009647 | 0.73843 | 25.2576 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44710 | 0.24097 | 44710 | 0.25833 | 0.41667 | Inverter started late due to Riso fault | 0.0045625 | 0.73195 | 11.8302 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44710 | 0.24097 | 44710 | 0.26389 | 0.55 | Inverter started late due to Riso fault | 0.009845 | 0.73195 | 25.4805 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44710 | 0.24097 | 44710 | 0.26944 | 0.68333 | Inverter started late due to Riso fault | 0.017979 | 0.73195 | 46.6576 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44711 | 0.24306 | 44711 | 0.26528 | 0.53333 | Inverter started late due to Riso fault | 0.0095093 | 0.72381 | 24.3829 | Reset and Restart
Pavagada | May | Inverter 17 | RISO fault | 3477.5 | 44711 | 0.24306 | 44711 | 0.25833 | 0.36667 | Inverter started late due to Riso fault | 0.0034137 | 0.72381 | 8.5924 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44711 | 0.24306 | 44711 | 0.25903 | 0.38333 | Inverter started late due to Riso fault | 0.0038525 | 0.72381 | 9.8601 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44711 | 0.24306 | 44711 | 0.25903 | 0.38333 | Inverter started late due to Riso fault | 0.0038525 | 0.72381 | 9.8869 | Reset and Restart
Pavagada | May | Inverter 12 Unit 1 | L - Over temp fault | 962 | 44711 | 0.52292 | 44711 | 0.53264 | 0.23333 | Inverter tripped on Island fault due to L-Over temp fault | 0.2453 | 0.72381 | 170.8017 | Inform to Service Engineer
Pavagada | May | 5B2-2 st 2 | String fault | 13 | 44711 | 0.45486 | 44711 | 0.46875 | 0.33333 | string cable damaged | 0.33505 | 0.72381 | 3.1527 | Rectified
Pavagada | May | 5A1-5 st 1 | String fault | 13 | 44711 | 0.47569 | 44711 | 0.48611 | 0.25 | string cable damaged | 0.26505 | 0.72381 | 2.494 | Rectified
Pavagada | May | 5B3-3 st 8 | String fault | 13 | 44711 | 0.49861 | 44711 | 0.51389 | 0.36667 | Inside conduit cables are short circuit | 0.38766 | 0.72381 | 3.6477 | Rectified
Pavagada | May | Inverter 11 | RISO fault | 3497 | 44712 | 0.24375 | 44712 | 0.26458 | 0.5 | Inverter started late due to Riso fault | 0.00581 | 0.75695 | 15.3793 | Reset and Restart
Pavagada | May | Inverter 15 | RISO fault | 3542.5 | 44712 | 0.24375 | 44712 | 0.27083 | 0.65 | Inverter started late due to Riso fault | 0.011069 | 0.75695 | 29.6827 | Reset and Restart
Pavagada | May | Inverter 16 | RISO fault | 3497 | 44712 | 0.24375 | 44712 | 0.26042 | 0.4 | Inverter started late due to Riso fault | 0.003336 | 0.75695 | 8.8305 | Reset and Restart
Pavagada | May | Inverter 18 | RISO fault | 3536 | 44712 | 0.24375 | 44712 | 0.26528 | 0.51667 | Inverter started late due to Riso fault | 0.006293 | 0.75695 | 16.8436 | Reset and Restart
Pavagada | May | Inverter 20 | RISO fault | 3545.6 | 44712 | 0.24375 | 44712 | 0.27153 | 0.66667 | Inverter started late due to Riso fault | 0.011773 | 0.75695 | 31.5977 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44713 | 0.24375 | 44713 | 0.26042 | 0.4 | Inverter started late due to Riso fault | 0.003396 | 0.7426 | 8.8681 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44713 | 0.24375 | 44713 | 0.26389 | 0.48333 | Inverter started late due to Riso fault | 0.005133 | 0.7426 | 13.3297 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44713 | 0.24375 | 44713 | 0.26458 | 0.5 | Inverter started late due to Riso fault | 0.00552 | 0.7426 | 14.3614 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44713 | 0.24375 | 44713 | 0.27083 | 0.65 | Inverter started late due to Riso fault | 0.0092235 | 0.7426 | 24.2638 | Reset and Restart
Pavagada | June | 10A2-4 st 9,10,11,12,13 | String fault | 65 | 44713 | 0.62222 | 44713 | 0.66111 | 0.93333 | Inside conduit, cables are short circuited | 0.56564 | 0.7426 | 27.3027 | Rectified
Pavagada | June | 10A2-5 st 1,2,3 | String fault | 39 | 44713 | 0.62222 | 44713 | 0.67708 | 1.3167 | Inside conduit, cables are short circuited | 0.71226 | 0.7426 | 20.6281 | Rectified
Pavagada | June | Inverter 2 | RISO fault | 3510 | 44714 | 0.2375 | 44714 | 0.25347 | 0.38333 | Inverter started late due to Riso fault | 0.001725 | 0.7427 | 4.4968 | Reset and Restart
Pavagada | June | Inverter 3 | RISO fault | 3526.6 | 44714 | 0.2375 | 44714 | 0.25347 | 0.38333 | Inverter started late due to Riso fault | 0.001725 | 0.7427 | 4.5181 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44714 | 0.2375 | 44714 | 0.27292 | 0.85 | Inverter started late due to Riso fault | 0.024412 | 0.7427 | 63.403 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44714 | 0.2375 | 44714 | 0.26667 | 0.7 | Inverter started late due to Riso fault | 0.013979 | 0.7427 | 36.7113 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44714 | 0.2375 | 44714 | 0.26111 | 0.56667 | Inverter started late due to Riso fault | 0.0069473 | 0.7427 | 18.2944 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44715 | 0.23819 | 44715 | 0.25764 | 0.46667 | Inverter started late due to Riso fault | 0.0025807 | 0.7189 | 6.4878 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44715 | 0.23819 | 44715 | 0.25694 | 0.45 | Inverter started late due to Riso fault | 0.0023175 | 0.7189 | 5.902 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44715 | 0.23819 | 44715 | 0.25694 | 0.45 | Inverter started late due to Riso fault | 0.0023175 | 0.7189 | 5.8262 | Reset and Restart
Pavagada | June | Inverter 3 | RISO fault | 3526.6 | 44716 | 0.23819 | 44716 | 0.25417 | 0.38333 | Inverter started late due to Riso fault | 0.0018055 | 0.72287 | 4.6027 | Reset and Restart
Pavagada | June | Inverter 5 | RISO fault | 3523 | 44716 | 0.23819 | 44716 | 0.26111 | 0.55 | Inverter started late due to Riso fault | 0.0057695 | 0.72287 | 14.693 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44716 | 0.23819 | 44716 | 0.2625 | 0.58333 | Inverter started late due to Riso fault | 0.0069008 | 0.72287 | 17.6714 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44716 | 0.23819 | 44716 | 0.26111 | 0.55 | Inverter started late due to Riso fault | 0.0057695 | 0.72287 | 14.5845 | Reset and Restart
Pavagada | June | 5A4-4 st 13 | String fault | 13 | 44716 | 0.43333 | 44716 | 0.44444 | 0.26667 | Inside conduit cables are short circuit | 0.21978 | 0.72287 | 2.0654 | Rectified
Pavagada | June | 4A4-2 st 7 | String fault | 13 | 44716 | 0.4625 | 44716 | 0.47431 | 0.28333 | Inside conduit cables are short circuit | 0.25221 | 0.72287 | 2.3701 | Rectified
Pavagada | June | 1B3-5 st 1 | String fault | 13 | 44716 | 0.48958 | 44716 | 0.49931 | 0.23333 | Inside conduit cables are short circuit | 0.20949 | 0.72287 | 1.9687 | Rectified
Pavagada | June | 1B3-1 st 13 | String fault | 13 | 44716 | 0.50694 | 44716 | 0.52153 | 0.35 | Inside conduit cables are short circuit | 0.31375 | 0.72287 | 2.9484 | Rectified
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44717 | 0.23681 | 44717 | 0.25278 | 0.38333 | Inverter started late due to Riso fault | 0.0012573 | 0.72237 | 3.2175 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44717 | 0.23681 | 44717 | 0.25486 | 0.43333 | Inverter started late due to Riso fault | 0.001937 | 0.72237 | 4.8931 | Reset and Restart
Pavagada | June | 4B1-3 st 6 | String fault | 13 | 44717 | 0.34375 | 44717 | 0.36042 | 0.4 | string cable damaged | 0.17648 | 0.72237 | 1.6573 | Rectified
Pavagada | June | 7B2-2 st 9 | String fault | 13 | 44717 | 0.37569 | 44717 | 0.39028 | 0.35 | string cable damaged | 0.20282 | 0.72237 | 1.9047 | Rectified
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44718 | 0.24792 | 44718 | 0.26667 | 0.45 | Inverter started late due to Riso fault | 0.0021015 | 0.77589 | 5.7338 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44718 | 0.24792 | 44718 | 0.26806 | 0.48333 | Inverter started late due to Riso fault | 0.0024602 | 0.77589 | 6.7372 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44718 | 0.24792 | 44718 | 0.27361 | 0.61667 | Inverter started late due to Riso fault | 0.004366 | 0.77589 | 11.8462 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44718 | 0.24792 | 44718 | 0.27778 | 0.71667 | Inverter started late due to Riso fault | 0.0064428 | 0.77589 | 17.5138 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44718 | 0.24792 | 44718 | 0.28264 | 0.83333 | Inverter started late due to Riso fault | 0.0099167 | 0.77589 | 27.2569 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44718 | 0.24792 | 44718 | 0.26597 | 0.43333 | Inverter started late due to Riso fault | 0.0019327 | 0.77589 | 5.2439 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44718 | 0.24792 | 44718 | 0.26597 | 0.43333 | Inverter started late due to Riso fault | 0.0019327 | 0.77589 | 5.2147 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44718 | 0.24792 | 44718 | 0.29167 | 1.05 | Inverter started late due to Riso fault | 0.020055 | 0.77589 | 55.022 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44718 | 0.24792 | 44718 | 0.29028 | 1.0167 | Inverter started late due to Riso fault | 0.018127 | 0.77589 | 49.8679 | Reset and Restart
Pavagada | June | 5B4-5 S1 | String fault | 13 | 44718 | 0.36111 | 44718 | 0.44583 | 2.0333 | string cable damaged | 1.4302 | 0.77589 | 14.4263 | Rectified
Pavagada | June | 6B4-2 S5 | String fault | 13 | 44718 | 0.375 | 44718 | 0.45833 | 2 | string cable damaged | 1.4643 | 0.77589 | 14.7698 | Rectified
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44719 | 0.24375 | 44719 | 0.26458 | 0.5 | Inverter started late due to Riso fault | 0.002125 | 0.74736 | 5.5537 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44719 | 0.24375 | 44719 | 0.26042 | 0.4 | Inverter started late due to Riso fault | 0.001248 | 0.74736 | 3.2677 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44719 | 0.24375 | 44719 | 0.26875 | 0.6 | Inverter started late due to Riso fault | 0.003402 | 0.74736 | 9.0069 | Reset and Restart
Pavagada | June | 3B2-4 st 10 | String fault | 13 | 44719 | 0.44097 | 44719 | 0.45903 | 0.43333 | string cable damaged | 0.35653 | 0.74736 | 3.4639 | Rectified
Pavagada | June | 8A1-4 st 10 | String fault | 13 | 44719 | 0.47847 | 44719 | 0.49861 | 0.48333 | string cable short circuit | 0.42775 | 0.74736 | 4.1559 | Rectified
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44720 | 0.24167 | 44720 | 0.275 | 0.8 | Inverter started late due to Riso fault | 0.022768 | 0.75197 | 60.4279 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44720 | 0.24167 | 44720 | 0.25694 | 0.36667 | Inverter started late due to Riso fault | 0.002992 | 0.75197 | 7.8679 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44720 | 0.24167 | 44720 | 0.25903 | 0.41667 | Inverter started late due to Riso fault | 0.0041583 | 0.75197 | 10.9552 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44720 | 0.24167 | 44720 | 0.25625 | 0.35 | Inverter started late due to Riso fault | 0.002653 | 0.75197 | 7.0672 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44720 | 0.24167 | 44720 | 0.26319 | 0.51667 | Inverter started late due to Riso fault | 0.0072643 | 0.75197 | 19.3156 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44720 | 0.24167 | 44720 | 0.26875 | 0.65 | Inverter started late due to Riso fault | 0.013143 | 0.75197 | 35.0416 | Reset and Restart
Pavagada | June | 8A2-1 st 9 | String fault | 13 | 44720 | 0.45139 | 44720 | 0.46667 | 0.36667 | string cable damaged | 0.3246 | 0.75197 | 3.1732 | Rectified
Pavagada | June | 3B2-4 st 4 | String fault | 13 | 44720 | 0.48889 | 44720 | 0.49722 | 0.2 | string cable damaged | 0.18961 | 0.75197 | 1.8535 | Rectified
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44721 | 0.24306 | 44721 | 0.26042 | 0.41667 | Inverter started late due to Riso fault | 0.0052167 | 0.75409 | 13.9357 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44721 | 0.24306 | 44721 | 0.25972 | 0.4 | Inverter started late due to Riso fault | 0.004728 | 0.75409 | 12.6071 | Reset and Restart
Pavagada | June | 5A1-4 st,7 | String fault | 13 | 44721 | 0.44167 | 44721 | 0.45347 | 0.28333 | string cable damaged | 0.25216 | 0.75409 | 2.472 | Rectified
Pavagada | June | 7B1-2 st,2 | String fault | 13 | 44721 | 0.48889 | 44721 | 0.50208 | 0.31667 | string cable damaged | 0.2994 | 0.75409 | 2.9351 | Rectified
Pavagada | June | 10B3-4 st,4 | String fault | 13 | 44721 | 0.63194 | 44721 | 0.64444 | 0.3 | string cable damaged | 0.19185 | 0.75409 | 1.8808 | Rectified
Pavagada | June | 10A4-2 st,12 | String fault | 13 | 44721 | 0.66111 | 44721 | 0.67639 | 0.36667 | string cable damaged | 0.15542 | 0.75409 | 1.5236 | Rectified
Pavagada | June | Inverter 3 | RISO fault | 3526.6 | 44722 | 0.24444 | 44722 | 0.25903 | 0.35 | Inverter started late due to Riso fault | 0.004473 | 0.74929 | 11.8197 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44722 | 0.24444 | 44722 | 0.26528 | 0.5 | Inverter started late due to Riso fault | 0.01053 | 0.74929 | 27.8992 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44722 | 0.24444 | 44722 | 0.27222 | 0.66667 | Inverter started late due to Riso fault | 0.0207 | 0.74929 | 54.9935 | Reset and Restart
Pavagada | June | Inverter 2 Unit 1 | L - Over temp fault | 968.5 | 44722 | 0.51181 | 44722 | 0.52292 | 0.26667 | Inverter unit 1 tripped on L Over temp fault | 0.27 | 0.74929 | 195.938 | Inform to Service Engineer
Pavagada | June | Inverter 12 Unit 1 | L - Over temp fault | 962 | 44722 | 0.53056 | 44722 | 0.53889 | 0.2 | Inverter unit 1 tripped on L Over temp fault | 0.20116 | 0.74929 | 145.0014 | Inform to Service Engineer
Pavagada | June | Inverter 2 Unit 1 | L - Over temp fault | 968.5 | 44723 | 0.54097 | 44723 | 0.55278 | 0.28333 | Inverter unit 1 tripped on L Over temp fault | 0.28577 | 0.74239 | 205.4681 | Inform to Service Engineer
Pavagada | June | Inverter 7 | RISO fault | 3479.5 | 44724 | 0.24236 | 44724 | 0.26319 | 0.5 | Inverter started late due to Riso fault | 0.00721 | 0.77893 | 19.5411 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44724 | 0.24236 | 44724 | 0.26667 | 0.58333 | Inverter started late due to Riso fault | 0.010337 | 0.77893 | 28.1562 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44724 | 0.24236 | 44724 | 0.27153 | 0.7 | Inverter started late due to Riso fault | 0.015967 | 0.77893 | 44.0586 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44724 | 0.24236 | 44724 | 0.25764 | 0.36667 | Inverter started late due to Riso fault | 0.0034173 | 0.77893 | 9.4123 | Reset and Restart
Pavagada | June | Inverter 1 | RISO fault | 3484 | 44725 | 0.24167 | 44725 | 0.25833 | 0.4 | Inverter started late due to Riso fault | 0.002912 | 0.73655 | 7.4726 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44725 | 0.24167 | 44725 | 0.2625 | 0.5 | Inverter started late due to Riso fault | 0.004665 | 0.73655 | 12.0157 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44725 | 0.24167 | 44725 | 0.26667 | 0.6 | Inverter started late due to Riso fault | 0.001182 | 0.73655 | 3.0841 | Reset and Restart
Pavagada | June | Inverter 19 | RISO fault | 3507.2 | 44725 | 0.24167 | 44725 | 0.25972 | 0.43333 | Inverter started late due to Riso fault | 0.03367 | 0.73655 | 86.9773 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44725 | 0.24167 | 44725 | 0.25833 | 0.4 | Inverter started late due to Riso fault | 0.003564 | 0.73655 | 9.3074 | Reset and Restart
Pavagada | June | 9a4-6 St,1,4 | String fault | 13 | 44725 | 0.45139 | 44725 | 0.47222 | 0.5 | string cable damaged | 0.45254 | 0.73655 | 4.3331 | Rectified
Pavagada | June | 9B1-1 st,13 | String fault | 13 | 44725 | 0.48264 | 44725 | 0.49444 | 0.28333 | string cable damaged | 0.2975 | 0.73655 | 2.8486 | Rectified
Pavagada | June | Inverter 1 | RISO fault | 3484 | 44726 | 0.24444 | 44726 | 0.25278 | 0.2 | Inverter started late due to Riso fault | 0.000724 | 0.74155 | 1.8705 | Reset and Restart
Pavagada | June | Inverter 3 | RISO fault | 3526.6 | 44726 | 0.24444 | 44726 | 0.25625 | 0.28333 | Inverter started late due to Riso fault | 0.0016235 | 0.74155 | 4.2457 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44726 | 0.24444 | 44726 | 0.25486 | 0.25 | Inverter started late due to Riso fault | 0.0012075 | 0.74155 | 3.1313 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44726 | 0.24444 | 44726 | 0.25347 | 0.21667 | Inverter started late due to Riso fault | 0.000871 | 0.74155 | 2.2545 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44726 | 0.24444 | 44726 | 0.25903 | 0.35 | Inverter started late due to Riso fault | 0.0027965 | 0.74155 | 7.3462 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44726 | 0.24444 | 44726 | 0.26667 | 0.53333 | Inverter started late due to Riso fault | 0.009296 | 0.74155 | 24.3751 | Reset and Restart
Pavagada | June | Inverter 19 | RISO fault | 3507.2 | 44726 | 0.24444 | 44726 | 0.25208 | 0.18333 | Inverter started late due to Riso fault | 0.000594 | 0.74155 | 1.5448 | Reset and Restart
Pavagada | June | Inverter 12 Unit 1 | L - Over temp fault | 962 | 44726 | 0.48958 | 44726 | 0.5 | 0.25 | Inverter unit 1 tripped on L Over temp fault | 0.26205 | 0.74155 | 186.9399 | Inform to Service Engineer
Pavagada | June | Inverter 12 Unit 1 | L - Over temp fault | 962 | 44726 | 0.59028 | 44726 | 0.60069 | 0.25 | Inverter unit 1 tripped on L Over temp fault | 0.18557 | 0.74155 | 132.3779 | Inform to Service Engineer
Pavagada | June | Inverter 2 Unit 1 | L - Over temp fault | 968.5 | 44726 | 0.50764 | 44726 | 0.51875 | 0.26667 | Inverter unit 1 tripped on L Over temp fault | 0.27722 | 0.74155 | 199.0951 | Inform to Service Engineer
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44727 | 0.25556 | 44727 | 0.275 | 0.46667 | Inverter started late due to Riso fault | 0.0019413 | 0.83071 | 5.6919 | Reset and Restart
Pavagada | June | Inverter 11 | RISO fault | 3497 | 44727 | 0.25556 | 44727 | 0.28472 | 0.7 | Inverter started late due to Riso fault | 0.004144 | 0.83071 | 12.0382 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44727 | 0.25556 | 44727 | 0.27986 | 0.58333 | Inverter started late due to Riso fault | 0.0029458 | 0.83071 | 8.6689 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44727 | 0.25556 | 44727 | 0.28958 | 0.81667 | Inverter started late due to Riso fault | 0.0054472 | 0.83071 | 15.7357 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44727 | 0.25556 | 44727 | 0.28958 | 0.81667 | Inverter started late due to Riso fault | 0.0054472 | 0.83071 | 16.0004 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44727 | 0.25556 | 44727 | 0.29167 | 0.86667 | Inverter started late due to Riso fault | 0.006032 | 0.83071 | 17.7664 | Reset and Restart
Pavagada | June | 6A1-1 st,11 | String fault | 13 | 44727 | 0.44028 | 44727 | 0.45347 | 0.31667 | string cable damaged | 0.13774 | 0.83071 | 1.4875 | Rectified
Pavagada | June | 6B3-2 st,12 | String fault | 13 | 44727 | 0.46111 | 44727 | 0.47431 | 0.31667 | string cable damaged | 0.13457 | 0.83071 | 1.4532 | Rectified
Pavagada | June | 6A3-4 st,13 | String fault | 13 | 44727 | 0.48681 | 44727 | 0.49722 | 0.25 | string cable damaged | 0.11563 | 0.83071 | 1.2487 | Rectified
Pavagada | June | 2A1-3 st,10 | String fault | 13 | 44727 | 0.5125 | 44727 | 0.52292 | 0.25 | string cable damaged | 0.11691 | 0.83071 | 1.2626 | Rectified
Pavagada | June | 2A3-2 st,1 | String fault | 13 | 44727 | 0.53403 | 44727 | 0.54653 | 0.3 | string cable damaged | 0.085659 | 0.83071 | 0.92505 | Rectified
Pavagada | June | 2A4-3 st,10 | String fault | 13 | 44727 | 0.55833 | 44727 | 0.57083 | 0.3 | string cable damaged | 0.079602 | 0.83071 | 0.85964 | Rectified
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44728 | 0.24444 | 44728 | 0.25972 | 0.36667 | Inverter started late due to Riso fault | 0.004015 | 0.75807 | 10.7426 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44728 | 0.24444 | 44728 | 0.26181 | 0.41667 | Inverter started late due to Riso fault | 0.005525 | 0.75807 | 14.6194 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44728 | 0.24444 | 44728 | 0.26389 | 0.46667 | Inverter started late due to Riso fault | 0.00735 | 0.75807 | 19.5209 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44728 | 0.24444 | 44728 | 0.26667 | 0.53333 | Inverter started late due to Riso fault | 0.010309 | 0.75807 | 27.6854 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44728 | 0.24444 | 44728 | 0.26111 | 0.4 | Inverter started late due to Riso fault | 0.004992 | 0.75807 | 13.1599 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44728 | 0.24444 | 44728 | 0.27639 | 0.76667 | Inverter started late due to Riso fault | 0.026442 | 0.75807 | 70.8799 | Reset and Restart
Pavagada | June | Inverter 19 | RISO fault | 3507.2 | 44728 | 0.24444 | 44728 | 0.27639 | 0.76667 | Inverter started late due to Riso fault | 0.026442 | 0.75807 | 70.3026 | Reset and Restart
Pavagada | June | Inverter 20 | RISO fault | 3545.6 | 44728 | 0.24444 | 44728 | 0.27778 | 0.8 | Inverter started late due to Riso fault | 0.029576 | 0.75807 | 79.4951 | Reset and Restart
Pavagada | June | 10A1-4 st 11 | String fault | 13 | 44728 | 0.4375 | 44728 | 0.44931 | 0.28333 | string cable damaged | 0.19566 | 0.75807 | 1.9283 | Rectified
Pavagada | June | 10A1-5 st 1 | String fault | 13 | 44728 | 0.45972 | 44728 | 0.47153 | 0.28333 | string cable damaged | 0.24508 | 0.75807 | 2.4153 | Rectified
Pavagada | June | 10A2-2 st 1 | String fault | 13 | 44728 | 0.48403 | 44728 | 0.50069 | 0.4 | string cable damaged | 0.36267 | 0.75807 | 3.5741 | Rectified
Pavagada | June | 10A2-5 st 2 | String fault | 13 | 44728 | 0.51667 | 44728 | 0.53472 | 0.43333 | string cable damaged | 0.23209 | 0.75807 | 2.2872 | Rectified
Pavagada | June | 10A1-3 st 5 | String fault | 13 | 44728 | 0.41389 | 44728 | 0.42986 | 0.38333 | string cable damaged | 0.29693 | 0.75807 | 2.9263 | Rectified
Pavagada | June | Inverter 4 | RISO fault | 3488 | 44729 | 0.25069 | 44729 | 0.26736 | 0.4 | Inverter started late due to Riso fault | 0.001528 | 0.74813 | 3.9873 | Reset and Restart
Pavagada | June | Inverter 7 | RISO fault | 3479.5 | 44729 | 0.25069 | 44729 | 0.27639 | 0.61667 | Inverter started late due to Riso fault | 0.0041378 | 0.74813 | 10.7713 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44729 | 0.25069 | 44729 | 0.27639 | 0.61667 | Inverter started late due to Riso fault | 0.0041378 | 0.74813 | 10.9261 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44729 | 0.25069 | 44729 | 0.27708 | 0.63333 | Inverter started late due to Riso fault | 0.00418 | 0.74813 | 10.9155 | Reset and Restart
Pavagada | June | Inverter 14 | RISO fault | 3503.5 | 44729 | 0.25069 | 44729 | 0.27361 | 0.55 | Inverter started late due to Riso fault | 0.0031295 | 0.74813 | 8.2027 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44729 | 0.25069 | 44729 | 0.26597 | 0.36667 | Inverter started late due to Riso fault | 0.0013017 | 0.74813 | 3.3865 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44729 | 0.25069 | 44729 | 0.26667 | 0.38333 | Inverter started late due to Riso fault | 0.0013992 | 0.74813 | 3.7013 | Reset and Restart
Pavagada | June | Inverter 14 | Ground fault | 3503.5 | 44729 | 0.43333 | 44729 | 0.44722 | 0.33333 | Inverter tripped on Ground gault of 7B2-1 | 0.23178 | 0.74813 | 607.5135 | Rectified
Pavagada | June | 4A2-1 st13 | String fault | 13 | 44729 | 0.37778 | 44729 | 0.39444 | 0.4 | String cable damaged | 0.23388 | 0.74813 | 2.2746 | Rectified
Pavagada | June | 4A1-5 st 4 | String fault | 13 | 44729 | 0.41111 | 44729 | 0.42361 | 0.3 | String cable damaged | 0.10683 | 0.74813 | 1.039 | Rectified
Pavagada | June | 7B2-1 st 10 | String fault | 13 | 44729 | 0.44722 | 44729 | 0.46875 | 0.51667 | String cable damaged | 0.36343 | 0.74813 | 3.5346 | Rectified
Pavagada | June | Inverter 1 | RISO fault | 3484 | 44730 | 0.24306 | 44730 | 0.26181 | 0.45 | Inverter started late due to Riso fault | 0.003582 | 0.7952 | 9.9239 | Reset and Restart
Pavagada | June | Inverter 9 | RISO fault | 3477.5 | 44730 | 0.24306 | 44730 | 0.27153 | 0.68333 | Inverter started late due to Riso fault | 0.010851 | 0.7952 | 30.0074 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44730 | 0.24306 | 44730 | 0.26944 | 0.63333 | Inverter started late due to Riso fault | 0.0087337 | 0.7952 | 24.5125 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44730 | 0.24306 | 44730 | 0.26319 | 0.48333 | Inverter started late due to Riso fault | 0.0043307 | 0.7952 | 12.1995 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44730 | 0.24306 | 44730 | 0.26458 | 0.51667 | Inverter started late due to Riso fault | 0.0051408 | 0.7952 | 14.2957 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44730 | 0.24306 | 44730 | 0.27222 | 0.7 | Inverter started late due to Riso fault | 0.011655 | 0.7952 | 32.2298 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44730 | 0.24306 | 44730 | 0.27361 | 0.73333 | Inverter started late due to Riso fault | 0.013295 | 0.7952 | 37.3843 | Reset and Restart
Pavagada | June | 2A3-5 st,3,8,10 | String fault | 39 | 44730 | 0.43056 | 44730 | 0.46042 | 0.71667 | String cable damaged | 0.62298 | 0.7952 | 19.3203 | Rectified
Pavagada | June | 2A3-5 st,11,12 | String fault | 26 | 44730 | 0.47083 | 44730 | 0.49514 | 0.58333 | String cable damaged | 0.29201 | 0.7952 | 6.0374 | Rectified
Pavagada | June | Inverter 1 | RISO fault | 3484 | 44731 | 0.24028 | 44731 | 0.25903 | 0.45 | Inverter started late due to Riso fault | 0.003114 | 0.80481 | 8.7315 | Reset and Restart
Pavagada | June | Inverter 9 | RISO fault | 3477.5 | 44731 | 0.24028 | 44731 | 0.25556 | 0.36667 | Inverter started late due to Riso fault | 0.0015547 | 0.80481 | 4.3511 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44731 | 0.24028 | 44731 | 0.26667 | 0.63333 | Inverter started late due to Riso fault | 0.008493 | 0.80481 | 24.125 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44731 | 0.24028 | 44731 | 0.26597 | 0.61667 | Inverter started late due to Riso fault | 0.007881 | 0.80481 | 22.0568 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44731 | 0.24028 | 44731 | 0.26597 | 0.61667 | Inverter started late due to Riso fault | 0.007881 | 0.80481 | 22.4278 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44732 | 0.24792 | 44732 | 0.26458 | 0.4 | Inverter started late due to Riso fault | 0.005744 | 0.79705 | 16.0993 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44732 | 0.24792 | 44732 | 0.26528 | 0.41667 | Inverter started late due to Riso fault | 0.0063292 | 0.79705 | 17.6083 | Reset and Restart
Pavagada | June | Inverter 16 | RISO fault | 3497 | 44732 | 0.24792 | 44732 | 0.26458 | 0.4 | Inverter started late due to Riso fault | 0.005744 | 0.79705 | 16.0101 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44732 | 0.24792 | 44732 | 0.27083 | 0.55 | Inverter started late due to Riso fault | 0.012221 | 0.79705 | 33.8733 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44732 | 0.24792 | 44732 | 0.27014 | 0.53333 | Inverter started late due to Riso fault | 0.011355 | 0.79705 | 32.0015 | Reset and Restart
Pavagada | June | 10B2-1 st 4 | String fault | 13 | 44732 | 0.43403 | 44732 | 0.45069 | 0.4 | String cable damaged | 0.20532 | 0.79705 | 2.1275 | Rectified
Pavagada | June | 7B3-4 st 11 | String fault | 13 | 44732 | 0.46667 | 44732 | 0.47986 | 0.31667 | String cable damaged | 0.21377 | 0.79705 | 2.215 | Rectified
Pavagada | June | 7B4-3 st 5 | String fault | 13 | 44732 | 0.48958 | 44732 | 0.50486 | 0.36667 | String cable damaged | 0.25715 | 0.79705 | 2.6645 | Rectified
Pavagada | June | 5B4-1 st 6 | String fault | 13 | 44732 | 0.52014 | 44732 | 0.53333 | 0.31667 | String cable damaged | 0.26644 | 0.79705 | 2.7607 | Rectified
Pavagada | June | 5A3-5 st 5 | String fault | 13 | 44732 | 0.54444 | 44732 | 0.55972 | 0.36667 | String cable damaged | 0.24288 | 0.79705 | 2.5166 | Rectified
Pavagada | June | Inverter-1 | RISO fault | 3484 | 44733 | 0.24028 | 44733 | 0.25833 | 0.43333 | Inverter started late due to Riso fault | 0.0024787 | 0.80168 | 6.923 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44733 | 0.24028 | 44733 | 0.26667 | 0.63333 | Inverter started late due to Riso fault | 0.008189 | 0.80168 | 23.171 | Reset and Restart
Pavagada | June | Inverter -17 | RISO fault | 3477.5 | 44733 | 0.24028 | 44733 | 0.25972 | 0.46667 | Inverter started late due to Riso fault | 0.0031733 | 0.80168 | 8.8467 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44733 | 0.24028 | 44733 | 0.26181 | 0.51667 | Inverter started late due to Riso fault | 0.0043917 | 0.80168 | 12.4492 | Reset and Restart
Pavagada | June | 8A4-3 st,13 | String fault | 13 | 44733 | 0.42708 | 44733 | 0.43611 | 0.21667 | String cable damaged | 0.18595 | 0.80168 | 1.9379 | Rectified
Pavagada | June | 4A1-5 st 4 | String fault | 13 | 44733 | 0.47153 | 44733 | 0.48125 | 0.23333 | String cable damaged | 0.14926 | 0.80168 | 1.5555 | Rectified
Pavagada | June | 10B2-1 St,2 | String fault | 13 | 44733 | 0.51806 | 44733 | 0.52778 | 0.23333 | String cable damaged | 0.10766 | 0.80168 | 1.122 | Rectified
Pavagada | June | Inverter 1 | RISO fault | 3484 | 44734 | 0.24028 | 44734 | 0.25625 | 0.38333 | Inverter started late due to Riso fault | 0.0034998 | 0.75182 | 9.1673 | Reset and Restart
Pavagada | June | Inverter 4 | RISO fault | 3488 | 44734 | 0.24028 | 44734 | 0.25694 | 0.4 | Inverter started late due to Riso fault | 0.003908 | 0.75182 | 10.2482 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44734 | 0.24028 | 44734 | 0.26458 | 0.58333 | Inverter started late due to Riso fault | 0.010179 | 0.75182 | 26.9116 | Reset and Restart
Pavagada | June | Inverter 10 | RISO fault | 3529.5 | 44734 | 0.24028 | 44734 | 0.26389 | 0.56667 | Inverter started late due to Riso fault | 0.0094803 | 0.75182 | 25.1567 | Reset and Restart
Pavagada | June | Inverter 17 | RISO fault | 3477.5 | 44734 | 0.24028 | 44734 | 0.25833 | 0.43333 | Inverter started late due to Riso fault | 0.0048013 | 0.75182 | 12.5529 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44734 | 0.24028 | 44734 | 0.25972 | 0.46667 | Inverter started late due to Riso fault | 0.0058053 | 0.75182 | 15.4332 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44735 | 0.24583 | 44735 | 0.26319 | 0.41667 | Inverter started late due to Riso fault | 0.0045458 | 0.76103 | 12.1654 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44735 | 0.24583 | 44735 | 0.26389 | 0.43333 | Inverter started late due to Riso fault | 0.0050007 | 0.76103 | 13.2837 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44735 | 0.24583 | 44735 | 0.26111 | 0.36667 | Inverter started late due to Riso fault | 0.003256 | 0.76103 | 8.7781 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44736 | 0.24653 | 44736 | 0.26319 | 0.4 | Inverter started late due to Riso fault | 0.005224 | 0.75671 | 13.9009 | Reset and Restart
Pavagada | June | Inverter 12 | RISO fault | 3490.5 | 44737 | 0.24653 | 44737 | 0.2625 | 0.38333 | Inverter started late due to Riso fault | 0.0053858 | 0.79632 | 14.9703 | Reset and Restart
Pavagada | June | Inverter 18 | RISO fault | 3536 | 44737 | 0.24653 | 44737 | 0.27083 | 0.58333 | Inverter started late due to Riso fault | 0.013953 | 0.79632 | 39.2898 | Reset and Restart
Pavagada | June | 9B1-3 st 6 | String fault | 13 | 44737 | 0.46875 | 44737 | 0.47847 | 0.23333 | String cable damaged | 0.097603 | 0.79632 | 1.0104 | Rectified
Pavagada | June | 9B1-6 st 4,5,6 | String fault | 39 | 44737 | 0.49097 | 44737 | 0.51667 | 0.61667 | String cable damaged | 0.3319 | 0.79632 | 10.3076 | Rectified
Pavagada | June | 9B2-1 st 11,12 | String fault | 26 | 44737 | 0.52847 | 44737 | 0.54792 | 0.46667 | String cable damaged | 0.21354 | 0.79632 | 4.4212 | Rectified
Pavagada | June | 9B3-3 st 7,13 | String fault | 26 | 44737 | 0.62778 | 44737 | 0.65417 | 0.63333 | String cable damaged | 0.33878 | 0.79632 | 7.0142 | Rectified
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44738 | 0.23958 | 44738 | 0.25694 | 0.41667 | Inverter started late due to Riso fault | 0.0022417 | 0.76982 | 6.0684 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3490.5 | 44739 | 0.24236 | 44739 | 0.26319 | 0.5 | Inverter started late due to Riso fault | 0.00283 | 0.80716 | 7.9733 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3542.5 | 44739 | 0.24236 | 44739 | 0.26528 | 0.55 | Inverter started late due to Riso fault | 0.0038775 | 0.80716 | 11.0872 | Reset and Restart
Pavagada | June | Inv-3 unit -3 | Island fault | 851.2 | 44739 | 0.48194 | 44739 | 0.48958 | 0.18333 | Inverter unit 3 tripped due to Island fault | 0.1633 | 0.80716 | 112.1982 | Reset and Restart and Inform to Sungrow Service Engineer
Pavagada | June | Inv-3 unit -3 | Island fault | 851.2 | 44739 | 0.52569 | 44739 | 0.53819 | 0.3 | Inverter unit 3 tripped due to Island fault | 0.19315 | 0.80716 | 132.7026 | Reset and Restart and Inform to Sungrow Service Engineer
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44740 | 0.24792 | 44740 | 0.2625 | 0.35 | Inverter started late due to Riso fault | 0.000882 | 0.80105 | 2.4845 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44740 | 0.24792 | 44740 | 0.26806 | 0.48333 | Inverter started late due to Riso fault | 0.0021025 | 0.80105 | 5.9663 | Reset and Restart
Pavagada | June | 2A1-3 st,3,9 | String fault | 26 | 44740 | 0.43056 | 44740 | 0.45278 | 0.53333 | String cable damaged | 0.35362 | 0.80105 | 7.365 | Rectified
Pavagada | June | 2A2-4 st,7,1 | String fault | 26 | 44740 | 0.46736 | 44740 | 0.48611 | 0.45 | String cable damaged | 0.34462 | 0.80105 | 7.1776 | Rectified
Pavagada | June | 2A3-1 st,5,2 | String fault | 26 | 44740 | 0.50278 | 44740 | 0.52222 | 0.46667 | String cable damaged | 0.33045 | 0.80105 | 6.8824 | Rectified
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44741 | 0.24167 | 44741 | 0.25694 | 0.36667 | Inverter started late due to Riso fault | 0.001452 | 0.76958 | 3.9295 | Reset and Restart
Pavagada | June | Inverter 8 | RISO fault | 3516.5 | 44742 | 0.24306 | 44742 | 0.25833 | 0.36667 | Inverter started late due to Riso fault | 0.0014043 | 0.75964 | 3.7513 | Reset and Restart
Pavagada | June | Inverter 15 | RISO fault | 3542.5 | 44742 | 0.24306 | 44742 | 0.26319 | 0.48333 | Inverter started late due to Riso fault | 0.0033543 | 0.75964 | 9.0265 | Reset and Restart
Pavagada | June | Inverter 3 Unit 4 | Island fault | 825.6 | 44742 | 0.58194 | 44742 | 0.59375 | 0.28333 | Inverter unit 4 tripped due to Island fault | 0.28308 | 0.75964 | 177.5359 | Reset and Restart
Pavagada | July | Inverter 3 | RISO fault | 3526.6 | 44743 | 0.24792 | 44743 | 0.26667 | 0.45 | Inverter started late due to Riso fault | 0.0070245 | 0.79108 | 19.5971 | Reset and Restart
Pavagada | July | Inverter 4 | RISO fault | 3488 | 44743 | 0.24792 | 44743 | 0.26528 | 0.41667 | Inverter started late due to Riso fault | 0.0059083 | 0.79108 | 16.3028 | Reset and Restart
Pavagada | July | Inverter 5 | RISO fault | 3523 | 44743 | 0.24792 | 44743 | 0.26597 | 0.43333 | Inverter started late due to Riso fault | 0.0064567 | 0.79108 | 17.9946 | Reset and Restart
Pavagada | July | Inverter 17 | RISO fault | 3477.5 | 44743 | 0.24792 | 44743 | 0.27222 | 0.58333 | Inverter started late due to Riso fault | 0.012495 | 0.79108 | 34.3735 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44743 | 0.24792 | 44743 | 0.27986 | 0.76667 | Inverter started late due to Riso fault | 0.022333 | 0.79108 | 62.6407 | Reset and Restart
Pavagada | July | Inverter 17 | RISO fault | 3477.5 | 44744 | 0.24306 | 44744 | 0.26458 | 0.51667 | Inverter started late due to Riso fault | 0.0059572 | 0.77321 | 16.0178 | Reset and Restart
Pavagada | July | Inverter 12 | RISO fault | 3490.5 | 44746 | 0.24514 | 44746 | 0.26111 | 0.38333 | Inverter started late due to Riso fault | 0.0014375 | 0.8289 | 4.1591 | Reset and Restart
Pavagada | July | Inverter 7 | RISO fault | 3479.5 | 44748 | 0.25347 | 44748 | 0.27153 | 0.43333 | Inverter started late due to Riso fault | 0.0030853 | 0.89467 | 9.6047 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44748 | 0.25347 | 44748 | 0.26875 | 0.36667 | Inverter started late due to Riso fault | 0.0021927 | 0.89467 | 6.9239 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44748 | 0.25347 | 44748 | 0.27708 | 0.56667 | Inverter started late due to Riso fault | 0.005406 | 0.89467 | 16.945 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44748 | 0.25347 | 44748 | 0.28264 | 0.7 | Inverter started late due to Riso fault | 0.008491 | 0.89467 | 26.8617 | Reset and Restart
Pavagada | July | Inverter 19 | RISO fault | 3507.2 | 44748 | 0.25347 | 44748 | 0.27639 | 0.55 | Inverter started late due to Riso fault | 0.0050875 | 0.89467 | 15.9635 | Reset and Restart
Pavagada | July | Inverter 05 | Ground fault | 3523 | 44748 | 0.72153 | 44748 | 0.74097 | 0.46667 | Inverter tripped on Ground fault | 0.014411 | 0.89467 | 45.4213 | Rectified
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44749 | 0.24792 | 44749 | 0.2625 | 0.35 | Inverter started late due to Riso fault | 0.0046585 | 0.82816 | 13.4413 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44749 | 0.24792 | 44749 | 0.26944 | 0.51667 | Inverter started late due to Riso fault | 0.011175 | 0.82816 | 32.666 | Reset and Restart
Pavagada | July | Inverter 11 | RISO fault | 3497 | 44749 | 0.24792 | 44749 | 0.275 | 0.65 | Inverter started late due to Riso fault | 0.019454 | 0.82816 | 56.3419 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44749 | 0.24792 | 44749 | 0.27569 | 0.66667 | Inverter started late due to Riso fault | 0.020587 | 0.82816 | 59.7316 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44749 | 0.24792 | 44749 | 0.27153 | 0.56667 | Inverter started late due to Riso fault | 0.014025 | 0.82816 | 41.0706 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44749 | 0.24792 | 44749 | 0.26458 | 0.4 | Inverter started late due to Riso fault | 0.006144 | 0.82816 | 18.0408 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44750 | 0.25139 | 44750 | 0.26944 | 0.43333 | Inverter started late due to Riso fault | 0.0041253 | 0.87013 | 12.6694 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44750 | 0.25139 | 44750 | 0.27431 | 0.55 | Inverter started late due to Riso fault | 0.0068365 | 0.87013 | 20.841 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44750 | 0.25139 | 44750 | 0.26597 | 0.35 | Inverter started late due to Riso fault | 0.002562 | 0.87013 | 7.8827 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44751 | 0.25 | 44751 | 0.26875 | 0.45 | Inverter started late due to Riso fault | 0.0054945 | 0.83287 | 16.1517 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44751 | 0.25 | 44751 | 0.27431 | 0.58333 | Inverter started late due to Riso fault | 0.0089133 | 0.83287 | 26.0087 | Reset and Restart
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44752 | 0.25139 | 44752 | 0.26667 | 0.36667 | Inverter started late due to Riso fault | 0.0025703 | 0.83529 | 7.48 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44752 | 0.25139 | 44752 | 0.27153 | 0.48333 | Inverter started late due to Riso fault | 0.0049348 | 0.83529 | 14.5486 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44752 | 0.25139 | 44752 | 0.27778 | 0.63333 | Inverter started late due to Riso fault | 0.0094303 | 0.83529 | 27.5972 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44752 | 0.25139 | 44752 | 0.28333 | 0.76667 | Inverter started late due to Riso fault | 0.015004 | 0.83529 | 44.3144 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44753 | 0.25069 | 44753 | 0.26736 | 0.4 | Inverter started late due to Riso fault | 0.002524 | 0.83355 | 7.4257 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44753 | 0.25069 | 44753 | 0.27361 | 0.55 | Inverter started late due to Riso fault | 0.004488 | 0.83355 | 13.1066 | Reset and Restart
Pavagada | July | Inverter 5 | RISO fault | 3523 | 44754 | 0.25278 | 44754 | 0.26806 | 0.36667 | Inverter started late due to Riso fault | 0.0025483 | 0.79016 | 7.0939 | Reset and Restart
Pavagada | July | Inverter 7 | RISO fault | 3479.5 | 44754 | 0.25278 | 44754 | 0.27292 | 0.48333 | Inverter started late due to Riso fault | 0.0048865 | 0.79016 | 13.4348 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44754 | 0.25278 | 44754 | 0.26875 | 0.38333 | Inverter started late due to Riso fault | 0.0028328 | 0.79016 | 7.9004 | Reset and Restart
Pavagada | July | Inverter 12 | RISO fault | 3490.5 | 44754 | 0.25278 | 44754 | 0.26944 | 0.4 | Inverter started late due to Riso fault | 0.003136 | 0.79016 | 8.6493 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44754 | 0.25278 | 44754 | 0.27639 | 0.56667 | Inverter started late due to Riso fault | 0.0069813 | 0.79016 | 19.3267 | Reset and Restart
Pavagada | July | Inverter 5 | RISO fault | 3523 | 44755 | 0.25556 | 44755 | 0.27778 | 0.53333 | Inverter started late due to Riso fault | 0.004416 | 0.8783 | 13.6642 | Reset and Restart
Pavagada | July | Inverter 7 | RISO fault | 3479.5 | 44755 | 0.25556 | 44755 | 0.27153 | 0.38333 | Inverter started late due to Riso fault | 0.0019473 | 0.8783 | 5.9511 | Reset and Restart
Pavagada | July | Inverter 7 | RISO fault | 3479.5 | 44756 | 0.24931 | 44756 | 0.26597 | 0.4 | Inverter started late due to Riso fault | 0.002912 | 0.78681 | 7.9722 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44756 | 0.24931 | 44756 | 0.26667 | 0.41667 | Inverter started late due to Riso fault | 0.0030833 | 0.78681 | 8.4995 | Reset and Restart
Pavagada | July | Inverter-18 | RISO fault | 3536 | 44757 | 0.24722 | 44757 | 0.26389 | 0.4 | Inverter started late due to Riso fault | 0.003332 | 0.77334 | 9.1114 | Reset and Restart
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44758 | 0.25 | 44758 | 0.26458 | 0.35 | Inverter started late due to Riso fault | 0.0023065 | 0.83297 | 6.6936 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44758 | 0.25 | 44758 | 0.26736 | 0.41667 | Inverter started late due to Riso fault | 0.0031708 | 0.83297 | 9.2535 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44758 | 0.25 | 44758 | 0.27361 | 0.56667 | Inverter started late due to Riso fault | 0.00663 | 0.83297 | 19.5279 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44758 | 0.25 | 44758 | 0.27361 | 0.56667 | Inverter started late due to Riso fault | 0.00663 | 0.83297 | 19.5809 | Reset and Restart
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44759 | 0.24722 | 44759 | 0.26319 | 0.38333 | Inverter started late due to Riso fault | 0.0018208 | 0.81032 | 5.1405 | Reset and Restart
Pavagada | July | Inverter 12 | RISO fault | 3490.5 | 44759 | 0.24722 | 44759 | 0.26944 | 0.53333 | Inverter started late due to Riso fault | 0.004576 | 0.81032 | 12.9429 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44759 | 0.24722 | 44759 | 0.26944 | 0.53333 | Inverter started late due to Riso fault | 0.004576 | 0.81032 | 12.9911 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44759 | 0.24722 | 44759 | 0.26944 | 0.53333 | Inverter started late due to Riso fault | 0.004576 | 0.81032 | 13.1472 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44760 | 0.25069 | 44760 | 0.27153 | 0.5 | Inverter started late due to Riso fault | 0.003345 | 0.85758 | 10.0502 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44760 | 0.25069 | 44760 | 0.27083 | 0.48333 | Inverter started late due to Riso fault | 0.0030982 | 0.85758 | 9.4204 | Reset and Restart
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44761 | 0.24306 | 44761 | 0.25903 | 0.38333 | Inverter started late due to Riso fault | 0.0019128 | 0.74516 | 4.9659 | Reset and Restart
Pavagada | July | Inverter 5 | RISO fault | 3523 | 44761 | 0.24306 | 44761 | 0.25972 | 0.4 | Inverter started late due to Riso fault | 0.002172 | 0.74516 | 5.7019 | Reset and Restart
Pavagada | July | Inverter 11 | RISO fault | 3497 | 44761 | 0.24306 | 44761 | 0.26667 | 0.56667 | Inverter started late due to Riso fault | 0.005865 | 0.74516 | 15.2831 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44761 | 0.24306 | 44761 | 0.26667 | 0.56667 | Inverter started late due to Riso fault | 0.005865 | 0.74516 | 15.3115 | Reset and Restart
Pavagada | July | Inverter 18 | RISO fault | 3536 | 44761 | 0.24306 | 44761 | 0.26597 | 0.55 | Inverter started late due to Riso fault | 0.005368 | 0.74516 | 14.144 | Reset and Restart
Pavagada | July | Inverter 12 | RISO fault | 3490.5 | 44766 | 0.24722 | 44766 | 0.26597 | 0.45 | Inverter started late due to Riso fault | 0.002484 | 0.76807 | 6.6595 | Reset and Restart
Pavagada | July | Inverter 5 | RISO fault | 3523 | 44769 | 0.24792 | 44769 | 0.26875 | 0.5 | Inverter started late due to Riso fault | 0.01023 | 0.76422 | 27.5426 | Reset and Restart
Pavagada | July | Inverter 9 | RISO fault | 3477.5 | 44769 | 0.24792 | 44769 | 0.27153 | 0.56667 | Inverter started late due to Riso fault | 0.020139 | 0.76422 | 53.5216 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44769 | 0.24792 | 44769 | 0.27569 | 0.66667 | Inverter started late due to Riso fault | 0.03306 | 0.76422 | 88.516 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44769 | 0.24792 | 44769 | 0.28056 | 0.78333 | Inverter started late due to Riso fault | 0.05065 | 0.76422 | 137.2426 | Reset and Restart
Pavagada | July | Inverter 1 | RISO fault | 3484 | 44770 | 0.24514 | 44770 | 0.26181 | 0.4 | Inverter started late due to Riso fault | 0.002376 | 0.75204 | 6.2253 | Reset and Restart
Pavagada | July | Inverter 6 | RISO fault | 3510 | 44770 | 0.24514 | 44770 | 0.26667 | 0.51667 | Inverter started late due to Riso fault | 0.0046293 | 0.75204 | 12.2198 | Reset and Restart
Pavagada | July | Inverter 11 | RISO fault | 3497 | 44770 | 0.24514 | 44770 | 0.27153 | 0.63333 | Inverter started late due to Riso fault | 0.007923 | 0.75204 | 20.8364 | Reset and Restart
Pavagada | July | Inverter 19 | RISO fault | 3507.2 | 44770 | 0.24514 | 44770 | 0.26389 | 0.45 | Inverter started late due to Riso fault | 0.0032085 | 0.75204 | 8.4625 | Reset and Restart
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44771 | 0.24861 | 44771 | 0.27292 | 0.58333 | Inverter started late due to Riso fault | 0.013306 | 0.74397 | 34.9388 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44771 | 0.24861 | 44771 | 0.27708 | 0.68333 | Inverter started late due to Riso fault | 0.020432 | 0.74397 | 53.2548 | Reset and Restart
Pavagada | July | Inverter 15 | RISO fault | 3542.5 | 44771 | 0.24861 | 44771 | 0.27361 | 0.6 | Inverter started late due to Riso fault | 0.014394 | 0.74397 | 37.9354 | Reset and Restart
Pavagada | July | Inverter 19 | RISO fault | 3507.2 | 44771 | 0.24861 | 44771 | 0.27014 | 0.51667 | Inverter started late due to Riso fault | 0.0094343 | 0.74397 | 24.6164 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44771 | 0.24861 | 44771 | 0.27153 | 0.55 | Inverter started late due to Riso fault | 0.01127 | 0.74397 | 29.7267 | Reset and Restart
Pavagada | July | Inverter 12 | RISO fault | 3490.5 | 44772 | 0.25417 | 44772 | 0.27083 | 0.4 | Inverter started late due to Riso fault | 0.005 | 0.76284 | 13.3135 | Reset and Restart
Pavagada | July | Inverter 14 | RISO fault | 3503.5 | 44772 | 0.25417 | 44772 | 0.27083 | 0.4 | Inverter started late due to Riso fault | 0.005 | 0.76284 | 13.363 | Reset and Restart
Pavagada | July | Inverter 19 | RISO fault | 3507.2 | 44772 | 0.25417 | 44772 | 0.27083 | 0.4 | Inverter started late due to Riso fault | 0.005 | 0.76284 | 13.3772 | Reset and Restart
Pavagada | July | Inverter 20 | RISO fault | 3545.6 | 44772 | 0.25417 | 44772 | 0.27083 | 0.4 | Inverter started late due to Riso fault | 0.005 | 0.76284 | 13.5236 | Reset and Restart
Pavagada | July | block-3 | HV cable end termination failure | 7033 | 44772 | 0.76181 | 44772 | 0.78958 | 0.66667 | IDT Tripped due to HV cable end termination failure | 0.0085667 | 0.76284 | 45.9606 | HV cable end termination changed and charged the transformer
Pavagada | July | Inverter 10 | RISO fault | 3529.5 | 44773 | 0.25347 | 44773 | 0.27292 | 0.46667 | Inverter started late due to Riso fault | 0.0085447 | 0.7794 | 23.5055 | Reset and Restart
Pavagada | August | Inverter 2 unit 1 | Ground fault | 968.5 | 44774 | 0.58194 | 44774 | 0.59236 | 0.25 | Inverter tripped due to Ground fault on 1B1-5 | 0.21084 | 0.76274 | 155.7534 | Rectified
Pavagada | August | 1B3-4 st 1 | String fault | 13 | 44775 | 0.39236 | 44775 | 0.43681 | 1.0667 | String cable damaged | 0.78967 | 0.74889 | 7.6879 | Rectified
Pavagada | August | 2A3-4 st 8 | String fault | 12.8 | 44775 | 0.39236 | 44775 | 0.46319 | 1.7 | String cable damaged | 1.3511 | 0.74889 | 12.9514 | Rectified
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44776 | 0.26597 | 44776 | 0.27986 | 0.33333 | Inverter started late due to Riso fault | 0.00037 | 0.77053 | 0.99884 | Reset and Restart
Pavagada | August | Inverter 19 | RISO fault | 3507.2 | 44776 | 0.26597 | 44776 | 0.28056 | 0.35 | Inverter started late due to Riso fault | 0.0003815 | 0.77053 | 1.031 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44776 | 0.26597 | 44776 | 0.28194 | 0.38333 | Inverter started late due to Riso fault | 0.00042167 | 0.77053 | 1.152 | Reset and Restart
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44777 | 0.25208 | 44777 | 0.27083 | 0.45 | Inverter started late due to Riso fault | 0.0023625 | 0.83646 | 6.9491 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44777 | 0.25208 | 44777 | 0.27292 | 0.5 | Inverter started late due to Riso fault | 0.0033 | 0.83646 | 9.599 | Reset and Restart
Pavagada | August | 4A3-4 st 8,9 | String fault | 26 | 44777 | 0.40625 | 44777 | 0.41944 | 0.31667 | String cable damaged | 0.076507 | 0.83646 | 1.6639 | Rectified
Pavagada | August | 4B2-3 st 7 | String fault | 13 | 44777 | 0.43333 | 44777 | 0.44861 | 0.36667 | String cable damaged | 0.14002 | 0.83646 | 1.5226 | Rectified
Pavagada | August | 5B4-5 st 1 | String fault | 13 | 44777 | 0.46458 | 44777 | 0.48403 | 0.46667 | String cable damaged | 0.2386 | 0.83646 | 2.5945 | Rectified
Pavagada | August | 5A4-3 st 5 | String fault | 13 | 44777 | 0.50347 | 44777 | 0.52014 | 0.4 | String cable damaged | 0.13682 | 0.83646 | 1.4877 | Rectified
Pavagada | August | 5A4-2 st 1,2,3,4 | String fault | 52 | 44777 | 0.59792 | 44777 | 0.65208 | 1.3 | Inside conduit cables are short circuit | 0.5756 | 0.83646 | 25.0362 | Rectified
Pavagada | August | Inverter 2 | RISO fault | 3510 | 44778 | 0.25486 | 44778 | 0.27153 | 0.4 | Inverter started late due to Riso fault | 0.004808 | 0.83656 | 14.1179 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44778 | 0.25486 | 44778 | 0.27639 | 0.51667 | Inverter started late due to Riso fault | 0.0080342 | 0.83656 | 23.6784 | Reset and Restart
Pavagada | August | Inverter 7 | RISO fault | 3479.5 | 44778 | 0.25486 | 44778 | 0.28819 | 0.8 | Inverter started late due to Riso fault | 0.020632 | 0.83656 | 60.0561 | Reset and Restart
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44778 | 0.25486 | 44778 | 0.28542 | 0.73333 | Inverter started late due to Riso fault | 0.016977 | 0.83656 | 49.9415 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44778 | 0.25486 | 44778 | 0.28403 | 0.7 | Inverter started late due to Riso fault | 0.015323 | 0.83656 | 44.5769 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44778 | 0.25486 | 44778 | 0.28333 | 0.68333 | Inverter started late due to Riso fault | 0.014528 | 0.83656 | 42.8951 | Reset and Restart
Pavagada | August | Inverter 11 | RISO fault | 3497 | 44778 | 0.25486 | 44778 | 0.27222 | 0.41667 | Inverter started late due to Riso fault | 0.0051958 | 0.83656 | 15.2002 | Reset and Restart
Pavagada | August | Inverter 12 | RISO fault | 3490.5 | 44778 | 0.25486 | 44778 | 0.27222 | 0.41667 | Inverter started late due to Riso fault | 0.0051958 | 0.83656 | 15.172 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44778 | 0.25486 | 44778 | 0.28542 | 0.73333 | Inverter started late due to Riso fault | 0.016977 | 0.83656 | 49.7569 | Reset and Restart
Pavagada | August | Inverter 15 | RISO fault | 3542.5 | 44778 | 0.25486 | 44778 | 0.29375 | 0.93333 | Inverter started late due to Riso fault | 0.029129 | 0.83656 | 86.3255 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44778 | 0.25486 | 44778 | 0.29444 | 0.95 | Inverter started late due to Riso fault | 0.030315 | 0.83656 | 88.6839 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44778 | 0.25486 | 44778 | 0.27917 | 0.58333 | Inverter started late due to Riso fault | 0.010377 | 0.83656 | 30.1897 | Reset and Restart
Pavagada | August | 10A1-6 st 1,2,3 | String fault | 26 | 44778 | 0.43333 | 44778 | 0.48889 | 1.3333 | string cable damaged | 0.48873 | 0.83656 | 10.6303 | Replaced the cable and Mc4 connector
Pavagada | August | 10B2-4 st 4 | String fault | 13 | 44778 | 0.50347 | 44778 | 0.52708 | 0.56667 | string cable damaged | 0.24753 | 0.83656 | 2.692 | Replaced the cable and Mc4 connector
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44779 | 0.25069 | 44779 | 0.26597 | 0.36667 | Inverter started late due to Riso fault | 0.0021707 | 0.74906 | 5.7176 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44779 | 0.25069 | 44779 | 0.26597 | 0.36667 | Inverter started late due to Riso fault | 0.0021707 | 0.74906 | 5.6542 | Reset and Restart
Pavagada | August | Inverter 11 | RISO fault | 3497 | 44779 | 0.25069 | 44779 | 0.27222 | 0.51667 | Inverter started late due to Riso fault | 0.0060967 | 0.74906 | 15.9699 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44779 | 0.25069 | 44779 | 0.27292 | 0.53333 | Inverter started late due to Riso fault | 0.0067093 | 0.74906 | 17.6074 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44779 | 0.25069 | 44779 | 0.27847 | 0.66667 | Inverter started late due to Riso fault | 0.013087 | 0.74906 | 34.2798 | Reset and Restart
Pavagada | August | 1A4-4 st,2 | String fault | 13 | 44779 | 0.43403 | 44779 | 0.44722 | 0.31667 | string cable damaged | 0.21705 | 0.74906 | 2.1135 | Rectified
Pavagada | August | 9A3-4 st,6,8 | String fault | 26 | 44779 | 0.45556 | 44779 | 0.47778 | 0.53333 | string cable damaged | 0.40717 | 0.74906 | 7.9298 | Rectified
Pavagada | August | 9A4-2 st,6 | String fault | 13 | 44779 | 0.48889 | 44779 | 0.50278 | 0.33333 | string cable damaged | 0.22675 | 0.74906 | 2.208 | Rectified
Pavagada | August | 9B3-3 st,11 | String fault | 13 | 44779 | 0.6375 | 44779 | 0.65278 | 0.36667 | string cable damaged | 0.10996 | 0.74906 | 1.0707 | Rectified
Pavagada | August | 6B3-5 st,6 | String fault | 13 | 44779 | 0.66389 | 44779 | 0.68056 | 0.4 | string cable damaged | 0.13284 | 0.74906 | 1.2936 | Rectified
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44780 | 0.25278 | 44780 | 0.27153 | 0.45 | Inverter started late due to Riso fault | 0.004482 | 0.81784 | 12.747 | Reset and Restart
Pavagada | August | Inverter 11 | RISO fault | 3497 | 44780 | 0.25278 | 44780 | 0.27917 | 0.63333 | Inverter started late due to Riso fault | 0.010349 | 0.81784 | 29.5971 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44780 | 0.25278 | 44780 | 0.28125 | 0.68333 | Inverter started late due to Riso fault | 0.012526 | 0.81784 | 35.8894 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44780 | 0.25278 | 44780 | 0.27917 | 0.63333 | Inverter started late due to Riso fault | 0.010349 | 0.81784 | 29.5971 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44780 | 0.25278 | 44780 | 0.29167 | 0.93333 | Inverter started late due to Riso fault | 0.026712 | 0.81784 | 75.9701 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44780 | 0.25278 | 44780 | 0.28958 | 0.88333 | Inverter started late due to Riso fault | 0.023558 | 0.81784 | 68.1286 | Reset and Restart
Pavagada | August | 2A4-2 st,1 to 13 | String fault | 169 | 44780 | 0.55347 | 44780 | 0.78125 | 5.4667 | SMB burn due string cable short circuit | 2.1951 | 0.81784 | 303.4019 | work in progress
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44781 | 0.25347 | 44781 | 0.27292 | 0.46667 | Inverter started late due to Riso fault | 0.0017687 | 0.84153 | 5.1855 | Reset and Restart
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44781 | 0.25347 | 44781 | 0.275 | 0.51667 | Inverter started late due to Riso fault | 0.0025265 | 0.84153 | 7.498 | Reset and Restart
Pavagada | August | Inverter 4 | RISO fault | 3488 | 44781 | 0.25347 | 44781 | 0.28056 | 0.65 | Inverter started late due to Riso fault | 0.0049985 | 0.84153 | 14.6718 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44781 | 0.25347 | 44781 | 0.28056 | 0.65 | Inverter started late due to Riso fault | 0.0049985 | 0.84153 | 14.819 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44781 | 0.25347 | 44781 | 0.26944 | 0.38333 | Inverter started late due to Riso fault | 0.00098133 | 0.84153 | 2.8718 | Reset and Restart
Pavagada | August | Inverter 11 | RISO fault | 3497 | 44781 | 0.25347 | 44781 | 0.27361 | 0.48333 | Inverter started late due to Riso fault | 0.001972 | 0.84153 | 5.8032 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44781 | 0.25347 | 44781 | 0.275 | 0.51667 | Inverter started late due to Riso fault | 0.0025265 | 0.84153 | 7.4489 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44781 | 0.25347 | 44781 | 0.27986 | 0.63333 | Inverter started late due to Riso fault | 0.0046613 | 0.84153 | 13.7175 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44781 | 0.25347 | 44781 | 0.28681 | 0.8 | Inverter started late due to Riso fault | 0.009368 | 0.84153 | 27.4146 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44781 | 0.25347 | 44781 | 0.275 | 0.51667 | Inverter started late due to Riso fault | 0.0025265 | 0.84153 | 7.518 | Reset and Restart
Pavagada | August | 2A4-2 st 1,2,3,4,6,7,8,9,10,11 | String fault | 130 | 44781 | 0.25347 | 44781 | 0.54861 | 7.0833 | string cable short circuit inside conduit | 1.9228 | 0.84153 | 210.3482 | Rectified
Pavagada | August | 2A4-1 st 4,5,6,7,8,9,10 | String fault | 91 | 44781 | 0.25347 | 44781 | 0.39444 | 3.3833 | string cable short circuit inside conduit | 0.32798 | 0.84153 | 25.1164 | Rectified
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44782 | 0.25486 | 44782 | 0.27014 | 0.36667 | Inverter started late due to Riso fault | 0.0016097 | 0.79404 | 4.5075 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44782 | 0.25486 | 44782 | 0.27361 | 0.45 | Inverter started late due to Riso fault | 0.002682 | 0.79404 | 7.5026 | Reset and Restart
Pavagada | August | Inverter 7 | RISO fault | 3479.5 | 44782 | 0.25486 | 44782 | 0.27708 | 0.53333 | Inverter started late due to Riso fault | 0.0041547 | 0.79404 | 11.4787 | Reset and Restart
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44782 | 0.25486 | 44782 | 0.27569 | 0.5 | Inverter started late due to Riso fault | 0.003505 | 0.79404 | 9.7867 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44782 | 0.25486 | 44782 | 0.27153 | 0.4 | Inverter started late due to Riso fault | 0.002008 | 0.79404 | 5.5446 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44782 | 0.25486 | 44782 | 0.27847 | 0.56667 | Inverter started late due to Riso fault | 0.004845 | 0.79404 | 13.5783 | Reset and Restart
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44783 | 0.25 | 44783 | 0.26528 | 0.36667 | Inverter started late due to Riso fault | 0.0017527 | 0.78128 | 4.7707 | Reset and Restart
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44783 | 0.25 | 44783 | 0.26667 | 0.4 | Inverter started late due to Riso fault | 0.002164 | 0.78128 | 5.9624 | Reset and Restart
Pavagada | August | Inverter 4 | RISO fault | 3488 | 44783 | 0.25 | 44783 | 0.26736 | 0.41667 | Inverter started late due to Riso fault | 0.002375 | 0.78128 | 6.4721 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44783 | 0.25 | 44783 | 0.27083 | 0.5 | Inverter started late due to Riso fault | 0.003695 | 0.78128 | 10.1703 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44783 | 0.25 | 44783 | 0.27639 | 0.63333 | Inverter started late due to Riso fault | 0.0069603 | 0.78128 | 18.9106 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44783 | 0.25 | 44783 | 0.27708 | 0.65 | Inverter started late due to Riso fault | 0.007449 | 0.78128 | 20.5787 | Reset and Restart
Pavagada | August | Inverter 19 | RISO fault | 3507.2 | 44783 | 0.25 | 44783 | 0.27569 | 0.61667 | Inverter started late due to Riso fault | 0.0064935 | 0.78128 | 17.7929 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44783 | 0.25 | 44783 | 0.27014 | 0.48333 | Inverter started late due to Riso fault | 0.0033882 | 0.78128 | 9.3856 | Reset and Restart
Pavagada | August | Inverter 9 | Ground fault | 3477.5 | 44783 | 0.68056 | 44783 | 0.69583 | 0.36667 | Inverter tripped due to ground fault on 5A3-5 | 0.12189 | 0.78128 | 331.1661 | Rectified
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44784 | 0.24931 | 44784 | 0.26389 | 0.35 | Inverter started late due to Riso fault | 0.001904 | 0.74739 | 4.9578 | Reset and Restart
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44784 | 0.24931 | 44784 | 0.26389 | 0.35 | Inverter started late due to Riso fault | 0.001904 | 0.74739 | 5.0185 | Reset and Restart
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44785 | 0.24931 | 44785 | 0.26736 | 0.43333 | Inverter started late due to Riso fault | 0.003328 | 0.7591 | 8.8016 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44785 | 0.24931 | 44785 | 0.26806 | 0.45 | Inverter started late due to Riso fault | 0.003717 | 0.7591 | 9.9404 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44785 | 0.24931 | 44785 | 0.27222 | 0.55 | Inverter started late due to Riso fault | 0.0067815 | 0.7591 | 17.9017 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44785 | 0.24931 | 44785 | 0.27153 | 0.53333 | Inverter started late due to Riso fault | 0.006176 | 0.7591 | 16.5775 | Reset and Restart
Pavagada | August | Inverter 7 | RISO fault | 3479.5 | 44786 | 0.25 | 44786 | 0.27153 | 0.51667 | Inverter started late due to Riso fault | 0.0038492 | 0.75311 | 10.0866 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44786 | 0.25 | 44786 | 0.26597 | 0.38333 | Inverter started late due to Riso fault | 0.0012382 | 0.75311 | 3.2427 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44786 | 0.25 | 44786 | 0.26736 | 0.41667 | Inverter started late due to Riso fault | 0.0016958 | 0.75311 | 4.5077 | Reset and Restart
Pavagada | August | Inverter 12 | RISO fault | 3490.5 | 44786 | 0.25 | 44786 | 0.26597 | 0.38333 | Inverter started late due to Riso fault | 0.0012382 | 0.75311 | 3.2548 | Reset and Restart
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44787 | 0.25694 | 44787 | 0.27153 | 0.35 | Inverter started late due to Riso fault | 0.005684 | 0.81054 | 16.0512 | Reset and Restart
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44787 | 0.25694 | 44787 | 0.275 | 0.43333 | Inverter started late due to Riso fault | 0.0088487 | 0.81054 | 25.2935 | Reset and Restart
Pavagada | August | Inverter 4 | RISO fault | 3488 | 44787 | 0.25694 | 44787 | 0.27708 | 0.48333 | Inverter started late due to Riso fault | 0.011151 | 0.81054 | 31.5243 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44787 | 0.25694 | 44787 | 0.28264 | 0.61667 | Inverter started late due to Riso fault | 0.018845 | 0.81054 | 53.8134 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44787 | 0.25694 | 44787 | 0.27153 | 0.35 | Inverter started late due to Riso fault | 0.005684 | 0.81054 | 16.141 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44787 | 0.25694 | 44787 | 0.27917 | 0.53333 | Inverter started late due to Riso fault | 0.013776 | 0.81054 | 38.8297 | Reset and Restart
Pavagada | August | Inverter 19 | RISO fault | 3507.2 | 44787 | 0.25694 | 44787 | 0.27431 | 0.41667 | Inverter started late due to Riso fault | 0.0081333 | 0.81054 | 23.1208 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44787 | 0.25694 | 44787 | 0.28542 | 0.68333 | Inverter started late due to Riso fault | 0.022994 | 0.81054 | 66.0818 | Reset and Restart
Pavagada | August | 3B3-1 st 1,2,3,4,5,6,7,8 | String fault | 104 | 44787 | 0.31597 | 44787 | 0.4125 | 2.3167 | Inside conduit cables are short circuit | 0.84839 | 0.81054 | 71.5157 | Rectified
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44788 | 0.25278 | 44788 | 0.27083 | 0.43333 | Inverter started late due to Riso fault | 0.0026867 | 0.76698 | 7.2863 | Reset and Restart
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44789 | 0.25347 | 44789 | 0.26875 | 0.36667 | Inverter started late due to Riso fault | 0.003718 | 0.74777 | 9.6863 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44789 | 0.25347 | 44789 | 0.27639 | 0.55 | Inverter started late due to Riso fault | 0.010939 | 0.74777 | 28.6595 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44789 | 0.25347 | 44789 | 0.27778 | 0.58333 | Inverter started late due to Riso fault | 0.012822 | 0.74777 | 33.3412 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44789 | 0.25347 | 44789 | 0.27847 | 0.6 | Inverter started late due to Riso fault | 0.013842 | 0.74777 | 36.5999 | Reset and Restart
Pavagada | August | Inverter 19 | RISO fault | 3507.2 | 44789 | 0.25347 | 44789 | 0.26944 | 0.38333 | Inverter started late due to Riso fault | 0.0041783 | 0.74777 | 10.958 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44789 | 0.25347 | 44789 | 0.26806 | 0.35 | Inverter started late due to Riso fault | 0.003304 | 0.74777 | 8.7599 | Reset and Restart
Pavagada | August | 7B3-5 st 12 | String fault | 13 | 44789 | 0.43472 | 44789 | 0.45347 | 0.45 | string cable damaged | 0.4055 | 0.74777 | 3.9419 | Rectified
Pavagada | August | 2B1-2 st 9 | String fault | 12.8 | 44789 | 0.46806 | 44789 | 0.49097 | 0.55 | string cable damaged | 0.54531 | 0.74777 | 5.2194 | Rectified
Pavagada | August | 2B1-3 st 1 | String fault | 12.8 | 44789 | 0.50347 | 44789 | 0.52153 | 0.43333 | string cable damaged | 0.43789 | 0.74777 | 4.1912 | Rectified
Pavagada | August | 3A4-5 st 1,2,3,4 | String fault | 52 | 44789 | 0.53819 | 44789 | 0.57153 | 0.8 | Inside conduit cables are short circuit | 0.75061 | 0.74777 | 29.1868 | Rectified
Pavagada | August | Inverter-1 | RISO fault | 3484 | 44790 | 0.25208 | 44790 | 0.26875 | 0.4 | Inverter started late due to Riso fault | 0.004096 | 0.74524 | 10.6349 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44790 | 0.25208 | 44790 | 0.27569 | 0.56667 | Inverter started late due to Riso fault | 0.011396 | 0.74524 | 29.7534 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44790 | 0.25208 | 44790 | 0.27083 | 0.45 | Inverter started late due to Riso fault | 0.0058725 | 0.74524 | 15.2189 | Reset and Restart
Pavagada | August | Inv-2 Unit-1 | L - Over temp fault | 968.5 | 44790 | 0.46528 | 44790 | 0.47847 | 0.31667 | Inverter tripped on due to L-Over temp fault | 0.2998 | 0.74524 | 216.3826 | Inform to Service Engineer
Pavagada | August | inv-12 unit-1 | L - Over temp fault | 967 | 44790 | 0.50972 | 44790 | 0.52014 | 0.25 | Inverter tripped on due to L-Over temp fault | 0.19197 | 0.74524 | 138.3438 | Inform to Service Engineer
Pavagada | August | Inverter 3 | RISO fault | 3526.6 | 44791 | 0.25139 | 44791 | 0.26875 | 0.41667 | Inverter started late due to Riso fault | 0.001125 | 0.74893 | 2.9713 | Reset and Restart
Pavagada | August | Inverter 4 | RISO fault | 3488 | 44791 | 0.25139 | 44791 | 0.27014 | 0.45 | Inverter started late due to Riso fault | 0.0012915 | 0.74893 | 3.3737 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44791 | 0.25139 | 44791 | 0.27986 | 0.68333 | Inverter started late due to Riso fault | 0.0029793 | 0.74893 | 7.8174 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44791 | 0.25139 | 44791 | 0.275 | 0.56667 | Inverter started late due to Riso fault | 0.0019777 | 0.74893 | 5.1506 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44792 | 0.25903 | 44792 | 0.28194 | 0.55 | Inverter started late due to Riso fault | 0.00814 | 0.80094 | 22.8416 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44792 | 0.25903 | 44792 | 0.27639 | 0.41667 | Inverter started late due to Riso fault | 0.0041583 | 0.80094 | 11.5821 | Reset and Restart
Pavagada | August | Inverter 1 | RISO fault | 3484 | 44793 | 0.25764 | 44793 | 0.27222 | 0.35 | Inverter started late due to Riso fault | 0.0038465 | 0.75751 | 10.1516 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44793 | 0.25764 | 44793 | 0.28056 | 0.55 | Inverter started late due to Riso fault | 0.0116 | 0.75751 | 30.7844 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44793 | 0.25764 | 44793 | 0.27847 | 0.5 | Inverter started late due to Riso fault | 0.009265 | 0.75751 | 24.4063 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44794 | 0.25625 | 44794 | 0.27292 | 0.4 | Inverter started late due to Riso fault | 0.004536 | 0.77206 | 12.1784 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44794 | 0.25625 | 44794 | 0.27292 | 0.4 | Inverter started late due to Riso fault | 0.004536 | 0.77206 | 12.2467 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44794 | 0.25625 | 44794 | 0.27986 | 0.56667 | Inverter started late due to Riso fault | 0.0096277 | 0.77206 | 25.8487 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44795 | 0.25208 | 44795 | 0.27083 | 0.45 | Inverter started late due to Riso fault | 0.0076455 | 0.76321 | 20.2916 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44795 | 0.25208 | 44795 | 0.27083 | 0.45 | Inverter started late due to Riso fault | 0.0076455 | 0.76321 | 20.633 | Reset and Restart
Pavagada | August | Inverter 12 | RISO fault | 3490.5 | 44796 | 0.25486 | 44796 | 0.27292 | 0.43333 | Inverter started late due to Riso fault | 0.0060797 | 0.75383 | 15.997 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44796 | 0.25486 | 44796 | 0.27292 | 0.43333 | Inverter started late due to Riso fault | 0.0060797 | 0.75383 | 16.0268 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44796 | 0.25486 | 44796 | 0.2875 | 0.78333 | Inverter started late due to Riso fault | 0.035258 | 0.75383 | 92.4261 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44796 | 0.25486 | 44796 | 0.2875 | 0.78333 | Inverter started late due to Riso fault | 0.035258 | 0.75383 | 93.9809 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44797 | 0.25972 | 44797 | 0.27569 | 0.38333 | Inverter started late due to Riso fault | 0.0038257 | 0.78583 | 10.4545 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44797 | 0.25972 | 44797 | 0.27569 | 0.38333 | Inverter started late due to Riso fault | 0.0038257 | 0.78583 | 10.5131 | Reset and Restart
Pavagada | August | 9A4-3 ST 13 | String fault | 13 | 44797 | 0.44444 | 44797 | 0.5 | 1.3333 | string cable damaged | 0.53457 | 0.78583 | 5.4611 | Rectified
Pavagada | August | 9B1-1 ST 12 | String fault | 13 | 44797 | 0.44444 | 44797 | 0.52083 | 1.8333 | string cable damaged | 0.87302 | 0.78583 | 8.9185 | Rectified
Pavagada | August | 9B1-6 ST 10 | String fault | 13 | 44797 | 0.47917 | 44797 | 0.54167 | 1.5 | string cable damaged | 0.99399 | 0.78583 | 10.1544 | Rectified
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44798 | 0.25556 | 44798 | 0.28542 | 0.71667 | Inverter started late due to Riso fault | 0.018533 | 0.78362 | 51.0696 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44798 | 0.25556 | 44798 | 0.28681 | 0.75 | Inverter started late due to Riso fault | 0.019935 | 0.78362 | 55.1361 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44798 | 0.25556 | 44798 | 0.27361 | 0.43333 | Inverter started late due to Riso fault | 0.0077177 | 0.78362 | 21.031 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44798 | 0.25556 | 44798 | 0.27986 | 0.58333 | Inverter started late due to Riso fault | 0.012903 | 0.78362 | 35.8507 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44799 | 0.26389 | 44799 | 0.28264 | 0.45 | Inverter started late due to Riso fault | 0.00144 | 0.78693 | 3.9922 | Reset and Restart
Pavagada | August | Inverter 8 | RISO fault | 3516.5 | 44799 | 0.26389 | 44799 | 0.27986 | 0.38333 | Inverter started late due to Riso fault | 0.00093917 | 0.78693 | 2.5989 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44799 | 0.26389 | 44799 | 0.28056 | 0.4 | Inverter started late due to Riso fault | 0.00106 | 0.78693 | 2.9441 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44799 | 0.26389 | 44799 | 0.28611 | 0.53333 | Inverter started late due to Riso fault | 0.0022667 | 0.78693 | 6.2492 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44799 | 0.26389 | 44799 | 0.29097 | 0.65 | Inverter started late due to Riso fault | 0.003757 | 0.78693 | 10.3389 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44799 | 0.26389 | 44799 | 0.30208 | 0.91667 | Inverter started late due to Riso fault | 0.0074708 | 0.78693 | 20.4443 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44799 | 0.26389 | 44799 | 0.30139 | 0.9 | Inverter started late due to Riso fault | 0.007227 | 0.78693 | 20.1097 | Reset and Restart
Pavagada | August | Inverter 20 | RISO fault | 3545.6 | 44799 | 0.26389 | 44799 | 0.3 | 0.86667 | Inverter started late due to Riso fault | 0.006734 | 0.78693 | 18.7888 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44800 | 0.25764 | 44800 | 0.27778 | 0.48333 | Inverter started late due to Riso fault | 0.019604 | 0.76975 | 52.4763 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44800 | 0.25764 | 44800 | 0.27917 | 0.51667 | Inverter started late due to Riso fault | 0.022139 | 0.76975 | 60.1487 | Reset and Restart
Pavagada | August | Inverter 11 | RISO fault | 3497 | 44800 | 0.25764 | 44800 | 0.28958 | 0.76667 | Inverter started late due to Riso fault | 0.041561 | 0.76975 | 111.875 | Reset and Restart
Pavagada | August | Inverter 12 | RISO fault | 3490.5 | 44800 | 0.25764 | 44800 | 0.28264 | 0.6 | Inverter started late due to Riso fault | 0.028326 | 0.76975 | 76.107 | Reset and Restart
Pavagada | August | Inverter 14 | RISO fault | 3503.5 | 44800 | 0.25764 | 44800 | 0.28542 | 0.66667 | Inverter started late due to Riso fault | 0.03338 | 0.76975 | 90.0202 | Reset and Restart
Pavagada | August | Inverter 15 | RISO fault | 3542.5 | 44800 | 0.25764 | 44800 | 0.27778 | 0.48333 | Inverter started late due to Riso fault | 0.019749 | 0.76975 | 53.8526 | Reset and Restart
Pavagada | August | Inverter 2 | RISO fault | 3510 | 44801 | 0.26806 | 44801 | 0.28681 | 0.45 | Inverter started late due to Riso fault | 0.002727 | 0.75884 | 7.2634 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3510 | 44801 | 0.26806 | 44801 | 0.28889 | 0.5 | Inverter started late due to Riso fault | 0.00363 | 0.75884 | 9.6685 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44802 | 0.25 | 44802 | 0.27708 | 0.65 | Inverter started late due to Riso fault | 0.01432 | 0.78491 | 39.0856 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44802 | 0.25 | 44802 | 0.27431 | 0.58333 | Inverter started late due to Riso fault | 0.0093158 | 0.78491 | 25.8556 | Reset and Restart
Pavagada | August | Inverter 17 | RISO fault | 3477.5 | 44803 | 0.24931 | 44803 | 0.26875 | 0.46667 | Inverter started late due to Riso fault | 0.0066127 | 0.72476 | 16.6661 | Reset and Restart
Pavagada | August | Inverter 18 | RISO fault | 3536 | 44803 | 0.24931 | 44803 | 0.26944 | 0.48333 | Inverter started late due to Riso fault | 0.006409 | 0.72476 | 16.4246 | Reset and Restart
Pavagada | August | Inverter 5 | RISO fault | 3523 | 44804 | 0.25069 | 44804 | 0.26736 | 0.4 | Inverter started late due to Riso fault | 0.002348 | 0.74291 | 6.1453 | Reset and Restart
Pavagada | August | Inverter 9 | RISO fault | 3477.5 | 44804 | 0.25069 | 44804 | 0.27986 | 0.7 | Inverter started late due to Riso fault | 0.01246 | 0.74291 | 32.1899 | Reset and Restart
Pavagada | August | Inverter 10 | RISO fault | 3529.5 | 44804 | 0.25069 | 44804 | 0.28056 | 0.71667 | Inverter started late due to Riso fault | 0.013187 | 0.74291 | 34.5766 | Reset and Restart
Pavagada | August | Inverter 15 | RISO fault | 3542.5 | 44804 | 0.25069 | 44804 | 0.27292 | 0.53333 | Inverter started late due to Riso fault | 0.005824 | 0.74291 | 15.3273 | Reset and Restart
Pavagada | August | Inverter 16 | RISO fault | 3497 | 44804 | 0.25069 | 44804 | 0.27292 | 0.53333 | Inverter started late due to Riso fault | 0.005824 | 0.74291 | 15.1304 | Reset and Restart
Pavagada | August | Inverter 19 | RISO fault | 3507.2 | 44804 | 0.25069 | 44804 | 0.28889 | 0.91667 | Inverter started late due to Riso fault | 0.024649 | 0.74291 | 64.224 | Reset and Restart
Pavagada | August | Inv-1 to 20 | Grid failure | 70197 | 44804 | 0.50556 | 44804 | 0.50764 | 0.05 | All Inverters tripped due to ac under voltage | 0.048122 | 0.74291 | 2509.5547 | Restart
Pavagada | September | Inverter 8 | RISO fault | 3516.5 | 44805 | 0.25347 | 44805 | 0.27014 | 0.4 | Inverter started late due to Riso fault | 0.007372 | 0.724 | 18.7688 | Reset and Restart
Pavagada | September | Inverter 9 | RISO fault | 3477.5 | 44805 | 0.25347 | 44805 | 0.27083 | 0.41667 | Inverter started late due to Riso fault | 0.0081125 | 0.724 | 20.425 | Reset and Restart
Pavagada | September | Inverter 11 | RISO fault | 3497 | 44805 | 0.25347 | 44805 | 0.27847 | 0.6 | Inverter started late due to Riso fault | 0.021708 | 0.724 | 54.9612 | Reset and Restart
Pavagada | September | Inverter 12 | RISO fault | 3490.5 | 44805 | 0.25347 | 44805 | 0.27708 | 0.56667 | Inverter started late due to Riso fault | 0.018802 | 0.724 | 47.5152 | Reset and Restart
Pavagada | September | Inverter 14 | RISO fault | 3503.5 | 44805 | 0.25347 | 44805 | 0.27778 | 0.58333 | Inverter started late due to Riso fault | 0.020288 | 0.724 | 51.4623 | Reset and Restart
Pavagada | September | Inverter 15 | RISO fault | 3542.5 | 44805 | 0.25347 | 44805 | 0.28403 | 0.73333 | Inverter started late due to Riso fault | 0.035266 | 0.724 | 90.4496 | Reset and Restart
Pavagada | September | Inverter 16 | RISO fault | 3497 | 44805 | 0.25347 | 44805 | 0.28403 | 0.73333 | Inverter started late due to Riso fault | 0.035266 | 0.724 | 89.2879 | Reset and Restart
Pavagada | September | Inverter 17 | RISO fault | 3477.5 | 44805 | 0.25347 | 44805 | 0.29236 | 0.93333 | Inverter started late due to Riso fault | 0.057307 | 0.724 | 144.2822 | Reset and Restart
Pavagada | September | Inverter 18 | RISO fault | 3536 | 44805 | 0.25347 | 44805 | 0.29236 | 0.93333 | Inverter started late due to Riso fault | 0.057307 | 0.724 | 146.7094 | Reset and Restart
Pavagada | September | Inverter 19 | RISO fault | 3507.2 | 44805 | 0.25347 | 44805 | 0.28611 | 0.78333 | Inverter started late due to Riso fault | 0.041313 | 0.724 | 104.903 | Reset and Restart
Pavagada | September | Inverter 1 | RISO fault | 3484 | 44806 | 0.25139 | 44806 | 0.27361 | 0.53333 | Inverter started late due to Riso fault | 0.0079147 | 0.72595 | 20.0178 | Reset and Restart
Pavagada | September | Inverter 4 | RISO fault | 3488 | 44806 | 0.25139 | 44806 | 0.27778 | 0.63333 | Inverter started late due to Riso fault | 0.012109 | 0.72595 | 30.6621 | Reset and Restart
Pavagada | September | Inverter 8 | RISO fault | 3516.5 | 44806 | 0.25139 | 44806 | 0.28681 | 0.85 | Inverter started late due to Riso fault | 0.022568 | 0.72595 | 57.6101 | Reset and Restart
Pavagada | September | Inverter 9 | RISO fault | 3477.5 | 44806 | 0.25139 | 44806 | 0.2875 | 0.86667 | Inverter started late due to Riso fault | 0.023651 | 0.72595 | 59.7073 | Reset and Restart
Pavagada | September | Inverter 12 | RISO fault | 3490.5 | 44806 | 0.25139 | 44806 | 0.27222 | 0.5 | Inverter started late due to Riso fault | 0.0067 | 0.72595 | 16.9772 | Reset and Restart
Pavagada | September | Inverter 14 | RISO fault | 3503.5 | 44806 | 0.25139 | 44806 | 0.27431 | 0.55 | Inverter started late due to Riso fault | 0.0085635 | 0.72595 | 21.78 | Reset and Restart
Pavagada | September | Inverter 1 | RISO fault | 3484 | 44807 | 0.25069 | 44807 | 0.27153 | 0.5 | Inverter started late due to Riso fault | 0.00403 | 0.71032 | 9.9732 | Reset and Restart
Pavagada | September | Inverter 2 | RISO fault | 3510 | 44807 | 0.25069 | 44807 | 0.27014 | 0.46667 | Inverter started late due to Riso fault | 0.0032853 | 0.71032 | 8.1911 | Reset and Restart
Pavagada | September | Inverter 8 | RISO fault | 3516.5 | 44807 | 0.25069 | 44807 | 0.26736 | 0.4 | Inverter started late due to Riso fault | 0.00206 | 0.71032 | 5.1455 | Reset and Restart
Pavagada | September | Inverter 9 | RISO fault | 3477.5 | 44807 | 0.25069 | 44807 | 0.27222 | 0.51667 | Inverter started late due to Riso fault | 0.0044537 | 0.71032 | 11.0011 | Reset and Restart
Pavagada | September | Inverter 10 | RISO fault | 3529.5 | 44807 | 0.25069 | 44807 | 0.27431 | 0.56667 | Inverter started late due to Riso fault | 0.005984 | 0.71032 | 15.0023 | Reset and Restart
Pavagada | September | 1A3-1 st 13 | String fault | 13 | 44807 | 0.39236 | 44807 | 0.40278 | 0.25 | string cable insulation damaged | 0.10244 | 0.71032 | 0.94597 | Rectified
Pavagada | September | 8A3-2 st 10 | String fault | 13 | 44807 | 0.42708 | 44807 | 0.43958 | 0.3 | string cable insulation damaged | 0.26845 | 0.71032 | 2.4789 | Rectified
Pavagada | September | 7A1-5 st 3 | String fault | 13 | 44807 | 0.46667 | 44807 | 0.48333 | 0.4 | string cable insulation damaged | 0.35858 | 0.71032 | 3.3111 | Rectified
Pavagada | September | 9A4-5 st 13 | String fault | 13 | 44807 | 0.50069 | 44807 | 0.51181 | 0.26667 | string cable insulation damaged | 0.22398 | 0.71032 | 2.0683 | Rectified
Pavagada | September | 9B3-2 st 12,13 | String fault | 26 | 44807 | 0.52222 | 44807 | 0.54097 | 0.45 | string cable insulation damaged | 0.49732 | 0.71032 | 9.1846 | Rectified
Pavagada | September | Inverter 1 | RISO fault | 3484 | 44808 | 0.25486 | 44808 | 0.27292 | 0.43333 | Inverter started late due to Riso fault | 0.0039867 | 0.7366 | 10.2311 | Reset and Restart
Pavagada | September | Inverter 4 | RISO fault | 3488 | 44808 | 0.25486 | 44808 | 0.27222 | 0.41667 | Inverter started late due to Riso fault | 0.0037042 | 0.7366 | 9.517 | Reset and Restart
Pavagada | September | Inverter 5 | RISO fault | 3523 | 44808 | 0.25486 | 44808 | 0.27361 | 0.45 | Inverter started late due to Riso fault | 0.0042525 | 0.7366 | 11.0355 | Reset and Restart
Pavagada | September | Inverter 17 | RISO fault | 3477.5 | 44808 | 0.25486 | 44808 | 0.27153 | 0.4 | Inverter started late due to Riso fault | 0.003416 | 0.7366 | 8.7502 | Reset and Restart
Pavagada | September | Inverter 18 | RISO fault | 3536 | 44808 | 0.25486 | 44808 | 0.27222 | 0.41667 | Inverter started late due to Riso fault | 0.0037042 | 0.7366 | 9.648 | Reset and Restart
Pavagada | September | Inverter 11 | RISO fault | 3497 | 44809 | 0.25417 | 44809 | 0.26875 | 0.35 | Inverter started late due to Riso fault | 0.002856 | 0.7546 | 7.5365 | Reset and Restart
Pavagada | September | Inverter 19 | RISO fault | 3507.2 | 44810 | 0.25139 | 44810 | 0.26667 | 0.36667 | Inverter started late due to Riso fault | 0.0089393 | 0.73763 | 23.1262 | Reset and Restart
Pavagada | September | Inverter 20 | RISO fault | 3545.6 | 44810 | 0.25139 | 44810 | 0.27569 | 0.58333 | Inverter started late due to Riso fault | 0.019127 | 0.73763 | 50.025 | Reset and Restart
Pavagada | September | Inverter 16 | Ground fault | 3497 | 44810 | 0.42569 | 44810 | 0.43264 | 0.16667 | Inverter tripped on Ground fault | 0.14306 | 0.73763 | 369.0355 | found fault in smb and restart inverter
Pavagada | September | Inverter 8 | RISO fault | 3516.5 | 44811 | 0.25347 | 44811 | 0.28125 | 0.66667 | Inverter started late due to Riso fault | 0.00964 | 0.76779 | 26.0275 | Reset and Restart
Pavagada | September | Inverter 9 | RISO fault | 3477.5 | 44811 | 0.25347 | 44811 | 0.28264 | 0.7 | Inverter started late due to Riso fault | 0.010969 | 0.76779 | 29.2873 | Reset and Restart
Pavagada | September | Inverter 10 | RISO fault | 3529.5 | 44811 | 0.25347 | 44811 | 0.28333 | 0.71667 | Inverter started late due to Riso fault | 0.011682 | 0.76779 | 31.6565 | Reset and Restart
Pavagada | September | Inverter 11 | RISO fault | 3497 | 44811 | 0.25347 | 44811 | 0.27361 | 0.48333 | Inverter started late due to Riso fault | 0.0040552 | 0.76779 | 10.888 | Reset and Restart
Pavagada | September | Inverter 12 | RISO fault | 3490.5 | 44811 | 0.25347 | 44811 | 0.27222 | 0.45 | Inverter started late due to Riso fault | 0.00333 | 0.76779 | 8.9243 | Reset and Restart
Pavagada | September | Inverter 15 | RISO fault | 3542.5 | 44811 | 0.25347 | 44811 | 0.27361 | 0.48333 | Inverter started late due to Riso fault | 0.0040552 | 0.76779 | 11.0297 | Reset and Restart
Pavagada | September | Inverter 16 | RISO fault | 3497 | 44811 | 0.25347 | 44811 | 0.27431 | 0.5 | Inverter started late due to Riso fault | 0.00445 | 0.76779 | 11.9481 | Reset and Restart
Pavagada | September | Inverter 20 | RISO fault | 3545.6 | 44811 | 0.25347 | 44811 | 0.27639 | 0.55 | Inverter started late due to Riso fault | 0.0057805 | 0.76779 | 15.7362 | Reset and Restart
Pavagada | September | Inverter 6 | RISO fault | 3510 | 44812 | 0.25764 | 44812 | 0.27361 | 0.38333 | Inverter started late due to Riso fault | 0.0010733 | 0.87873 | 3.3105 | Reset and Restart
Pavagada | September | Inverter 19 | RISO fault | 3507.2 | 44812 | 0.25764 | 44812 | 0.28264 | 0.6 | Inverter started late due to Riso fault | 0.00612 | 0.87873 | 18.8612 | Reset and Restart
Pavagada | September | Inverter 20 | RISO fault | 3545.6 | 44812 | 0.25764 | 44812 | 0.27222 | 0.35 | Inverter started late due to Riso fault | 0.000721 | 0.87873 | 2.2464 | Reset and Restart
Pavagada | September | Inverter 4 | RISO fault | 3488 | 44813 | 0.25417 | 44813 | 0.26875 | 0.35 | Inverter started late due to Riso fault | 0.001722 | 0.78589 | 4.7203 | Reset and Restart
Pavagada | September | Inverter 20 | Ground fault | 3545.6 | 44813 | 0.40833 | 44813 | 0.42847 | 0.48333 | string cable insulation damaged | 0.28573 | 0.78589 | 796.1654 | found fault in smb-10B3-3 and restart inverter
Pavagada | September | 10B3- st 9,11 | String fault | 26 | 44813 | 0.44167 | 44813 | 0.46528 | 0.56667 | string cable insulation damaged | 0.29288 | 0.78589 | 5.9845 | Rectified
Pavagada | September | 10B3-1 st,3 | String fault | 13 | 44813 | 0.48958 | 44813 | 0.50278 | 0.31667 | string cable insulation damaged | 0.18737 | 0.78589 | 1.9143 | Rectified
Pavagada | September | Inverter 1 | RISO fault | 3484 | 44814 | 0.25417 | 44814 | 0.27153 | 0.41667 | Inverter started late due to Riso fault | 0.0028125 | 0.8184 | 8.0193 | Reset and Restart
Pavagada | September | Inverter 4 | RISO fault | 3488 | 44814 | 0.25417 | 44814 | 0.27153 | 0.41667 | Inverter started late due to Riso fault | 0.0028125 | 0.8184 | 8.0285 | Reset and Restart
Pavagada | September | Inverter 20 | RISO fault | 3545.6 | 44814 | 0.25417 | 44814 | 0.27986 | 0.61667 | Inverter started late due to Riso fault | 0.0087875 | 0.8184 | 25.4988 | Reset and Restart
Pavagada | September | Inverter 20 | RISO fault | 3545.6 | 44815 | 0.25486 | 44815 | 0.27361 | 0.45 | Inverter started late due to Riso fault | 0.003879 | 0.77096 | 10.6033 | Reset and Restart
Pavagada | September | Inverter 10 | PDP Pro fault | 3529.5 | 44815 | 0.41806 | 44815 | 0.42222 | 0.1 | Inverter tripped due to PDP Pro fault | 0.088846 | 0.77096 | 241.7578 | Inform to Service Engineer
Pavagada | September | Inverter 10 | PDP Pro fault | 3529.5 | 44815 | 0.44236 | 44815 | 0.44792 | 0.13333 | Inverter tripped due to PDP Pro fault | 0.075985 | 0.77096 | 206.7628 | Inform to Service Engineer
Pavagada | September | Inverter 10 | PDP Pro fault | 3529.5 | 44815 | 0.4875 | 44815 | 0.49306 | 0.13333 | Inverter tripped due to PDP Pro fault | 0.064211 | 0.77096 | 174.7229 | Inform to Service Engineer
Pavagada | September | Inverter 10 unit -3 | PDP Pro fault | 851.5 | 44815 | 0.49306 | 44815 | 0.58611 | 2.2333 | Inverter tripped due to PDP Pro fault | 1.8915 | 0.77096 | 1241.7105 | as per service Engineer instructions to unit-3 turned off
Pavagada | September | Inverter 2 | RISO fault | 3510 | 44816 | 0.25139 | 44816 | 0.27153 | 0.48333 | Inverter started late due to Riso fault | 0.003161 | 0.78174 | 8.6735 | Reset and Restart
Pavagada | September | Inverter 4 | RISO fault | 3488 | 44816 | 0.25139 | 44816 | 0.26736 | 0.38333 | Inverter started late due to Riso fault | 0.0013532 | 0.78174 | 3.6897 | Reset and Restart
Pavagada | September | Inverter 10 unit -3 | PDP Pro fault | 851.5 | 44816 | 0.49306 | 44816 | 0.59028 | 2.3333 | Inverter tripped due to PDP Pro fault | 1.8577 | 0.78174 | 1236.604 | as per service Engineer instructions to unit-3 turned off
Pavagada | September | Inverter 10 | RISO fault | 3529.5 | 44817 | 0.24861 | 44817 | 0.26458 | 0.38333 | Inverter started late due to Riso fault | 0.0021927 | 0.77721 | 6.0148 | Reset and Restart
Pavagada | September | Inverter 11 | RISO fault | 3497 | 44817 | 0.24861 | 44817 | 0.27292 | 0.58333 | Inverter started late due to Riso fault | 0.0068483 | 0.77721 | 18.613 | Reset and Restart
Pavagada | September | Inverter 16 | RISO fault | 3497 | 44817 | 0.24861 | 44817 | 0.26875 | 0.48333 | Inverter started late due to Riso fault | 0.0040407 | 0.77721 | 10.9821 | Reset and Restart
Pavagada | September | Inverter 19 | RISO fault | 3507.2 | 44817 | 0.24861 | 44817 | 0.27083 | 0.53333 | Inverter started late due to Riso fault | 0.0052533 | 0.77721 | 14.3196 | Reset and Restart
Pavagada | September | Inverter 8 | RISO fault | 3516.5 | 44818 | 0.25486 | 44818 | 0.27153 | 0.4 | Inverter started late due to Riso fault | 0.0054 | 0.76036 | 14.4385 | Reset and Restart
Pavagada | September | Inverter 9 | RISO fault | 3477.5 | 44818 | 0.25486 | 44818 | 0.27083 | 0.38333 | Inverter started late due to Riso fault | 0.0046882 | 0.76036 | 12.3962 | Reset and Restart
Pavagada | September | Inverter 11 | RISO fault | 3497 | 44818 | 0.25486 | 44818 | 0.27778 | 0.55 | Inverter started late due to Riso fault | 0.013233 | 0.76036 | 35.1862 | Reset and Restart
Pavagada | September | Inverter 19 | RISO fault | 3507.2 | 44818 | 0.25486 | 44818 | 0.29028 | 0.85 | Inverter started late due to Riso fault | 0.042143 | 0.76036 | 112.3841 | Reset and Restart
Polepally | April | SCB.25.05 | String fault | 9 | 44655 | 0.27431 | 44655 | 0.44792 | 4.1667 | 20amps fuse blown | 1.7435 | 0.76895 | 12.0659 | Replaced with new fuse.
Polepally | April | SCB.09.06 | String fault | 9 | 44657 | 0.27361 | 44657 | 0.49167 | 5.2333 | 20amps fuse blown | 3.01 | 0.76801 | 20.8055 | Replaced with new fuse.
Polepally | April | All Inverters | 132KV LA failure | 28421.435 | 44658 | 0.66736 | 44658 | 0.75139 | 2.0167 | 132KV LA (R-phase) flash over happened at Line bay. | 0.39888 | 0.72298 | 8196.2552 | LA isolated & charged the plant
Polepally | April | All Inverters | Grid failure | 28421.435 | 44677 | 0.50903 | 44677 | 0.525 | 0.38333 | Incomer failure at substation end | 0.2827 | 0.79079 | 6353.8305 | Grid supply resumed automatically
Polepally | April | Inverter 30 | Comm. failure | 959.4 | 44677 | 0.52569 | 44677 | 0.5625 | 0.88333 | Communication disturbed | 0.7634 | 0.79079 | 579.1828 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 02 | Comm. failure | 974.025 | 44684 | 0.61667 | 44684 | 0.65556 | 0.93333 | Communication disturbed | 0.49 | 0.76703 | 366.0838 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44695 | 0.43542 | 44695 | 0.45486 | 0.46667 | Communication disturbed | 0.419 | 0.77733 | 281.4063 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44695 | 0.46597 | 44695 | 0.47708 | 0.26667 | Communication disturbed | 0.259 | 0.77733 | 173.9481 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44696 | 0.43958 | 44696 | 0.45 | 0.25 | Communication disturbed | 0.24 | 0.78808 | 163.4155 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 01 | Comm. failure | 974.925 | 44697 | 0.26458 | 44697 | 0.30208 | 0.9 | Communication disturbed | 0.13 | 0.77222 | 97.8709 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44697 | 0.43194 | 44697 | 0.44444 | 0.3 | Communication disturbed | 0.263 | 0.77222 | 175.4722 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44697 | 0.45694 | 44697 | 0.47569 | 0.45 | Communication disturbed | 0.421 | 0.77222 | 280.889 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44697 | 0.48403 | 44697 | 0.50139 | 0.41667 | Communication disturbed | 0.407 | 0.77222 | 271.5482 | Kepted Auxillary supply OFF condition 10 min & Restarted
Polepally | May | Inverter 22 | Comm. failure | 864 | 44697 | 0.51111 | 44697 | 0.76042 | 5.9833 | Communication disturbed | 2.946 | 0.77222 | 1965.5555 | Inverter not restrated & kept in off mode
Polepally | May | Inverter 01 | DC switch issue | 974.925 | 44702 | 0.2625 | 44702 | 0.30903 | 1.1167 | DC Switch issue | 0.087 | 0.83127 | 70.5072 | DC breaker reset done & started the inverter
Polepally | May | SCB.06.04 | String fault | 9 | 44702 | 0.2625 | 44702 | 0.51319 | 6.0167 | 20 amps fuse blown | 2.45 | 0.83127 | 18.3296 | Replaced with new fuse.
Polepally | May | SCB.03.02 | String fault | 9 | 44703 | 0.25625 | 44703 | 0.45208 | 4.7 | 20 amps fuse blown | 2.34 | 0.80539 | 16.9615 | Replaced with new fuse.
Polepally | June | Inverter 22 | Comm. failure | 864 | 44728 | 0.70556 | 44728 | 0.74167 | 0.86667 | Communication disturbed | 1.14 | 0.84467 | 831.9699 | buffer module bypassed & restarted the inverter
Polepally | June | Inverter 04 | Comm. failure | 974.025 | 44741 | 0.44583 | 44741 | 0.45208 | 0.15 | Communication disturbed | 0.12 | 0.81632 | 95.414 | Kepted Auxillary supply OFF condition 5 min & Restarted
Polepally | June | Inverter 04 | Comm. failure | 974.025 | 44741 | 0.45833 | 44741 | 0.46944 | 0.26667 | Communication disturbed | 0.17 | 0.81632 | 135.1698 | Kepted Auxillary supply OFF condition 5 min & Restarted
Polepally | July | All Inverters | Grid failure | 28421.435 | 44755 | 0.57014 | 44755 | 0.58056 | 0.25 | Incomer failure at substation end | 0.06 | 0.91773 | 1564.9865 | Grid supply resumed automatically
Polepally | July | Inverter 22 | Comm. failure | 864 | 44766 | 0.41181 | 44766 | 0.43333 | 0.51667 | Communication disturbed | 0.25 | 0.84572 | 182.6765 | Kepted Auxillary supply OFF condition 5 min & Restarted
Polepally | July | SCB.26.01 | String fault | 9 | 44771 | 0.27083 | 44771 | 0.45278 | 4.3667 | 20 amps fuse blown | 2.04 | 0.79914 | 14.6722 | Replaced with new fuse.
Polepally | August | SCB.14.03 | String fault | 8.77 | 44797 | 0.26458 | 44797 | 0.67083 | 9.75 | String cable damage | 5.7257 | 0.8076 | 40.5533 | Damage cable replaced
Polepally | August | SCB.11.03 | String fault | 8.77 | 44797 | 0.26458 | 44797 | 0.51806 | 6.0833 | 04Amps Fuse Blown | 3.7104 | 0.8076 | 26.2796 | Replaced with new fuse.
Polepally | August | SCB.08.04 | String fault | 8.77 | 44797 | 0.26458 | 44797 | 0.5 | 5.65 | 04Amps Fuse Blown | 3.2686 | 0.8076 | 23.1505 | Replaced with new fuse.
Polepally | September | IDT 01 | Master trip relay operated | 1948.05 | 44813 | 0.59653 | 44813 | 0.59861 | 0.05 | Master Trip relay operated | 0.03 | 0.84845 | 49.5849 | Relay reset & charged the breaker.
Prayagraj | April | Inverter 08.04 | Contactor fault | 864.5 | 44658 | 0.30486 | 44658 | 0.76181 | 10.9667 | Contactor Fault | 1.5128 | 0.76129 | 995.5988 | Inverter check & found Unit 4 contactor issue, so unit 4 stop and other 1,2,3 unit run as usual. After generation hour replaced the new coil & pcb.
Prayagraj | April | Inverter 10.04 | Contactor fault | 844.77 | 44659 | 0.30069 | 44659 | 0.76458 | 11.1333 | Contactor Fault | 2.1176 | 0.75072 | 1342.9621 | Inverter check & found Unit 4 contactor issue, so unit 4 stop and other 1,2,3 unit run as usual. After generation hour replaced the new coil & pcb.
Prayagraj | April | Inverter 03.02 | Contactor fault | 910 | 44660 | 0.3 | 44660 | 0.76528 | 11.1667 | Contactor Fault | 2.04 | 0.74848 | 1389.4738 | Inverter check & found Unit 2 contactor issue, so unit 2 stop and other 1,3,4 unit run as usual. After generation hour replaced the new coil & pcb.
Prayagraj | April | Inverter 08.02 | Contactor fault | 792.9 | 44661 | 0.30069 | 44661 | 0.76528 | 11.15 | Contactor Fault | 1.6618 | 0.73579 | 969.5355 | Inverter check & found Unit 2 contactor issue, so unit 2 stop and other 1,3,4 unit run as usual. After generation hour replaced the new coil & pcb.
Prayagraj | April | Inverter 05 | Ground fault | 3604.405 | 44664 | 0.42083 | 44664 | 0.43681 | 0.38333 | GND Fault | 0.27514 | 0.76779 | 761.4288 | Checked floating voltage and replace the new fuse.
Prayagraj | April | All Inverters | Grid failure | 68557.27 | 44670 | 0.59028 | 44670 | 0.60278 | 0.3 | All inverter goes to breakdown due to grid frequency mismatched | 0.20993 | 0.76261 | 10975.6021 | All parameter checked and found inverter tripped due F fault after that all inverter restart manually one by one
Prayagraj | April | All Inverters | Grid failure | 68557.27 | 44671 | 0.59931 | 44671 | 0.60139 | 0.05 | All inverter goes to breakdown due to grid frequency mismatched | 0.05 | 0.74482 | 2553.1309 | All parameter checked and found inverter tripped due F fault after that all inverter restart manually one by one
Prayagraj | April | All Inverters | Grid failure | 68557.27 | 44671 | 0.60486 | 44671 | 0.60833 | 0.083333 | All inverter goes to breakdown due to grid frequency mismatched | 0.06 | 0.74482 | 3063.7571 | All parameter checked and found inverter tripped due F fault after that all inverter restart manually one by one
Prayagraj | April | All Inverters | Grid failure | 68557.27 | 44671 | 0.67917 | 44671 | 0.68472 | 0.13333 | All inverter goes to breakdown due to grid frequency mismatched | 0.04 | 0.74482 | 2042.5047 | All parameter checked and found inverter tripped due to F fault .Issue discuss with OEM and frequency parameter changed after that issue was closed .
Prayagraj | May | Inverter 06 | PDP Pro Fault | 3425.83 | 44700 | 0.28542 | 44700 | 0.29722 | 0.28333 | PDP Protection fault | 0.05474 | 0.73069 | 137.0281 | Inverter auto restart.
Prayagraj | May | All Inverters | Grid failure | 68557.27 | 44704 | 0.65764 | 44704 | 0.72292 | 1.5667 | Under volatge triping from Meja GSS, | 0.17 | 0.73196 | 8530.8128 | Line tripped from Meja gss after issue resolve then breaker on and line charged.
Prayagraj | June | All Inverters | Grid failure | 68557.27 | 44724 | 0.73958 | 44724 | 0.76458 | 0.6 | 132KV Line triping due to line maintenance. | 0.037833 | 0.76255 | 1977.8762 | Line tripped & shutdown from Meja GSS due to line maintenance.
Prayagraj | June | Inverter 05 | Ground fault | 3604.405 | 44728 | 0.36528 | 44728 | 0.37847 | 0.31667 | GND Fault | 0.014461 | 0.87947 | 45.8408 | Check Scb current floating and ground fuse. Found ground fuse blowen then replace it and inverter start.
Prayagraj | June | Inverter 20 | Ground fault | 3454.2 | 44728 | 0.38125 | 44728 | 0.42014 | 0.93333 | GND Fault | 0.1066 | 0.87947 | 323.8335 | Check Scb current floating and ground fuse. Found ground fuse blowen then replace it and inverter start.
Prayagraj | June | Inverter 01 | Ground fault | 3437 | 44740 | 0.60625 | 44740 | 0.61458 | 0.2 | GND Fault | 0.0057352 | 0.84305 | 16.6181 | Check Scb current floating and ground fuse. Found ground fuse blowen then replace it and inverter start.
Prayagraj | June | Inverter 03 | Ground fault | 3476.785 | 44740 | 0.60625 | 44740 | 0.61458 | 0.2 | GND Fault | 0.0057352 | 0.84305 | 16.8105 | Check Scb current floating and ground fuse. Found ground fuse blowen then replace it and inverter start.
Prayagraj | June | Inverter 04 | Ground fault | 3424.2 | 44740 | 0.60625 | 44740 | 0.61458 | 0.2 | GND Fault | 0.0057352 | 0.84305 | 16.5562 | Check Scb current floating and ground fuse. Found ground fuse blowen then replace it and inverter start.
Prayagraj | June | All Inverters | Grid failure | 68557.27 | 44740 | 0.61528 | 44740 | 0.65972 | 1.0667 | 132KV Line triped from Meja GSS, | 0.42978 | 0.84305 | 24839.9049 | Line tripped from Meja gss after issue resolve then breaker on and line charged.
Prayagraj | June | SCB.02.02.03 | String fault | 0 | 44742 | 0.22222 | 44742 | 0.78611 | 13.5333 | 23Nos Modules in diode failure issues | 3.48 | 0.87307 | 0 | PV Module replacement work is in under progress.
Prayagraj | July | SCB.02.02.03 | String fault | 0 | 44743 | 0.22014 | 44743 | 0.47222 | 6.05 | 23 nos. PV Module diode failure due to lighting issue & 1 nos Module in JB Broken issue. | 3.48 | 0.81844 | 0 | All modules replaced as per requirement & String restoration work complete.
Prayagraj | July | All Inverters | Grid failure | 68557.27 | 44743 | 0.47222 | 44743 | 0.76736 | 7.0833 | 132 line trip from Meja GSS,after line visual inspection in line jumper found broken at 6.535 KM from Meja GSS. | 3.2105 | 0.81844 | 180138.4097 | 132 line trip from Meja GSS,after line visual inspection in line jumper found broken at 6.535 KM from Meja GSS. Grid line restored after line jumper rectification work completed.
Prayagraj | July | All Inverters | Grid failure | 68557.27 | 44746 | 0.60764 | 44746 | 0.78125 | 4.1667 | Grid down due to Line maintenance Meja GSS. | 1.47 | 0.81886 | 82523.9414 | Shutdown from Meja GSS due to line maintenance.
Prayagraj | July | Inverter 18.03 | L over temp. fault | 844.8 | 44750 | 0.49444 | 44750 | 0.50278 | 0.2 | Reactor temp Issue | 0.20184 | 0.77765 | 132.6015 | First key stop the inverter and then called the SunGrow Engineer. after that we are opened the inverter door. after that turn on the inverter as per instructed by the Sungrow Engineer.
Prayagraj | July | Inverter 18.03 | L over temp. fault | 844.8 | 44752 | 0.54167 | 44752 | 0.54931 | 0.18333 | Reactor temp Issue | 0.17689 | 0.77915 | 116.4364 | First key stop the inverter and then called the SunGrow Engineer. after that we are opened the inverter door. after that turn on the inverter as per instructed by the Sungrow Engineer.
Prayagraj | July | Inverter 18.03 | L over temp. fault | 844.8 | 44754 | 0.59028 | 44754 | 0.60139 | 0.26667 | Reactor temp Issue | 0.12056 | 0.78211 | 79.656 | First key stop the inverter and then called the SunGrow Engineer. after that we are opened the inverter door. after that turn on the inverter as per instructed by the Sungrow Engineer.
Prayagraj | July | Inverter 18.03 | L over temp. fault | 844.8 | 44759 | 0.52569 | 44759 | 0.53681 | 0.26667 | Reactor temp Issue | 0.24637 | 0.76391 | 158.9946 | First key stop the inverter and then called the SunGrow Engineer. after that we are opened the inverter door. after that turn on the inverter as per instructed by the Sungrow Engineer.
Prayagraj | July | Inverter 05 | Ground fault | 3604.405 | 44762 | 0.28056 | 44762 | 0.29931 | 0.45 | GND Fault | 0.1001 | 0.80397 | 290.0856 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 17.02 | L over temp. fault | 862.8 | 44764 | 0.54236 | 44764 | 0.55556 | 0.31667 | Reactor temp Issue | 0.19964 | 0.79908 | 137.6416 | First key stop the inverter and then called the SunGrow Engineer. after that we are opened the inverter door. after that turn on the inverter as per instructed by the Sungrow Engineer.
Prayagraj | July | Inverter 05 | Ground fault | 3604.405 | 44768 | 0.25347 | 44768 | 0.26736 | 0.33333 | GND Fault | 0.029886 | 0.7918 | 85.294 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 20 | Ground fault | 3454.2 | 44768 | 0.22708 | 44768 | 0.24722 | 0.48333 | GND Fault | 0.0063504 | 0.7918 | 17.3685 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 01 | Ground fault | 3437 | 44769 | 0.23681 | 44769 | 0.24514 | 0.2 | GND Fault | 0.0009033 | 0.79494 | 2.468 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 02 | Ground fault | 3431.2 | 44769 | 0.23681 | 44769 | 0.25069 | 0.33333 | GND Fault | 0.0016469 | 0.79494 | 4.492 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 03 | Ground fault | 3476.785 | 44769 | 0.23681 | 44769 | 0.25833 | 0.51667 | GND Fault | 0.0051274 | 0.79494 | 14.1712 | Check floating voltage and replace the new fuse.
Prayagraj | July | Inverter 04 | Ground fault | 3424.2 | 44769 | 0.23681 | 44769 | 0.26389 | 0.65 | GND Fault | 0.0079077 | 0.79494 | 21.525 | Check floating voltage and replace the new fuse.
Prayagraj | July | SCB.01.01.02 | String fault | 0 | 44769 | 0.24375 | 44769 | 0.37847 | 3.2333 | Floating Voltage Unbalance | 0.37054 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.01.01.03 | String fault | 0 | 44769 | 0.24375 | 44769 | 0.32361 | 1.9167 | Floating Voltage Unbalance | 0.21802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.01.01.04 | String fault | 0 | 44769 | 0.24375 | 44769 | 0.32778 | 2.0167 | Floating Voltage Unbalance | 0.21802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.01.03.02 | String fault | 0 | 44769 | 0.24375 | 44769 | 0.36111 | 2.8167 | Floating Voltage Unbalance | 0.31758 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.02.01.05 | String fault | 0 | 44769 | 0.24722 | 44769 | 0.33194 | 2.0333 | Floating Voltage Unbalance | 0.23802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.02.02.05 | String fault | 0 | 44769 | 0.24722 | 44769 | 0.35903 | 2.6833 | Floating Voltage Unbalance | 0.23802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.03.01.02 | String fault | 0 | 44769 | 0.25764 | 44769 | 0.38333 | 3.0167 | Floating Voltage Unbalance | 0.23802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.03.02.05 | String fault | 0 | 44769 | 0.25764 | 44769 | 0.33819 | 1.9333 | Floating Voltage Unbalance | 0.24802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.03.04.02 | String fault | 0 | 44769 | 0.25764 | 44769 | 0.34444 | 2.0833 | Floating Voltage Unbalance | 0.24802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.03.04.05 | String fault | 0 | 44769 | 0.25764 | 44769 | 0.34514 | 2.1 | Floating Voltage Unbalance | 0.24802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.01.02 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.34722 | 2.0333 | Floating Voltage Unbalance | 0.24802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.01.05 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.37708 | 2.75 | Floating Voltage Unbalance | 0.38989 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.03.02 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.34861 | 2.0667 | Floating Voltage Unbalance | 0.25802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.03.03 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.35 | 2.1 | Floating Voltage Unbalance | 0.25802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.04.01 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.35069 | 2.1167 | Floating Voltage Unbalance | 0.25802 | 0.79494 | 0 | Check floating voltage found ok then start.
Prayagraj | July | SCB.04.04.03 | String fault | 0 | 44769 | 0.2625 | 44769 | 0.78056 | 12.4333 | DC Cable insulation failed | 3.9293 | 0.79494 | 0 | 300SQMM DC Cable Changed (250m)
Prayagraj | July | Inverter 05 | Ground fault | 3604.405 | 44770 | 0.57639 | 44770 | 0.58333 | 0.16667 | GND Fault | 0.023901 | 0.82745 | 71.2825 | Check floating voltage and replace the new fuse.
Prayagraj | July | SCB.02.01.01 | String fault | 0 | 44770 | 0.22569 | 44770 | 0.34722 | 2.9167 | GND Fault | 0.8846 | 0.82745 | 0 | String restoration work complete.
Prayagraj | July | SCB.02.01.01 | String fault | 0 | 44770 | 0.22569 | 44770 | 0.4125 | 4.4833 | GND Fault | 1.1846 | 0.82745 | 0 | String restoration work complete.
Prayagraj | July | SCB.02.01.01 | String fault | 0 | 44770 | 0.22569 | 44770 | 0.49722 | 6.5167 | GND Fault | 2.456 | 0.82745 | 0 | String restoration work complete.
Prayagraj | July | SCB.01.01.02 | String fault | 0 | 44770 | 0.22569 | 44770 | 0.52083 | 7.0833 | GND Fault | 2.838 | 0.82745 | 0 | String restoration work complete.
Prayagraj | July | SCB.05.02.03 | String fault | 0 | 44771 | 0.22708 | 44771 | 0.35417 | 3.05 | GND Fault | 0.56946 | 0.7892 | 0 | String restoration work complete.
Prayagraj | August | SCB.02.03.02 | String fault | 0 | 44776 | 0.23194 | 44776 | 0.78542 | 13.2833 | 08Nos Modules in diode failure issues | 5.6197 | 0.78146 | 0 | PV Module replacement work is in under progress.
Prayagraj | August | SCB.03.03.05 | String fault | 0 | 44776 | 0.23194 | 44776 | 0.78542 | 13.2833 | 08Nos Modules in diode failure issues | 5.6197 | 0.78146 | 0 | PV Module replacement work is in under progress.
Prayagraj | August | SCB.02.03.02 | String fault | 0 | 44777 | 0.24028 | 44777 | 0.54861 | 7.4 | Block-01,I-2C,CB-02 St-6:- 08Nos Modules in diode failure issues | 2.8413 | 0.82099 | 0 | Diode failure PV Module replacement work complete
Prayagraj | August | SCB.03.03.05 | String fault | 0 | 44777 | 0.24028 | 44777 | 0.68125 | 10.5833 | Block-02,I-1C,CB-05 St-13-:08Nos Modules in diode failure issues | 3.8474 | 0.82099 | 0 | Diode failure PV Module replacement work complete
Prayagraj | August | SCB.02.03.05 | String fault | 0 | 44778 | 0.22847 | 44778 | 0.41528 | 4.4833 | Block-01,I-2C,CB-05 St-10:- 320 W 10 Module restoration work done | 1.3912 | 0.77892 | 0 | 1 nos Half string under breakdown from 5:29 Hrs to 09:58 Hrs due to 320 Wp modules replacement work (10 module changed) at Block-01,I-2C,CB-05 St-10.
Prayagraj | August | Inverter 19 | Ground fault | 3480.6 | 44781 | 0.23264 | 44781 | 0.25347 | 0.5 | GND Fault | 0.0083376 | 0.79385 | 23.0374 | Check floating voltage and replace the new fuse.
Prayagraj | August | SCB.19.04.05 | String fault | 0 | 44781 | 0.23264 | 44781 | 0.40347 | 4.1 | Block-10,I-1D,CB-05 St-11 nos string under breakdown from 5:35 Hrs to 09:41 Hrs due to string cable fault. | 1.2012 | 0.79385 | 0 | Faulty String cable changed
Prayagraj | August | SCB.19.04.05 | String fault | 0 | 44781 | 0.23264 | 44781 | 0.41319 | 4.3333 | Block-10,I-1D,CB-05 St-14 nos string under breakdown from 5:35 Hrs to 09:55 Hrs due to string cable fault. | 1.2311 | 0.79385 | 0 | Faulty Line fuse changed
Prayagraj | August | All Inverters | Grid failure | 68557.27 | 44782 | 0.7375 | 44782 | 0.76944 | 0.76667 | 132 line trip from Meja GSS. | 0.047279 | 0.78784 | 2553.6069 | Grid line restored after line charged
Prayagraj | August | SCB.09.04.05 | String fault | 0 | 44785 | 0.22986 | 44785 | 0.525 | 7.0833 | Block-05,I-1D,CB-05 St-14 nos string under breakdown from 5:31 Hrs to 13:36 Hrs due to string cable fault. | 2.8 | 0.81382 | 0 | String restoration work complete.
Prayagraj | August | SCB.17.02.03 | String fault | 0 | 44786 | 0.22986 | 44786 | 0.62292 | 9.4333 | Block-09,I-1B,CB-03 St-11 nos string under breakdown from 5:31 Hrs to 14:57 Hrs due to string cable fault. | 4.8505 | 0.78161 | 0 | String restoration work complete.
Prayagraj | August | SCB.02.04.04 | String fault | 0 | 44790 | 0.22986 | 44790 | 0.46528 | 5.65 | Block-01,I-2D,CB-04 St-03 Half nos string under breakdown from 5:31 Hrs to 11:10 Hrs due to MC4 Connector melt. | 2.8009 | 0.76729 | 0 | String restoration work complete.
Prayagraj | August | SCB.02.04.04 | String fault | 0 | 44791 | 0.22917 | 44791 | 0.43056 | 4.8333 | Block-04,I-2B,CB-4,st-2 Half nos string under breakdown from 5:30 Hrs to 10:20 Hrs due to MC4 Connector melt. | 2.011 | 0.80038 | 0 | String restoration work complete.
Prayagraj | August | SCB.02.04.04 | String fault | 0 | 44791 | 0.22917 | 44791 | 0.61111 | 9.1667 | Block-06,I-2C,CB-2,st-1 One nos string under breakdown from 5:30 Hrs to 14:40 Hrs due String cable Fault. | 5.167 | 0.80038 | 0 | String restoration work complete.
Prayagraj | August | Inverter 01 | PT 01 tripped | 34339 | 44799 | 0.24306 | 44799 | 0.36528 | 33.47 | Block-1 Under breakdown from due to 25 MVA Power trafo-1 trip in buchholz relay operated | 5.167 | 0.7801 | 13853.7709 | This Panel Restore after load shifting done with buscupler to Power trafo-2
Prayagraj | August | Inverter 01 | PT 02 tripped | 41087 | 44799 | 0.56667 | 44799 | 0.76389 | 4.7333 | This Panel under breakdown due to Power trafo-2 trip in Overload | 2.3096 | 0.7801 | 74964 | This Panel Restore after restoration work completed of Power trafo-1.
Prayagraj | August | Inverter 09 | Block 05 tripped on EF | 6811 | 44800 | 0.24236 | 44800 | 0.75694 | 12.35 | Block-5 Outgoing HT Panel trip in OC/EF | 5.8936 | 0.64274 | 25802 | This block restored after bypass of Block-5 Outgoing HT Panel via using Incomer busbar Jumper linking.
Prayagraj | August | Inverter 11 | Block 06 tripped on EF | 6881 | 44800 | 0.24236 | 44800 | 0.75694 | 12.35 | Block-5 Outgoing HT Panel trip in OC/EF | 5.8936 | 0.64274 | 26066 | This block restored after bypass of Block-5 Outgoing HT Panel via using Incomer busbar Jumper linking.
Prayagraj | August | Inverter 17 | RISO fault | 3353.9 | 44802 | 0.24583 | 44802 | 0.27986 | 0.81667 | RISO FAULT | 0.035591 | 0.83343 | 99.4854 | System check found ok then inverter start.
Prayagraj | August | Inverter 20 | RISO fault | 3454.2 | 44802 | 0.24583 | 44802 | 0.27639 | 0.73333 | RISO FAULT | 0.028729 | 0.83343 | 82.7049 | System check found ok then inverter start.
Prayagraj | August | Inverter 19 | RISO fault | 3480.6 | 44802 | 0.24583 | 44802 | 0.27639 | 0.73333 | RISO FAULT | 0.028729 | 0.83343 | 83.337 | System check found ok then inverter start.
Prayagraj | August | Inverter 20 | Ground fault | 3454.2 | 44802 | 0.3875 | 44802 | 0.40764 | 0.48333 | GND Fault | 0.17708 | 0.83343 | 509.7912 | Check floating voltage and replace the new fuse.
Prayagraj | August | SCB.20.03.02 | String fault | 0 | 44803 | 0.26944 | 44803 | 0.45833 | 4.5333 | Block-10,I-2C,CB-02 St-01 One nos string under breakdown from 6:28 Hrs to 11:00 Hrs due to MC4 connector Moisture issues . | 1.906 | 0.79847 | 0 | String restoration work complete.
Prayagraj | August | SCB.20.03.02 | String fault | 0 | 44803 | 0.26944 | 44803 | 0.45833 | 4.5333 | Block-10,I-2C,CB-02 St-09 One nos string under breakdown from 6:28 Hrs to 11:00 Hrs due to MC4 connector Moisture issues . | 1.906 | 0.79847 | 0 | String restoration work complete.
Prayagraj | August | Inverter 20 | L over temp. fault | 3454.2 | 44804 | 0.51736 | 44804 | 0.53819 | 0.5 | Reactor Temp exceeded as per set value. | 0.30334 | 0.79821 | 836.3605 | Check alarm /fault and restart as per instruction Sungrow's Engineer
Prayagraj | September | Inverter 01 | Ground fault | 3437 | 44806 | 0.59514 | 44806 | 0.60903 | 0.33333 | GND Fault | 0.037098 | 0.80442 | 102.5672 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | SCB.01.01.03 | String fault | 0 | 44806 | 0.60903 | 44806 | 0.71528 | 2.55 | SCB under breakdown due to Floating voltage abnormal | 0.19361 | 0.80442 | 0 | Faulty string isolated from SCB end and SCB restored.
Prayagraj | September | SCB.01.02.02 | String fault | 0 | 44806 | 0.60903 | 44806 | 0.71528 | 2.55 | SCB under breakdown due to Floating voltage abnormal | 0.19361 | 0.80442 | 0 | Faulty string isolated from SCB end and SCB restored.
Prayagraj | September | SCB.01.03.03 | String fault | 0 | 44806 | 0.60903 | 44806 | 0.71528 | 2.55 | SCB under breakdown due to Floating voltage abnormal | 0.19361 | 0.80442 | 0 | Faulty string isolated from SCB end and SCB restored.
Prayagraj | September | SCB.01.01.03 | String fault | 0 | 44806 | 0.71528 | 44806 | 0.75694 | 1 | Water ingress issue in MC4 connector . | 0.19361 | 0.80442 | 0 | It will be check tomorrow and restored it.
Prayagraj | September | SCB.01.02.02 | String fault | 0 | 44806 | 0.71528 | 44806 | 0.75694 | 1 | Water ingress issue in MC4 connector . | 0.19361 | 0.80442 | 0 | It will be check tomorrow and restored it.
Prayagraj | September | SCB.01.03.03 | String fault | 0 | 44806 | 0.71528 | 44806 | 0.75694 | 1 | Water ingress issue in MC4 connector . | 0.19361 | 0.80442 | 0 | It will be check tomorrow and restored it.
Prayagraj | September | SCB.01.01.03 | String fault | 0 | 44807 | 0.2375 | 44807 | 0.44306 | 4.9333 | B-01,I-1D,CB-5 Water ingress issue in MC4 connector . | 1.7127 | 0.84198 | 0 | String restoration work complete.
Prayagraj | September | SCB.01.02.02 | String fault | 0 | 44807 | 0.2375 | 44807 | 0.45069 | 5.1167 | B-01,I-1C,CB-3,St-1 Water ingress issue in MC4 connector . | 1.7573 | 0.84198 | 0 | String restoration work complete.
Prayagraj | September | SCB.01.03.03 | String fault | 0 | 44807 | 0.2375 | 44807 | 0.45694 | 5.2667 | B-01,I-1B,CB-2,St-03 Water ingress issue in MC4 connector . | 1.8 | 0.84198 | 0 | String restoration work complete.
Prayagraj | September | Inverter 04 | PDP Pro Fault | 3424.2 | 44808 | 0.44167 | 44808 | 0.44444 | 0.066667 | PDP Protection fault | 0.057384 | 0.78669 | 154.5799 | Inverter auto restart.
Prayagraj | September | Inverter 01.04 | L over temp. fault | 818.8 | 44808 | 0.55903 | 44808 | 0.58056 | 0.51667 | Reactor Temp exceeded as per set value. | 0.32041 | 0.78669 | 206.3876 | Check alarm /fault and restart as per instruction Sungrow's Engineer
Prayagraj | September | Inverter 16 | Ground fault | 3382.525 | 44812 | 0.525 | 44812 | 0.5625 | 0.9 | GND Fault | 0.036288 | 0.81706 | 100.2902 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | Inverter 19 | Ground fault | 3480.6 | 44812 | 0.525 | 44812 | 0.57986 | 1.3167 | GND Fault | 0.072419 | 0.81706 | 205.9491 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | Inverter 13 | Ground fault | 3316.81 | 44812 | 0.525 | 44812 | 0.55278 | 0.66667 | GND Fault | 0.02146 | 0.81706 | 58.1582 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | Inverter 17 | Ground fault | 3353.9 | 44812 | 0.525 | 44812 | 0.57014 | 1.0833 | GND Fault | 0.049118 | 0.81706 | 134.5996 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | Inverter 20 | Ground fault | 3454.2 | 44812 | 0.525 | 44812 | 0.58333 | 1.4 | GND Fault | 0.08315 | 0.81706 | 234.6748 | Check floating voltage and replace the faulty fuse with spare a new fuse. And isolated the suspected SCB from Inverter End.
Prayagraj | September | SCB.13.01.02 | String fault | 0 | 44812 | 0.55347 | 44812 | 0.64931 | 2.3 | Floating Voltage Unbalance | 0.51 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.13.02.01 | String fault | 0 | 44812 | 0.55347 | 44812 | 0.64931 | 2.3 | Floating Voltage Unbalance | 0.51 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.13.03.01 | String fault | 0 | 44812 | 0.55347 | 44812 | 0.65972 | 2.55 | Floating Voltage Unbalance | 0.58 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.16.03.03 | String fault | 0 | 44812 | 0.56319 | 44812 | 0.66528 | 2.45 | Floating Voltage Unbalance | 0.56524 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.17.01.05 | String fault | 0 | 44812 | 0.57083 | 44812 | 0.68681 | 2.7833 | Floating Voltage Unbalance | 0.67638 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.17.04.02 | String fault | 0 | 44812 | 0.57083 | 44812 | 0.70347 | 3.1833 | Floating Voltage Unbalance | 0.7371 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.19.01.02 | String fault | 0 | 44812 | 0.58056 | 44812 | 0.67431 | 2.25 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.19.01.05 | String fault | 0 | 44812 | 0.58056 | 44812 | 0.67431 | 2.25 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.19.03.01 | String fault | 0 | 44812 | 0.58056 | 44812 | 0.67431 | 2.25 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.19.04.02 | String fault | 0 | 44812 | 0.58056 | 44812 | 0.67431 | 2.25 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.20.01.01 | String fault | 0 | 44812 | 0.58403 | 44812 | 0.675 | 2.1833 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.20.01.04 | String fault | 0 | 44812 | 0.58403 | 44812 | 0.675 | 2.1833 | Floating Voltage Unbalance | 0.59523 | 0.81706 | 0 | Check floating voltage found ok then start.
Prayagraj | September | SCB.13.03.01 | String fault | 0 | 44812 | 0.66042 | 44812 | 0.75486 | 2.2667 | String 13 Floating Voltage Unbalance | 0.26395 | 0.81706 | 0 | Check floating voltage found not ok then string open and start.
Prayagraj | September | SCB.17.01.05 | String fault | 0 | 44812 | 0.68681 | 44812 | 0.75486 | 1.6333 | String 13 Floating Voltage Unbalance | 0.1269 | 0.81706 | 0 | Check floating voltage found not ok then string open and start.
Prayagraj | September | SCB.13.03.01 | String fault | 0 | 44813 | 0.23958 | 44813 | 0.75903 | 12.4667 | String 13 Floating Voltage Unbalance | 5.4409 | 0.77842 | 0 | Check floating voltage found not ok then string open and start.
Prayagraj | September | SCB.17.01.05 | String fault | 0 | 44813 | 0.23958 | 44813 | 0.75903 | 12.4667 | String 05 Floating Voltage Unbalance | 5.4409 | 0.77842 | 0 | Check floating voltage found not ok then string open and start.
Prayagraj | September | All Inverters | Grid failure | 68557.27 | 44814 | 0.25208 | 44814 | 0.29028 | 0.91667 | Grid failed from Meja GSS | 0.089536 | 0.78424 | 4813.9529 | All Inverter have restored after Grid Avilable.
Prayagraj | September | Inverter 01 | VCB tripped | 6868 | 44814 | 0.29097 | 44814 | 0.47361 | 4.3833 | VCB Trip due to Master relay operate | 1.5161 | 0.78424 | 8166 | After checking and tested found that the TNC switch is faulty and restored after rectfication work completed.
Prayagraj | September | Inverter 02.02 | Contactor fault | 916.5 | 44814 | 0.47431 | 44814 | 0.75694 | 6.7833 | Contactor Fault | 2.7862 | 0.78424 | 2002.6356 | Inverter 02 have restored after rectified with replacement of conteactor coil & PCB card replaced of unit 2
Prayagraj | September | Inverter 19.01 | Island fault | 851.7 | 44814 | 0.29097 | 44814 | 0.54444 | 6.0833 | Island Fault | 2.2614 | 0.78424 | 1510.5126 | Inverter 17 restored after Inverter circuit reset.
Prayagraj | September | Inverter 19.02 | Island fault | 858 | 44814 | 0.29097 | 44814 | 0.54444 | 6.0833 | Island Fault | 2.2614 | 0.78424 | 1521.6858 | Inverter 17 restored after Inverter circuit reset.
Prayagraj | September | Inverter 01 | I Leakage Pro fault | 3437 | 44815 | 0.41389 | 44815 | 0.41806 | 0.1 | I Leakage Pro | 0.047226 | 0.79295 | 128.7086 | Inverter auto start
Prayagraj | September | Inverter 02.02 | Contactor fault | 916.5 | 44815 | 0.34861 | 44815 | 0.75625 | 9.7833 | Contactor Fault | 1.8663 | 0.79295 | 1356.3077 | Inverter 02 Unit-02 rectified work under progress
Prayagraj | September | Inverter 02 | PDP Pro Fault | 3431.2 | 44816 | 0.44375 | 44816 | 0.44583 | 0.05 | PDP Pro Fault | 0.04252 | 0.81289 | 118.5958 | Auto start
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44654 | 0.31806 | 44654 | 0.32708 | 0.21667 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.54559 | 67.5663 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44655 | 0.57917 | 44655 | 0.57986 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main Breaker Trip | 0.02 | 0.54197 | 22.3723 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44655 | 0.61944 | 44655 | 0.62014 | 0.016667 | Grid failure from 132/33 Kv Connecting substation | 0.02 | 0.54197 | 22.3723 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44656 | 0.37569 | 44656 | 0.38681 | 0.26667 | Grid failure from 132/33 Kv Connecting substation | 0.18 | 0.53701 | 199.5093 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44656 | 0.56181 | 44656 | 0.56667 | 0.11667 | Grid failure from 132/33 Kv Connecting substation | 0.12 | 0.53701 | 133.0062 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44656 | 0.65625 | 44656 | 0.65972 | 0.083333 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.53701 | 55.4193 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44657 | 0.50972 | 44657 | 0.55417 | 1.0667 | Grid failure from 33/11 Kv Connecting substation, CT Burnt | 1.06 | 0.57668 | 1261.6756 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44657 | 0.57292 | 44657 | 0.57361 | 0.016667 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.57668 | 11.9026 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44657 | 0.58958 | 44657 | 0.61181 | 0.53333 | Grid failure from 132/33 Kv Connecting substation | 0.34 | 0.57668 | 404.6884 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44658 | 0.55903 | 44658 | 0.56181 | 0.066667 | Grid failure from 132/33 Kv Connecting substation | 0.07 | 0.55147 | 79.6763 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44658 | 0.68472 | 44658 | 0.76528 | 1.9333 | Grid failure from 33/11 Kv Connecting substation, Voltage Level below 9 KV | 0.24 | 0.55147 | 273.1758 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44661 | 0.43542 | 44661 | 0.43681 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Padhera Line Earth Fault | 0.03 | 0.52411 | 32.4527 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44661 | 0.51319 | 44661 | 0.51458 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Padhera Line Earth Fault | 0.04 | 0.52411 | 43.2703 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44662 | 0.69514 | 44662 | 0.69653 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Padhera Line Earth Fault | 0.01 | 0.50874 | 10.5004 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44663 | 0.35903 | 44663 | 0.36597 | 0.16667 | Grid failure from 132/33 Kv Connecting substation | 0.07 | 0.5185 | 74.9131 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44663 | 0.56389 | 44663 | 0.56597 | 0.05 | Grid failure from 33/11 Kv Connecting substation | 0.05 | 0.5185 | 53.5094 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44665 | 0.57431 | 44665 | 0.57708 | 0.066667 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.50939 | 63.0829 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44665 | 0.69861 | 44665 | 0.71181 | 0.31667 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.50939 | 63.0829 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44665 | 0.71806 | 44665 | 0.72222 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.50939 | 10.5138 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44667 | 0.68125 | 44667 | 0.69861 | 0.41667 | Grid failure from 132/33 Kv Connecting substation | 0.13 | 0.46341 | 124.3424 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44667 | 0.70278 | 44667 | 0.70556 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.46341 | 9.5648 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44668 | 0.54514 | 44668 | 0.54792 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.47828 | 69.1015 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44668 | 0.63958 | 44668 | 0.64167 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.47828 | 29.6149 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44669 | 0.37986 | 44669 | 0.38403 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.47278 | 58.549 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44669 | 0.44236 | 44669 | 0.45139 | 0.21667 | Grid failure from 132/33 Kv Connecting substation | 0.19 | 0.47278 | 185.4051 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44669 | 0.69375 | 44669 | 0.76736 | 1.7667 | Grid failure from 132/33 Kv Connecting substation | 0.21 | 0.47278 | 204.9215 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44670 | 0.65694 | 44670 | 0.77153 | 2.75 | Grid failure from 132/33 Kv Connecting substation | 0.51 | 0.4748 | 499.7969 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44671 | 0.52847 | 44671 | 0.61111 | 1.9833 | Grid failure from 132/33 Kv Connecting substation | 1.73 | 0.48679 | 1738.1765 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44671 | 0.68125 | 44671 | 0.69167 | 0.25 | Grid failure from 132/33 Kv Connecting substation | 0.07 | 0.48679 | 70.3308 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44672 | 0.62778 | 44672 | 0.62917 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.50518 | 20.854 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44672 | 0.63403 | 44672 | 0.65 | 0.38333 | Grid failure from 132/33 Kv Connecting substation | 0.15 | 0.50518 | 156.4049 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44672 | 0.65833 | 44672 | 0.71528 | 1.3667 | Grid failure from 132/33 Kv Connecting substation | 0.24 | 0.50518 | 250.2478 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44673 | 0.34236 | 44673 | 0.34583 | 0.083333 | Grid failure from 132/33 Kv Connecting substation | 0.43 | 0.49214 | 436.7881 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44674 | 0.53194 | 44674 | 0.54861 | 0.4 | Grid failure from 132/33 Kv Connecting substation | 0.38 | 0.49102 | 385.1194 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44675 | 0.23542 | 44675 | 0.26181 | 0.63333 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.49706 | 10.2592 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44675 | 0.43333 | 44675 | 0.43819 | 0.11667 | Grid failure from 132/33 Kv Connecting substation | 0.12 | 0.49706 | 123.1107 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44675 | 0.60347 | 44675 | 0.60694 | 0.083333 | Grid failure from 132/33 Kv Connecting substation | 0.07 | 0.49706 | 71.8145 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44675 | 0.67153 | 44675 | 0.67569 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.04 | 0.49706 | 41.0369 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44676 | 0.46875 | 44676 | 0.47708 | 0.2 | Grid failure from 132/33 Kv Connecting substation | 0.21 | 0.52078 | 225.727 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44676 | 0.53958 | 44676 | 0.62014 | 1.9333 | 33 KV Grid line manual shutdown from 132/33 Kv Connecting substation, due to CT Replacement | 1.7 | 0.52078 | 1827.3139 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44676 | 0.70139 | 44676 | 0.70278 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main Breaker Trip | 0.01 | 0.52078 | 10.7489 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44676 | 0.72639 | 44676 | 0.73056 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main Breaker Trip | 0.01 | 0.52078 | 10.7489 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44677 | 0.29722 | 44677 | 0.54583 | 5.9667 | 33 KV Grid line manual shutdown from 132/33 Kv Connecting substation, due to tree trimming work | 4.34 | 0.4996 | 4475.3162 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44677 | 0.56806 | 44677 | 0.57014 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Mathiya Feeder Trip | 0.05 | 0.4996 | 51.5589 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44679 | 0.37292 | 44679 | 0.37569 | 0.066667 | Grid failure from 33/11 Kv Connecting substation | 0.04 | 0.51406 | 42.4409 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44680 | 0.63264 | 44680 | 0.63403 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.54602 | 22.5397 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44680 | 0.66736 | 44680 | 0.66806 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.54602 | 11.2698 | Grid Resumed
Priapus | April | All Inverters | Ext. Grid failure | 2064 | 44681 | 0.42014 | 44681 | 0.42847 | 0.2 | Grid failure from 33/11 Kv Connecting substation, Main T/F fuse burnt | 0.16 | 0.55697 | 183.9337 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.30417 | 44682 | 0.30556 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.59439 | 12.2682 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.3125 | 44682 | 0.32847 | 0.38333 | Grid failure from 132/33 Kv Connecting substation | 0.11 | 0.59439 | 134.9502 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.33125 | 44682 | 0.34306 | 0.28333 | Grid failure from 132/33 Kv Connecting substation | 0.09 | 0.59439 | 110.4138 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.39375 | 44682 | 0.39444 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Mathiya Feeder Trip | 0.01 | 0.59439 | 12.2682 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.41736 | 44682 | 0.41875 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.59439 | 12.2682 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.44444 | 44682 | 0.59583 | 3.6333 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 2.98 | 0.59439 | 3655.9248 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44682 | 0.69097 | 44682 | 0.69306 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.59439 | 12.2682 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44683 | 0.49861 | 44683 | 0.50278 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.12 | 0.60729 | 150.4143 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44684 | 0.35417 | 44684 | 0.36597 | 0.28333 | Grid failure from 132/33 Kv Connecting substation | 0.13 | 0.61966 | 166.2659 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44684 | 0.37014 | 44684 | 0.37431 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.61966 | 63.9484 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44684 | 0.43333 | 44684 | 0.43611 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.61966 | 76.7381 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44684 | 0.52292 | 44684 | 0.53056 | 0.18333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.16 | 0.61966 | 204.6349 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44684 | 0.56181 | 44684 | 0.56319 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.61966 | 51.1587 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44685 | 0.31736 | 44685 | 0.31875 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.63322 | 13.0697 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44685 | 0.44236 | 44685 | 0.44375 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.63322 | 39.2092 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44686 | 0.37708 | 44686 | 0.38958 | 0.3 | Grid failure from 132/33 Kv Connecting substation | 0.2 | 0.60417 | 249.4006 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44686 | 0.40069 | 44686 | 0.40208 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.60417 | 37.4101 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44686 | 0.42569 | 44686 | 0.42708 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.60417 | 49.8801 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44686 | 0.44306 | 44686 | 0.44375 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.60417 | 24.9401 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44686 | 0.47292 | 44686 | 0.47361 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Padhera Line Earth Fault | 0.03 | 0.60417 | 37.4101 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44687 | 0.52847 | 44687 | 0.53542 | 0.16667 | Grid failure from 132/33 Kv Connecting substation | 0.15 | 0.59948 | 185.5999 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44687 | 0.56736 | 44687 | 0.57014 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.59948 | 74.2399 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44687 | 0.59931 | 44687 | 0.60139 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.59948 | 49.4933 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44687 | 0.61667 | 44687 | 0.66042 | 1.05 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.57 | 0.59948 | 705.2795 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.31875 | 44688 | 0.33264 | 0.33333 | Grid failure from 132/33 Kv Connecting substation | 0.11 | 0.62661 | 142.2658 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.33819 | 44688 | 0.34653 | 0.2 | Grid failure from 132/33 Kv Connecting substation | 0.08 | 0.62661 | 103.466 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.37917 | 44688 | 0.38264 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.62661 | 64.6663 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.43056 | 44688 | 0.43194 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.62661 | 38.7998 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.51944 | 44688 | 0.53889 | 0.46667 | Grid failure from 33/11 Kv Connecting substation, CT Replacement | 0.4 | 0.62661 | 517.3301 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.57292 | 44688 | 0.57431 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.62661 | 51.733 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44688 | 0.61181 | 44688 | 0.74583 | 3.2167 | Grid failure from 33/11 Kv Connecting substation, CT Replacement | 1.05 | 0.62661 | 1357.9916 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44689 | 0.37431 | 44689 | 0.37569 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.35048 | 14.4676 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44689 | 0.38542 | 44689 | 0.38611 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.35048 | 14.4676 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44689 | 0.47361 | 44689 | 0.47708 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.35048 | 57.8706 | Grid Resumed
Priapus | May | All Inverters | Int. Grid failure | 2064 | 44689 | 0.51667 | 44689 | 0.75486 | 5.7167 | 11 KV Grid line is in breakdown condition, UG cable punchered. | 2.92 | 0.35048 | 2112.2756 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44690 | 0.30347 | 44690 | 0.31667 | 0.31667 | Grid failure from 132/33 Kv Connecting substation | 0.08 | 0.65225 | 107.6989 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44690 | 0.57361 | 44690 | 0.57708 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.65225 | 94.2365 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44691 | 0.6625 | 44691 | 0.66389 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.63694 | 26.2929 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44691 | 0.67778 | 44691 | 0.67917 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.63694 | 13.1464 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44692 | 0.55903 | 44692 | 0.56042 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.66445 | 41.1425 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44692 | 0.71736 | 44692 | 0.72014 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.66445 | 13.7142 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44693 | 0.26111 | 44693 | 0.26736 | 0.15 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.63129 | 13.0298 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44694 | 0.45556 | 44694 | 0.46042 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.11 | 0.62677 | 142.3008 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44694 | 0.71875 | 44694 | 0.72361 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.62677 | 25.8729 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44695 | 0.28333 | 44695 | 0.28611 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.58481 | 12.0705 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44696 | 0.36875 | 44696 | 0.37569 | 0.16667 | Grid failure from 132/33 Kv Connecting substation | 0.1 | 0.63295 | 130.6417 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44696 | 0.51111 | 44696 | 0.5125 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.63295 | 52.2567 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44696 | 0.64722 | 44696 | 0.64861 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.63295 | 26.1283 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44697 | 0.62639 | 44697 | 0.62986 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.71024 | 14.6593 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44698 | 0.52569 | 44698 | 0.52708 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.64501 | 53.2522 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44698 | 0.55694 | 44698 | 0.56181 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.1 | 0.64501 | 133.1304 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44698 | 0.6125 | 44698 | 0.61389 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.64501 | 26.6261 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44698 | 0.62083 | 44698 | 0.77083 | 3.6 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.86 | 0.64501 | 1144.9216 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.54931 | 44699 | 0.55417 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.1 | 0.63747 | 131.5739 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.55625 | 44699 | 0.55833 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.63747 | 65.787 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.57083 | 44699 | 0.57222 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.63747 | 39.4722 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.57569 | 44699 | 0.57639 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.63747 | 26.3148 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.62431 | 44699 | 0.65556 | 0.75 | Grid failure from 132/33 Kv Connecting substation | 0.21 | 0.63747 | 276.3053 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.65833 | 44699 | 0.66111 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.63747 | 13.1574 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.71736 | 44699 | 0.72569 | 0.2 | Grid failure from 132/33 Kv Connecting substation | 0.03 | 0.63747 | 39.4722 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44699 | 0.74653 | 44699 | 0.75486 | 0.2 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.63747 | 13.1574 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44700 | 0.5375 | 44700 | 0.54444 | 0.16667 | Grid failure from 132/33 Kv Connecting substation | 0.16 | 0.59661 | 197.025 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44700 | 0.56806 | 44700 | 0.5875 | 0.46667 | Grid failure from 33/11 Kv Connecting substation, Main Breaker Isse | 0.38 | 0.59661 | 467.9345 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44700 | 0.60903 | 44700 | 0.61042 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.59661 | 36.9422 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44700 | 0.62986 | 44700 | 0.63125 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.59661 | 36.9422 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44700 | 0.6375 | 44700 | 0.64028 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.59661 | 49.2563 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44702 | 0.60417 | 44702 | 0.60486 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.6442 | 26.5924 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44702 | 0.68403 | 44702 | 0.69514 | 0.26667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.6442 | 106.3697 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44703 | 0.37778 | 44703 | 0.37917 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.65788 | 40.7361 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44704 | 0.34444 | 44704 | 0.36458 | 0.48333 | Grid failure from 132/33 Kv Connecting substation | 0.03 | 0.23028 | 14.2589 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44704 | 0.36667 | 44704 | 0.37847 | 0.28333 | Grid failure from 132/33 Kv Connecting substation | 0.02 | 0.23028 | 9.5059 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44704 | 0.38056 | 44704 | 0.51667 | 3.2667 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.15 | 0.23028 | 71.2946 | Grid Resumed
Priapus | May | All Inverters | Int. Grid failure | 2064 | 44704 | 0.55278 | 44704 | 0.66389 | 2.6667 | 11 KV Grid line is in breakdown condition, UG cable punchered. | 1.35 | 0.23028 | 641.651 | Grid Resumed
Priapus | May | All Inverters | Int. Grid failure | 2064 | 44704 | 0.66597 | 44704 | 0.68333 | 0.41667 | 11 KV Grid line is in breakdown condition, UG cable punchered. | 0.11 | 0.23028 | 52.2827 | Grid Resumed
Priapus | May | All Inverters | Int. Grid failure | 2064 | 44704 | 0.71181 | 44704 | 0.78472 | 1.75 | 11 KV Grid line is in breakdown condition, UG cable punchered. | 0.15 | 0.23028 | 71.2946 | Grid Resumed
Priapus | May | All Inverters | Int. Grid failure | 2064 | 44705 | 0.23403 | 44705 | 0.27847 | 1.0667 | 11 KV Grid line is in breakdown condition | 0.02 | 0.70299 | 29.0196 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44707 | 0.67222 | 44707 | 0.67361 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.68225 | 28.1634 | Grid Resumed
Priapus | May | All Inverters | Ext. Grid failure | 2064 | 44712 | 0.75208 | 44712 | 0.76875 | 0.4 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.02 | 0.6731 | 27.7854 | Grid Resumed
Priapus | June | All Inverters | Int. Grid failure | 2064 | 44713 | 0.26458 | 44713 | 0.27014 | 0.13333 | 11 KV Grid line is in breakdown condition, Fuse Burnt | 0.01 | 0.64248 | 13.2609 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.33125 | 44713 | 0.33542 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.64248 | 53.0435 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.41806 | 44713 | 0.42292 | 0.11667 | Grid failure from 132/33 Kv Connecting substation | 0.09 | 0.64248 | 119.3479 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.50347 | 44713 | 0.50417 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.64248 | 26.5218 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.50625 | 44713 | 0.50972 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.64248 | 106.0871 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.51181 | 44713 | 0.51806 | 0.15 | Grid failure from 132/33 Kv Connecting substation | 0.14 | 0.64248 | 185.6524 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.575 | 44713 | 0.57986 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.1 | 0.64248 | 132.6088 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44713 | 0.60069 | 44713 | 0.61042 | 0.23333 | Grid failure from 132/33 Kv Connecting substation | 0.18 | 0.64248 | 238.6959 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44714 | 0.54236 | 44714 | 0.54306 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.64715 | 26.7142 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44715 | 0.29306 | 44715 | 0.29583 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.61172 | 12.626 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44715 | 0.38194 | 44715 | 0.47431 | 2.2167 | Grid failure from 132/33 Kv Connecting substation | 1.78 | 0.61172 | 2247.4283 | Grid Resumed
Priapus | June | All Inverters | Int. Grid failure | 2064 | 44716 | 0.45347 | 44716 | 0.49653 | 1.0333 | 11 KV Grid line is in breakdown condition, Tree Bush fallen on conductor | 0.94 | 0.52718 | 1022.8172 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44716 | 0.53889 | 44716 | 0.54444 | 0.13333 | Grid failure from 132/33 Kv Connecting substation | 0.13 | 0.52718 | 141.4534 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44716 | 0.57083 | 44716 | 0.57431 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.52718 | 87.0483 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44716 | 0.60694 | 44716 | 0.60833 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.52718 | 32.6431 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44716 | 0.62708 | 44716 | 0.62847 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.52718 | 32.6431 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44717 | 0.43056 | 44717 | 0.43542 | 0.11667 | Grid failure from 132/33 Kv Connecting substation | 0.1 | 0.61709 | 127.3664 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44717 | 0.57986 | 44717 | 0.58194 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.61709 | 63.6832 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44718 | 0.65694 | 44718 | 0.66111 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.60507 | 62.4433 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44718 | 0.67222 | 44718 | 0.67361 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.60507 | 49.9547 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.37153 | 44719 | 0.37292 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.60702 | 25.058 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.38542 | 44719 | 0.38681 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.60702 | 25.058 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.68542 | 44719 | 0.68681 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.60702 | 12.529 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.69653 | 44719 | 0.69792 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.60702 | 12.529 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.70903 | 44719 | 0.71319 | 0.1 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.60702 | 12.529 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44719 | 0.75417 | 44719 | 0.76806 | 0.33333 | Grid failure from 33/11 Kv Connecting substation, Fuse burnt | 0.01 | 0.60702 | 12.529 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.22917 | 44720 | 0.425 | 4.7 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 1.48 | 0.56883 | 1737.6193 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.42847 | 44720 | 0.42986 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.56883 | 35.222 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.45347 | 44720 | 0.45486 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.56883 | 35.222 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.46458 | 44720 | 0.46528 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.56883 | 23.4813 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.47708 | 44720 | 0.53194 | 1.3167 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 1.11 | 0.56883 | 1303.2145 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.58403 | 44720 | 0.58472 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.56883 | 23.4813 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.60347 | 44720 | 0.60417 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.56883 | 23.4813 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.61111 | 44720 | 0.6125 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.56883 | 35.222 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.63472 | 44720 | 0.63611 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.56883 | 23.4813 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.64722 | 44720 | 0.69792 | 1.2167 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.52 | 0.56883 | 610.5149 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44720 | 0.71181 | 44720 | 0.71528 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.56883 | 23.4813 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44721 | 0.21875 | 44721 | 0.51042 | 7 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 3.37 | 0.57524 | 4001.1552 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44721 | 0.64514 | 44721 | 0.64653 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.57524 | 23.7457 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44723 | 0.3375 | 44723 | 0.34097 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.59498 | 36.8412 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44723 | 0.37292 | 44723 | 0.49653 | 2.9667 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 2.15 | 0.59498 | 2640.2865 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44724 | 0.25347 | 44724 | 0.44167 | 4.5167 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 2.04 | 0.57006 | 2400.2732 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44725 | 0.69028 | 44725 | 0.69167 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.60075 | 12.3994 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44725 | 0.69792 | 44725 | 0.70278 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, 33 KV Grid line is in breakdown condition | 0.01 | 0.60075 | 12.3994 | Grid Resumed
Priapus | June | All Inverters | Int. Grid failure | 2064 | 44726 | 0.29375 | 44726 | 0.32639 | 0.78333 | 11 KV Grid line is in breakdown condition, Jumper Burnt | 0.19 | 0.59908 | 234.9345 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44727 | 0.49583 | 44727 | 0.49931 | 0.083333 | Grid failure from 132/33 Kv Connecting substation | 0.09 | 0.62301 | 115.7308 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44728 | 0.22847 | 44728 | 0.41181 | 4.4 | Grid failure from 132/33 Kv Connecting substation | 1.13 | 0.5984 | 1395.6603 | Grid Resumed
Priapus | June | Inverter 02 | LCL fan failure | 1032 | 44728 | 0.48542 | 44728 | 0.58889 | 2.4833 | Inv Tripped due to DI 2 (1082) fault, LCL fan fail | 2.02 | 0.8 | 1667.712 | Inverter started on 30% load by shifting fan.
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44728 | 0.50556 | 44728 | 0.50694 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.5984 | 49.4039 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44728 | 0.55069 | 44728 | 0.56042 | 0.23333 | Grid failure from 132/33 Kv Connecting substation | 0.21 | 0.8 | 346.752 | Grid Resumed
Priapus | June | Inverter 02 | ISU failure | 1032 | 44728 | 0.58889 | 44732 | 0.52778 | 8.95 | Inverter running at 30% load | 1.88 | 0.5984 | 3805 | Inverter running at 30% load
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44729 | 0.41111 | 44729 | 0.42014 | 0.21667 | Grid failure from 132/33 Kv Connecting substation | 0.02 | 0.66312 | 27.3734 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44729 | 0.43056 | 44729 | 0.43333 | 0.066667 | Grid failure from 132/33 Kv Connecting substation | 0.03 | 0.66312 | 41.0601 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44730 | 0.70556 | 44730 | 0.70833 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.6473 | 26.7204 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44733 | 0.49097 | 44733 | 0.49375 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.68359 | 112.8744 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44733 | 0.50278 | 44733 | 0.50556 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.68359 | 112.8744 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44733 | 0.60972 | 44733 | 0.61181 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.04 | 0.68359 | 56.4372 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44733 | 0.7 | 44733 | 0.70278 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.68359 | 28.2186 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44734 | 0.47847 | 44734 | 0.48194 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.6639 | 109.6227 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44735 | 0.43125 | 44735 | 0.43542 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.09 | 0.66174 | 122.9255 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44736 | 0.29444 | 44736 | 0.29792 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.58807 | 24.2755 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44736 | 0.38681 | 44736 | 0.38958 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.58807 | 60.6888 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.44861 | 44737 | 0.45139 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.59569 | 73.7701 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.52014 | 44737 | 0.53681 | 0.4 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.32 | 0.59569 | 393.4406 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.54931 | 44737 | 0.55208 | 0.066667 | Grid failure from 33/11 Kv Connecting substation | 0.05 | 0.59569 | 61.4751 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.55694 | 44737 | 0.56042 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.59569 | 86.0651 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.57014 | 44737 | 0.57222 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.59569 | 61.4751 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.57917 | 44737 | 0.59306 | 0.33333 | Grid failure from 33/11 Kv Connecting substation, Incomer failure (Kapoorpur) | 0.28 | 0.59569 | 344.2605 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44737 | 0.61042 | 44737 | 0.61806 | 0.18333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.11 | 0.59569 | 135.2452 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44739 | 0.26528 | 44739 | 0.275 | 0.23333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.7018 | 28.9705 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44739 | 0.48403 | 44739 | 0.4875 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.09 | 0.7018 | 130.3672 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44739 | 0.53333 | 44739 | 0.53958 | 0.15 | Grid failure from 132/33 Kv Connecting substation | 0.1 | 0.7018 | 144.8524 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44739 | 0.59375 | 44739 | 0.60486 | 0.26667 | Grid failure from 132/33 Kv Connecting substation | 0.21 | 0.7018 | 304.1901 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44740 | 0.5375 | 44740 | 0.55694 | 0.46667 | Grid failure from 132/33 Kv Connecting substation | 0.38 | 0.80148 | 628.6187 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44742 | 0.35069 | 44742 | 0.36875 | 0.43333 | Grid failure from 33/11 Kv Connecting substation, Working on Main Transformer | 0.038 | 0.81284 | 63.7524 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44742 | 0.44931 | 44742 | 0.52292 | 1.7667 | Grid failure from 33/11 Kv Connecting substation, main T/f tripped due to Overheat issue | 0.57 | 0.81284 | 956.2863 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44742 | 0.57361 | 44742 | 0.58056 | 0.16667 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.81284 | 83.8848 | Grid Resumed
Priapus | June | All Inverters | Ext. Grid failure | 2064 | 44742 | 0.59931 | 44742 | 0.60208 | 0.066667 | Grid failure from 132/33 Kv Connecting substation | 0.02 | 0.81284 | 33.5539 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44743 | 0.31042 | 44743 | 0.36389 | 1.2833 | Grid failure from 132/33 Kv Connecting substation | 0.15 | 0.75478 | 233.679 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44743 | 0.62569 | 44743 | 0.62847 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.75478 | 46.7358 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44744 | 0.63958 | 44744 | 0.68472 | 1.0833 | Grid failure from 132/33 Kv Connecting substation | 0.07 | 0.87464 | 126.3676 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44747 | 0.41736 | 44747 | 0.42292 | 0.13333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.12 | 0.68589 | 169.8811 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44747 | 0.43819 | 44747 | 0.44097 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.68589 | 99.0973 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44748 | 0.42014 | 44748 | 0.46042 | 0.96667 | Grid failure from 33/11 Kv Connecting substation, Jumper Burnt | 0.81 | 0.71163 | 1189.7344 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44748 | 0.54167 | 44748 | 0.54792 | 0.15 | Grid failure from 132/33 Kv Connecting substation | 0.15 | 0.71163 | 220.3212 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44749 | 0.32361 | 44749 | 0.32917 | 0.13333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.66109 | 68.2245 | Grid Resumed
Priapus | July | All Inverters | Int. Grid failure | 2064 | 44749 | 0.56875 | 44749 | 0.58681 | 0.43333 | 11 KV Grid line is in breakdown condition, Line Jumper Burnt | 0.37 | 0.66109 | 504.861 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44749 | 0.60417 | 44749 | 0.63403 | 0.71667 | Grid failure from 132/33 Kv Connecting substation | 0.45 | 0.66109 | 614.0201 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44751 | 0.47292 | 44751 | 0.47708 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.83586 | 17.2522 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44751 | 0.63403 | 44751 | 0.64167 | 0.18333 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.83586 | 103.513 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44753 | 0.77014 | 44753 | 0.79514 | 0.6 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.70187 | 14.4867 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44757 | 0.28056 | 44757 | 0.29236 | 0.28333 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.69986 | 72.2256 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44757 | 0.31667 | 44757 | 0.32014 | 0.083333 | Grid failure from 132/33 Kv Connecting substation | 0.03 | 0.69986 | 43.3354 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44757 | 0.37153 | 44757 | 0.375 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.69986 | 72.2256 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44757 | 0.48472 | 44757 | 0.48542 | 0.016667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.69986 | 28.8902 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44758 | 0.61736 | 44758 | 0.65556 | 0.91667 | Grid failure from 132/33 Kv Connecting substation | 0.01 | 0.69645 | 14.3747 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44759 | 0.24514 | 44759 | 0.70139 | 10.95 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 6.06 | 0.37292 | 4664.4537 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44760 | 0.42014 | 44760 | 0.42222 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.68638 | 85.001 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44761 | 0.41875 | 44761 | 0.42569 | 0.16667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.77869 | 128.5778 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44761 | 0.48472 | 44761 | 0.49028 | 0.13333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.13 | 0.77869 | 208.9389 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44761 | 0.66736 | 44761 | 0.66944 | 0.05 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.77869 | 16.0722 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44762 | 0.49722 | 44762 | 0.56181 | 1.55 | Grid failure from 132/33 Kv Connecting substation | 0.06 | 0.76998 | 95.3537 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44764 | 0.53403 | 44764 | 0.55972 | 0.61667 | Grid failure from 33/11 Kv Connecting substation, Fuse burnt | 0.31 | 0.763 | 488.1986 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44765 | 0.34931 | 44765 | 0.51458 | 3.9667 | Grid failure from 33/11 Kv Connecting substation, Flash over on Transformer & CB | 2.39 | 0.68905 | 3399.0787 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44765 | 0.71736 | 44765 | 0.7375 | 0.48333 | Grid failure from 33/11 Kv Connecting substation | 0.04 | 0.68905 | 56.8883 | Grid Resumed
Priapus | July | All Inverters | Int. Grid failure | 2064 | 44766 | 0.46111 | 44766 | 0.47778 | 0.4 | 11 KV Grid line is in breakdown condition | 0.23 | 0.7124 | 338.1885 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44766 | 0.63472 | 44766 | 0.64028 | 0.13333 | Grid failure from 33/11 Kv Connecting substation | 0.02 | 0.7124 | 29.4077 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44767 | 0.33819 | 44767 | 0.33958 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.76346 | 31.5158 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44768 | 0.22847 | 44768 | 0.25903 | 0.73333 | Grid failure from 132/33 Kv Connecting substation | 0.02 | 0.78794 | 32.526 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44769 | 0.44028 | 44769 | 0.55069 | 2.65 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 0.67 | 0.84506 | 1168.6203 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44772 | 0.34722 | 44772 | 0.35 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.7272 | 30.0188 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44772 | 0.43056 | 44772 | 0.79167 | 8.6667 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 1.63 | 0.7272 | 2446.5291 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44773 | 0.22917 | 44773 | 0.325 | 2.3 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 0.07 | 0.62119 | 89.7497 | Grid Resumed
Priapus | July | All Inverters | Ext. Grid failure | 2064 | 44773 | 0.33194 | 44773 | 0.38403 | 1.25 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 0.17 | 0.62119 | 217.9635 | Grid Resumed
Priapus | July | Inverter 01 | Over current fault | 1032 | 44773 | 0.38403 | 44773 | 0.55486 | 4.1 | Inverter fail on Overcurrent fault (2380) | 1.18 | 0.62119 | 756.4616 | AC Fuse replaced
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44775 | 0.6625 | 44775 | 0.7625 | 2.4 | Grid failure from 132/33 Kv Connecting substation | 0.11 | 0.70334 | 159.6853 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44776 | 0.41111 | 44776 | 0.53611 | 3 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 1.3 | 0.79967 | 2145.6709 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44776 | 0.55278 | 44776 | 0.57014 | 0.41667 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 0.3 | 0.79967 | 495.1548 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44776 | 0.60556 | 44776 | 0.78958 | 4.4167 | Grid failure from 33/11 Kv Connecting substation, Incomer failure | 1.45 | 0.79967 | 2393.2484 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44777 | 0.64097 | 44777 | 0.65069 | 0.23333 | Grid failure from 132/33 Kv Connecting substation | 0.05 | 0.77337 | 79.8118 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44779 | 0.5375 | 44779 | 0.57639 | 0.93333 | Grid failure from 132/33 Kv Connecting substation | 0.62 | 0.763 | 976.3972 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44782 | 0.22847 | 44782 | 0.45972 | 5.55 | Grid failure from 132/33 Kv Connecting substation | 2.04 | 0.65925 | 2775.7934 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44784 | 0.55764 | 44784 | 0.57431 | 0.4 | Grid Manually tripped from 132/33 Kv Connecting substation | 0.3 | 0.77914 | 482.4444 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44787 | 0.53819 | 44787 | 0.55 | 0.28333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.76462 | 110.4717 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44788 | 0.31389 | 44788 | 0.32639 | 0.3 | Grid Manually tripped from 132/33 Kv Connecting substation | 0.06 | 0.73754 | 91.3372 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44791 | 0.23333 | 44791 | 0.33194 | 2.3667 | Grid failure from 132/33 Kv Connecting substation | 0.37 | 0.71163 | 543.4589 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44791 | 0.57292 | 44791 | 0.58125 | 0.2 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.2 | 0.71163 | 293.7616 | Grid Resumed
Priapus | August | All Inverters | Int. Grid failure | 2064 | 44795 | 0.30347 | 44795 | 0.34306 | 0.95 | 11 KV Line jumper burnt | 0.33 | 0.72056 | 490.7862 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44797 | 0.51389 | 44797 | 0.55208 | 0.91667 | Grid maually Tripped from GSS end | 0.93 | 0.73392 | 1408.7696 | Grid Resumed
Priapus | August | All Inverters | Int. Grid failure | 2064 | 44798 | 0.23611 | 44798 | 0.32222 | 2.0667 | 11 kv grid line tripped | 0.18 | 0.71598 | 266.0026 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44799 | 0.2875 | 44799 | 0.29375 | 0.15 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.69989 | 14.4456 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44799 | 0.50764 | 44799 | 0.75208 | 5.8667 | Grid Maually tripped from 132/33 Kv Connecting substation, CT & PT changed incoming panel | 2.63 | 0.69989 | 3799.2055 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44800 | 0.55764 | 44800 | 0.56111 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.09 | 0.72394 | 134.48 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44800 | 0.68611 | 44800 | 0.68889 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.72394 | 29.8844 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44800 | 0.69861 | 44800 | 0.70139 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.72394 | 29.8844 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44801 | 0.58264 | 44801 | 0.58611 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.77216 | 95.6243 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44802 | 0.31528 | 44802 | 0.32014 | 0.11667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.75861 | 15.6577 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44802 | 0.51181 | 44802 | 0.51458 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.02 | 0.75861 | 31.3154 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44802 | 0.56736 | 44802 | 0.57153 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.11 | 0.75861 | 172.2348 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44803 | 0.50208 | 44803 | 0.50486 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.7101 | 117.2523 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44803 | 0.51736 | 44803 | 0.52083 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.1 | 0.7101 | 146.5654 | Grid Resumed
Priapus | August | All Inverters | Ext. Grid failure | 2064 | 44804 | 0.53403 | 44804 | 0.54514 | 0.26667 | Cable burn in cubical meter Panel | 0.25 | 0.68707 | 354.529 | Grid Resumed
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.32083 | 44806 | 0.33819 | 0.41667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.75673 | 46.8565
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.4375 | 44806 | 0.44167 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.75673 | 78.0941
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.56458 | 44806 | 0.56736 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.75673 | 15.6188
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.57708 | 44806 | 0.58125 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.75673 | 78.0941
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.60833 | 44806 | 0.61111 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.75673 | 15.6188
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44806 | 0.64236 | 44806 | 0.64375 | 0.033333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.75673 | 15.6188
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.31319 | 44807 | 0.31597 | 0.066667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.01 | 0.67435 | 13.9187
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.50556 | 44807 | 0.60625 | 2.4167 | Grid Manually tripped from 132/33 Kv Connecting substation | 2.15 | 0.67435 | 2992.5101
Priapus | September | Inverter 01 | Over current fault | 1032 | 44807 | 0.63125 | 44807 | 0.77083 | 3.35 | Inverter trip on iNT Confihuration error. | 0.83 | 0.67435 | 577.624 | Charging resistor bypassed and made to run inverter on 70 % Limit.
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.61319 | 44807 | 0.61736 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.08 | 0.67435 | 111.3492
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.63194 | 44807 | 0.63542 | 0.083333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.06 | 0.67435 | 83.5119
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.67153 | 44807 | 0.67569 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.05 | 0.67435 | 69.5933
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44807 | 0.6875 | 44807 | 0.69167 | 0.1 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.03 | 0.67435 | 41.756
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44808 | 0.31042 | 44808 | 0.32153 | 0.26667 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.07 | 0.7272 | 105.0657
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44809 | 0.34028 | 44809 | 0.35625 | 0.38333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.18 | 0.70343 | 261.3398
Priapus | September | All Inverters | Ext. Grid failure | 2064 | 44809 | 0.36528 | 44809 | 0.38333 | 0.43333 | Grid failure from 33/11 Kv Connecting substation, Main T/F Trip | 0.26 | 0.70343 | 377.4908
Punganur | April | Inverter 38 | Auto reset fault | 1217.7 | 44653 | 0.26806 | 44653 | 0.28958 | 0.51667 | Autoreset fault | 0.018202 | 0.77514 | 17.1807 | Inverter 38 tripped on Autoreset fault, checked the related circuit and restarted the inverter.
Punganur | April | Feeder 04 | O/L fault | 11957.219999999998 | 44656 | 0.73889 | 44656 | 0.76806 | 0.7 | O/L fault | 0.006418 | 0.78567 | 60.2937 | Feeder 4 tripped on O/L ,Found the GSS end switchyard R-phase jumper was cut due to pad clamp melt, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 01 | O/L fault | 12013.320000000002 | 44658 | 0.25486 | 44658 | 0.39792 | 3.4333 | O/L fault | 1.022 | 0.73304 | 9000.0278 | Feeder 1 tripped on O/L ,Found the insulator was flashover at DP7, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 03 | Ground fault | 11681.670000000002 | 44659 | 0.46389 | 44659 | 0.46667 | 0.066667 | LC Taken | 0.068468 | 0.74151 | 593.0726 | Feeder tripped due to Block-08 outgoing cable End termination kit failure
Punganur | April | All Inverters | Grid failure | 47694.570000000007 | 44659 | 0.61736 | 44659 | 0.61944 | 0.05 | Grid fluctuation | 0.040203 | 0.74151 | 1421.8023 | Grid fluctuation from GSS end
Punganur | April | All Inverters | Grid failure | 47694.570000000007 | 44659 | 0.74792 | 44659 | 0.76597 | 0.43333 | Grid down | 0.0058738 | 0.74151 | 207.7329 | Grid down from GSS end
Punganur | April | Inverter 22 | No comm. fault | 1190.6400000000001 | 44659 | 0.61944 | 44659 | 0.63056 | 0.26667 | Communication issue | 0.18011 | 0.74151 | 159.0131 | Inverter-22 tripped on communication issue and check all parameters and restarted the inverter.
Punganur | April | Block 08 | Outgoing cable kit failure | 4814 | 44659 | 0.46667 | 44659 | 0.76597 | 7.1833 | Block-08 Outgoing cable kit failure | 4.5208 | 0.74151 | 16137 | Block-08 Outgoing cable End kit failure
Punganur | April | Inverter 31 | Short circuit fault | 1217.7 | 44663 | 0.49306 | 44663 | 0.49653 | 0.083333 | Short ckt fault | 0.076449 | 0.79296 | 73.8185 | Inverter 31 tripped on short ckt fault, checked healthyness of system and after generation hrs IGBT cleaning done.
Punganur | April | Inverter 15 | Short circuit fault | 1212.42 | 44664 | 0.46944 | 44664 | 0.48125 | 0.28333 | Short ckt fault | 0.27774 | 0.80474 | 270.9858 | Inverter 15 tripped on short ckt fault, checked healthyness of system and after generation hrs IGBT cleaning done.
Punganur | April | Inverter 15 | Short circuit fault | 1212.42 | 44666 | 0.53264 | 44666 | 0.53819 | 0.13333 | Short ckt fault | 0.13201 | 0.7881 | 126.1354 | Inverter 15 tripped on short ckt fault, checked healthyness of system and after generation hrs IGBT cleaning done.
Punganur | April | Inverter 16 | Short circuit fault | 1183.3800000000001 | 44667 | 0.46528 | 44667 | 0.49653 | 0.75 | CH2 COMM lost | 0.72358 | 0.81809 | 700.5059 | Inveter 16 tripped on CH2 comm loss fault,Contact with ABB person checked related circuit and restarted the inverters.
Punganur | April | All Inverters | Grid failure | 47694.570000000007 | 44667 | 0.44583 | 44667 | 0.4625 | 0.4 | Grid down | 0.35393 | 0.81809 | 13809.9241 | Grid down from GSS end
Punganur | April | Feeder 03 | Under voltage fault | 11681.670000000002 | 44668 | 0.24931 | 44668 | 0.42917 | 4.3167 | Under voltage | 1.6278 | 0.74724 | 14208.8491 | Feeder 3 tripped on under voltage line patrolling done and found insulator flashover and jumper damage replacemengt done.
Punganur | April | Inverter 38 | Short circuit fault | 1217.7 | 44668 | 0.45833 | 44668 | 0.49653 | 0.91667 | Short ckt fault | 0.56279 | 0.74724 | 512.0887 | Inverter 38 tripped on short ckt fault, checked healthyness of system and after generation hrs IGBT cleaning done.
Punganur | April | Inverter 32 | No comm. fault | 1173.1500000000001 | 44668 | 0.46875 | 44668 | 0.47917 | 0.25 | Communication issue | 0.093525 | 0.74724 | 81.9864 | Inverter 32 tripped on No communication fault checked related connection and restart the inverter.
Punganur | April | Feeder 01 | Ground fault | 12013.320000000002 | 44670 | 0.69028 | 44670 | 0.76875 | 1.8833 | E/L fault | 0.063939 | 0.80312 | 616.891 | Feeder 1 tripped on E/L fault,Found the all insulatosr was flashover at T09, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 02 | Ground fault | 12042.360000000002 | 44670 | 0.68333 | 44670 | 0.71528 | 0.76667 | E/L fault | 0.04797 | 0.80312 | 463.941 | Feeder 2 tripped on E/L fault trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 03 | O/L fault | 11681.670000000002 | 44670 | 0.69792 | 44670 | 0.76875 | 1.7 | O/L fault | 0.048977 | 0.80312 | 459.4894 | Feeder 3 tripped on O/L ,Found the insulator was flashover at TO7, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 04 | O/L fault | 11957.219999999998 | 44670 | 0.69028 | 44670 | 0.76875 | 1.8833 | O/L fault | 0.063939 | 0.80312 | 614.0103 | Feeder 4 tripped on O/L ,Found the insulator was flashover at DP7, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 04 | O/L fault | 11957.219999999998 | 44671 | 0.24028 | 44671 | 0.46736 | 5.45 | E/L fault | 2.374 | 0.67326 | 19111.8547 | Feeder 4 tripped on O/L ,Found the insulator was flashover at CP7, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Feeder 04 | Ground fault | 11957.219999999998 | 44674 | 0.59028 | 44674 | 0.66042 | 1.6833 | E/L fault | 1.1185 | 0.75126 | 10047.7124 | Feeder 4 tripped on E/L ,Found the insulator was flashover at T02, replacement done,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Inverter 34 | LCL fan fault | 1217.7 | 44675 | 0.48264 | 44675 | 0.50347 | 0.5 | LCL FAN FAULT | 0.42422 | 0.78064 | 403.257 | Inverter 34 tripped on LC FAN Fault, checked healthyness of system found ISU 3 LCL fan not working replaced restart the inverter.
Punganur | April | Feeder 01 | Ground fault | 12013.320000000002 | 44677 | 0.60139 | 44677 | 0.60764 | 0.15 | E/L fault | 0.11894 | 0.77325 | 1104.8515 | Feeder 1 tripped on E/L ,trail charge taken T/M line withstanded and feeder charged.
Punganur | April | Inverter 01 | Auxilary supply failure | 1212.42 | 44677 | 0.60139 | 44677 | 0.60764 | 0.15 | Auxilary supply fail | 0.11894 | 0.77325 | 111.5049 | Inverter 1 tripped due Aux supply failed at the time of Feeder 1 tripped communicaton was failed so change over not done.
Punganur | April | Inverter 02 | Auxilary supply failure | 1168.8599999999999 | 44677 | 0.60139 | 44677 | 0.60764 | 0.15 | Auxilary supply fail | 0.11894 | 0.77325 | 107.4987 | Inverter 2 tripped due Aux supply failed at the time of Feeder 1 tripped communicaton was failed so change over not done.
Punganur | April | Inverter 16 | LCL fan fault | 1183.3800000000001 | 44677 | 0.60764 | 44677 | 0.625 | 0.41667 | Communication issue | 0.311 | 0.77325 | 284.5803 | Inverter 34 tripped on LC FAN Fault, checked healthyness of system found ISU 3 LCL fan not working replaced restart the inverter.
Punganur | April | Inverter 01 | Run disable fault | 1212.42 | 44678 | 0.27083 | 44678 | 0.29236 | 0.51667 | Run disable | 0.03318 | 0.7774 | 31.2736 | Inverter 1 tripped on RUN disable fault checked the related connection restarted inverter.
Punganur | April | SCB.37.04 | String fault | 14.6 | 44679 | 0.49653 | 44679 | 0.50694 | 0.25 | String fault | 0.22655 | 0.77873 | 2.5758 | Found string failure while checking Critical SCB string testing and rectification done
Punganur | April | SCB.01.03 | String fault | 14.6 | 44679 | 0.49653 | 44679 | 0.53472 | 0.91667 | String fault | 0.87801 | 0.77873 | 9.9826 | Found string failure while checking Critical SCB string testing and rectification done
Punganur | April | Inverter 01 | Short circuit fault | 1212.42 | 44679 | 0.27778 | 44679 | 0.29514 | 0.41667 | Short ckt fault | 0.044408 | 0.77873 | 41.9283 | Inverter 1 tripped on Short circuit,checked the related connection restarted inverter.after generation ISU 2 W FRC cable changed
Punganur | April | Inverter 01 | Short circuit fault | 1212.42 | 44680 | 0.27431 | 44680 | 0.29861 | 0.58333 | Short ckt fault | 0.071173 | 0.77549 | 66.9178 | Inverter 1 tripped on Short circuit,checked the related connection restarted inverter.after generation cleaning done,If it repeate same tomarrow we will change IGBT by the ABB team.
Punganur | April | All Inverters | Grid failure | 47694.570000000007 | 44680 | 0.70694 | 44680 | 0.73681 | 0.71667 | Grid down | 0.016451 | 0.77549 | 608.4705 | Grid down from GSS end
Punganur | May | All Inverters | Grid failure | 47694.570000000007 | 44682 | 0.64931 | 44682 | 0.67569 | 0.63333 | Grid down | 0.017246 | 0.78887 | 648.8652 | Due to Heavy winds and thunders manuval tripping done from GSS
Punganur | May | Inverter 32 | Ground fault | 1173.1500000000001 | 44682 | 0.67708 | 44682 | 0.69792 | 0.5 | DI4 Fault | 0.01201 | 0.78887 | 11.1148 | Inverter 32 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | Inverter 37 | Ground fault | 1217.7 | 44682 | 0.69097 | 44682 | 0.7 | 0.21667 | DI4 Fault | 0.00801 | 0.78887 | 7.6945 | Inverter 32 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | All Inverters | Grid failure | 47694.570000000007 | 44683 | 0.68056 | 44683 | 0.69722 | 0.4 | Grid down | 0.1726 | 0.77078 | 6344.9543 | Due to Heavy winds and thunders manuval tripping done from GSS
Punganur | May | Inverter 37 | Ground fault | 1217.7 | 44683 | 0.26389 | 44683 | 0.37083 | 2.5667 | DI4 & Earth fault | 0.47645 | 0.77078 | 447.1845 | Inverter 37 tripped on DI4 fault found 2 stings faulty and ISU 1 B-phase 1000 A fuse blown,Replaced and restatred the inverter.
Punganur | May | Inverter 37 | Ground fault | 1217.7 | 44685 | 0.66458 | 44685 | 0.67639 | 0.28333 | DI4 & Earth fault | 0.004986 | 0.79196 | 4.8083 | Inverter 37 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | Inverter 31 | Ground fault | 1217.7 | 44685 | 0.65556 | 44685 | 0.67708 | 0.51667 | DI4 & Earth fault | 0.010062 | 0.79196 | 9.7035 | Inverter 31 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | Inverter 22 | No comm. fault | 1190.6400000000001 | 44686 | 0.44028 | 44686 | 0.46528 | 0.6 | No Communication Fault | 0.524 | 0.81532 | 508.6755 | Inverter-22 tripped on NO communication fault after check and found the FO Cable is not clicking and replaced with new one.
Punganur | May | Feeder 04 | Ground fault | 11957.219999999998 | 44687 | 0.45972 | 44687 | 0.55833 | 2.3667 | E/L fault | 2.1571 | 0.68768 | 17736.8369 | Feeder4 tripped on E/L ,line patrolloing carringout found insulator damage at DP4 replaced ,trail charge taken T/M line withstanded and feeder charged.
Punganur | May | All Inverters | Grid failure | 47694.570000000007 | 44687 | 0.71597 | 44687 | 0.73125 | 0.36667 | Grid down | 0.018953 | 0.68768 | 621.6307 | Due to Heavy winds and thunders manuval tripping done from GSS
Punganur | May | Inverter 26 | Ground fault | 1197.9000000000001 | 44687 | 0.68889 | 44687 | 0.70139 | 0.3 | DI4 Fault | 0.048516 | 0.68768 | 39.966 | Inverter 26 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | Inverter 06 | Ground fault | 1219.68 | 44687 | 0.67222 | 44687 | 0.6875 | 0.36667 | DI4 Fault | 0.047527 | 0.68768 | 39.8635 | Inverter 6 tripped on DI4 fault checked related connection and restart the inverter.
Punganur | May | Inverter 03 | DI1 fault | 1219.68 | 44688 | 0.41736 | 44688 | 0.43681 | 0.46667 | DI1 fault | 0.36617 | 0.79212 | 353.7661 | Inverter 1 tripped on DI 1 fault checked related connection found LCL filter fan fail,replacement done and restart the inverter.
Punganur | May | Inverter 01 | Short circuit fault | 1212.42 | 44690 | 0.27778 | 44690 | 0.30903 | 0.75 | Short ckt fault | 0.062258 | 0.82891 | 62.5683 | Inverter 1 tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | May | Inverter 06 | Ground fault | 1219.68 | 44691 | 0.34931 | 44691 | 0.35972 | 0.25 | DI4 fault | 0.013787 | 0.8524 | 14.3342 | Inverter 6 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 14 | Ground fault | 1183.3800000000001 | 44692 | 0.36597 | 44692 | 0.37431 | 0.2 | DI4 fault | 0.047419 | 0.84492 | 47.4124 | Inverter 14 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 06 | Ground fault | 1219.68 | 44693 | 0.38403 | 44693 | 0.39236 | 0.2 | DI4 fault | 0.056834 | 0.84392 | 58.5 | Inverter 6 tripped on DI4 fault checked related connections found 6 strings faulty rectified,and restart the inverter.
Punganur | May | SCB.06.06 | Ground fault | 43.8 | 44693 | 0.39236 | 44693 | 0.52083 | 3.0833 | DI4 fault | 1.143 | 0.84392 | 42.2481 | SCB 6 str 1,2,9,10,12,13 found DI4 fault rectified the strings.
Punganur | May | Inverter 26 | Ground fault | 1197.9000000000001 | 44693 | 0.6 | 44693 | 0.60625 | 0.15 | DI4 fault | 0.010025 | 0.84392 | 10.1341 | Inverter 26 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 01 | Short circuit fault | 1212.42 | 44696 | 0.27917 | 44696 | 0.31597 | 0.88333 | Short ckt fault | 0.13857 | 0.81973 | 137.7179 | Inverter 1 tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | May | Inverter 01 | Ground fault | 1212.42 | 44697 | 0.27431 | 44697 | 0.27917 | 0.11667 | Short ckt fault | 0.0052908 | 0.83248 | 5.3401 | Inverter 1 tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | May | Inverter 05 | Ground fault | 1190.6400000000001 | 44698 | 0.33403 | 44698 | 0.34444 | 0.25 | DI4 fault | 0.088563 | 0.81194 | 85.616 | Inverter 5 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 22 | Ground fault | 1190.6400000000001 | 44698 | 0.64722 | 44698 | 0.66042 | 0.31667 | DI4 fault | 0.035219 | 0.81194 | 34.0474 | Inverter 22 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 05 | Ground fault | 1190.6400000000001 | 44699 | 0.57639 | 44699 | 0.58681 | 0.25 | DI4 fault | 0.082047 | 0.82602 | 80.6935 | Inverter 5 tripped on DI4 fault checked related connections found 1 faulty string rectified,and restart the inverter.
Punganur | May | Inverter 38 | Ground fault | 1217.7 | 44699 | 0.58333 | 44699 | 0.60278 | 0.46667 | DI4 fault | 0.12765 | 0.82602 | 128.394 | Inverter 38 tripped on DI4 fault checked related connections found 1 faulty string rectified,and restart the inverter.
Punganur | May | Inverter 16 | Ground fault | 1183.3800000000001 | 44700 | 0.27431 | 44700 | 0.28611 | 0.28333 | DI4 fault | 0.028543 | 0.82558 | 27.8858 | Inverter 16 tripped on DI4 fault checked related connections found 2 faulty string rectified,and restart the inverter.
Punganur | May | Inverter 38 | Ground fault | 1217.7 | 44700 | 0.58472 | 44700 | 0.59167 | 0.16667 | DI4 fault | 0.017155 | 0.82558 | 17.2461 | Inverter 38 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | May | Inverter 25 | CH2 COM Loss | 1205.1600000000001 | 44701 | 0.28125 | 44701 | 0.36806 | 2.0833 | CH2 COM Loss | 0.028543 | 0.82098 | 28.2407 | Inverter 16 tripped on CH2 COm loss fault checked related connections 2 FO cables changed as per ABB person instructions,and restart the inverter.
Punganur | May | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44706 | 0.60139 | 44706 | 0.62639 | 0.6 | Short ckt fault | 0.41808 | 0.81144 | 406.3857 | Inverter26 tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | May | Inverter 28 | Ground fault | 1205.1600000000001 | 44707 | 0.27917 | 44707 | 0.29375 | 0.35 | DI4 fault | 0.039494 | 0.81698 | 38.8855 | Inverter 28 tripped on DI4 fault checked related connections 2 string found faulty rectified,and restart the inverter.
Punganur | May | Inverter 15 | Short circuit fault | 1212.42 | 44712 | 0.46597 | 44712 | 0.47569 | 0.23333 | Short ckt fault | 0.1808 | 0.80873 | 177.2765 | Inverter 15tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | May | SCB.16.02 | String fault | 14.6 | 44712 | 0.23889 | 44712 | 0.64583 | 9.7667 | String fault | 5.4665 | 0.80873 | 64.5456 | Two faulty strings identified and rectification done
Punganur | June | Inverter 15 | Short circuit fault | 1212.42 | 44714 | 0.66806 | 44714 | 0.69444 | 0.63333 | Short ckt fault | 0.22508 | 0.80861 | 220.6642 | Inverter 15tripped on Short circuit fault checked related connections,and restart the inverter.after generation hours IGBT cleaning done.
Punganur | June | Inverter 28 | Ground fault | 1205.1600000000001 | 44714 | 0.24861 | 44714 | 0.27083 | 0.53333 | DI4 fault | 0.018096 | 0.80861 | 17.6347 | Inverter 28 tripped on DI4 fault checked related connections 2 string found faulty rectified,and restart the inverter.
Punganur | June | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44715 | 0.46389 | 44715 | 0.49167 | 0.66667 | Short ckt fault | 0.57371 | 0.79322 | 545.1381 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter.after generation hours IGBT cleaning done.
Punganur | June | Inverter 18 | Ground fault | 900.24 | 44715 | 0.35417 | 44715 | 0.3625 | 0.2 | DI4 fault | 0.090982 | 0.79322 | 64.9688 | Inverter 18 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | June | SCB.28.06 | String fault | 14.6 | 44715 | 0.25139 | 44715 | 0.60417 | 8.4667 | String fault | 5.0811 | 0.79322 | 58.8439 | Two faulty strings identified and rectification done
Punganur | June | SCB.03.04 | String fault | 14.6 | 44715 | 0.24861 | 44715 | 0.65625 | 9.7833 | String fault | 5.8891 | 0.79322 | 68.2011 | Two faulty strings identified and rectification done
Punganur | June | Inverter 05 | Ground fault | 1190.6400000000001 | 44716 | 0.23681 | 44716 | 0.37847 | 3.4 | DI4 fault | 0.14338 | 0.80646 | 137.6708 | Inverter 05 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | June | Inverter 15 | Short circuit fault | 1212.42 | 44717 | 0.49583 | 44717 | 0.50347 | 0.18333 | Short ckt fault | 0.15953 | 0.79495 | 153.7552 | Inverter 15tripped on Short circuit fault checked related connections,and restart the inverter.
Punganur | June | Inverter 22 | Ground fault | 1190.6400000000001 | 44718 | 0.28125 | 44718 | 0.29861 | 0.41667 | DI4 fault | 0.037692 | 0.80636 | 36.1871 | Inverter 22 tripped on DI4 fault checked related connections found 4 faulty strings rectified,and restart the inverter.
Punganur | June | SCB.22.07 | String fault | 29.2 | 44718 | 0.29861 | 44718 | 0.52083 | 5.3333 | String fault | 3.2975 | 0.80636 | 77.643 | Four faulty strings identified and rectification done
Punganur | June | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44720 | 0.25278 | 44720 | 0.27083 | 0.43333 | Short ckt fault | 0.013988 | 0.79798 | 13.3712 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter.after generation hours IGBT cleaning done.
Punganur | June | Inverter 30 | Ground fault | 1217.7 | 44720 | 0.32778 | 44720 | 0.33472 | 0.16667 | DI4 fault | 0.048875 | 0.79798 | 47.4921 | Inverter 31 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | June | Feeder 03 | Ground fault | 11681.670000000002 | 44721 | 0.45764 | 44721 | 0.4625 | 0.11667 | E/L fault | 0.097093 | 0.79777 | 904.8462 | Feeder 3 tripped on E/L ,trail charge taken T/M line withstanded and feeder charged.
Punganur | June | SCB.01.03 | String fault | 29.2 | 44723 | 0.25139 | 44723 | 0.52083 | 6.4667 | String fault | 3.0697 | 0.81393 | 72.9559 | Four faulty strings identified and rectification done
Punganur | June | Inverter 11 | Short circuit fault | 1197.9000000000001 | 44724 | 0.37986 | 44724 | 0.40278 | 0.55 | Short ckt fault | 0.35688 | 0.80876 | 345.7538 | Inverter 11 tripped on Short circuit fault checked related connections,and restart the inverter.after generation hours IGBT cleaning done.
Punganur | June | Inverter 01 | Ground fault | 1212.42 | 44724 | 0.42222 | 44724 | 0.42778 | 0.13333 | DI4 fault | 0.10807 | 0.80876 | 105.9693 | Inverter 1 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | June | All Inverters | Grid failure | 47694.570000000007 | 44725 | 0.51806 | 44725 | 0.52917 | 0.26667 | Grid down | 0.22797 | 0.82486 | 8968.5449 | Grid down from GSS end
Punganur | June | Feeder 03 | Ground fault | 11681.670000000002 | 44727 | 0.70764 | 44727 | 0.7125 | 0.11667 | E/L fault | 0.030999 | 0.80621 | 291.9513 | Feeder 3 tripped on E/L ,trail charge taken T/M line withstanded and feeder charged.
Punganur | June | Inverter 30 | Short circuit fault | 1217.7 | 44727 | 0.51667 | 44727 | 0.52569 | 0.21667 | Short ckt fault | 0.21391 | 0.80621 | 209.9978 | Inverter 30 tripped on Short circuit fault checked related connections,and restart the inverter.after generation hours IGBT cleaning done.
Punganur | June | SCB.08.05 | String fault | 29.2 | 44728 | 0.25208 | 44728 | 0.52083 | 6.45 | String fault | 3.006 | 0.82176 | 72.131 | Four faulty strings identified and rectification done
Punganur | June | Feeder 01 | Ground fault | 12013.320000000002 | 44729 | 0.38333 | 44729 | 0.38611 | 0.066667 | E/L fault | 0.03605 | 0.82575 | 357.6181 | Feeder 1 tripped on E/L ,trail charge taken T/M line withstanded and feeder charged.
Punganur | June | Inverter 27 | Short circuit fault | 1212.42 | 44730 | 0.47847 | 44730 | 0.48958 | 0.26667 | Short ckt fault | 0.16962 | 0.8212 | 168.8793 | Inverter 27 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | June | Inverter 27 | Short circuit fault | 1212.42 | 44730 | 0.51667 | 44730 | 0.53472 | 0.43333 | Short ckt fault | 0.15293 | 0.8212 | 152.2653 | Inverter 27 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | June | Inverter 27 | Short circuit fault | 1212.42 | 44730 | 0.63889 | 44730 | 0.68542 | 1.1167 | Short ckt fault | 0.27388 | 0.8212 | 272.6909 | Inverter 27 tripped on Short circuit fault checked related connections,and ISU 3 U FRC cable changed ,restarted the inverter.
Punganur | June | Inverter 30 | Ground fault | 1217.7 | 44732 | 0.53264 | 44732 | 0.54583 | 0.31667 | Earth fault | 0.23222 | 0.81317 | 229.9409 | Inverter 30 tripped on earth fault checked related connections found ISU 1 B-phase fuse failure replaced, inverter restarted.
Punganur | June | Inverter 33 | Ground fault | 1173.1500000000001 | 44732 | 0.31806 | 44732 | 0.33056 | 0.3 | DI4 fault | 0.062613 | 0.81317 | 59.7308 | Inverter 33 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | June | Inverter 15 | Exhaust fan faulty | 1212.42 | 44733 | 0.45417 | 44733 | 0.48125 | 0.65 | Exhaust Fan | 0.55032 | 0.81853 | 546.1326 | Inverter-15 Exhaust fan is failure and replaced with new one.
Punganur | June | Feeder 01 | Isolator Issue | 12013.320000000002 | 44733 | 0.3125 | 44733 | 0.33403 | 0.51667 | Isolator Issue | 0.13396 | 0.81853 | 1317.2208 | Feeder-03,Line isolator Female contact issue at GSS End ad rectification done
Punganur | June | SCB.27.01 | String fault | 21.78 | 44736 | 0.24167 | 44736 | 0.78056 | 12.9333 | String fault | 6.7397 | 0.8128 | 119.3105 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.03 | String fault | 43.56 | 44736 | 0.24167 | 44736 | 0.78056 | 12.9333 | String fault | 6.7397 | 0.8128 | 238.621 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.04 | String fault | 29.04 | 44736 | 0.24167 | 44736 | 0.78056 | 12.9333 | String fault | 6.7397 | 0.8128 | 159.0807 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.01 | String fault | 21.78 | 44737 | 0.24306 | 44737 | 0.78125 | 12.9167 | String fault | 5.034 | 0.82079 | 89.9927 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.03 | String fault | 43.56 | 44737 | 0.24306 | 44737 | 0.78125 | 12.9167 | String fault | 5.034 | 0.82079 | 179.9855 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.04 | String fault | 29.04 | 44737 | 0.24306 | 44737 | 0.78125 | 12.9167 | String fault | 5.034 | 0.82079 | 119.9903 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.01 | String fault | 21.78 | 44738 | 0.24236 | 44738 | 0.77986 | 12.9 | String fault | 5.8327 | 0.81272 | 103.2456 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.03 | String fault | 43.56 | 44738 | 0.24236 | 44738 | 0.77986 | 12.9 | String fault | 5.8327 | 0.81272 | 206.4912 | String fauilure was not identify due to continues climate changes
Punganur | June | SCB.27.04 | String fault | 29.04 | 44738 | 0.24236 | 44738 | 0.77986 | 12.9 | String fault | 5.8327 | 0.81272 | 137.6608 | String fauilure was not identify due to continues climate changes
Punganur | June | Feeder 02 | Ground fault | 12042.360000000002 | 44739 | 0.56111 | 44739 | 0.56389 | 0.066667 | Earth Fault | 0.048595 | 0.83589 | 489.1608 | Feeder 2 tripped on E/L ,trail charge taken T/M line withstanded and feeder charged.
Punganur | June | Inverter 27 | Auto reset fault | 1212.42 | 44739 | 0.56111 | 44739 | 0.575 | 0.33333 | Autoreset fault | 0.17942 | 0.83589 | 181.8316 | Inverter 27 tripped on Autoreset fault, checked the related circuit and restarted the inverter.
Punganur | June | Inverter 28 | Auto reset fault | 1205.1600000000001 | 44739 | 0.56111 | 44739 | 0.575 | 0.33333 | Autoreset fault | 0.17942 | 0.83589 | 180.7428 | Inverter 28 tripped on Autoreset fault, checked the related circuit and restarted the inverter.
Punganur | June | SCB.27.01 | String fault | 21.78 | 44739 | 0.25 | 44739 | 0.55278 | 7.2667 | String fault | 2.9146 | 0.83589 | 53.0628 | Three faulty strings identified and rectification done
Punganur | June | SCB.27.03 | String fault | 43.56 | 44739 | 0.25 | 44739 | 0.62708 | 9.05 | String fault | 3.6565 | 0.83589 | 133.1377 | Six faulty strings identified and rectification done
Punganur | June | SCB.27.04 | String fault | 29.04 | 44739 | 0.25 | 44739 | 0.62708 | 9.05 | String fault | 3.6565 | 0.83589 | 88.7585 | Four faulty strings identified and rectification done
Punganur | July | IDT 11 | Ground fault | 2389 | 44743 | 0.25417 | 44743 | 0.41667 | 3.9 | Block-06 Out going tripped on E/L & O/L fault due to CT flashover | 1.3266 | 0.8087 | 2562.9278 | Replaced the CT and charged panel
Punganur | July | IDT 12 | Ground fault | 2396 | 44743 | 0.25417 | 44743 | 0.35278 | 2.3667 | Block-06 Out going tripped on E/L & O/L fault due to CT flashover | 0.44964 | 0.8087 | 871.244 | Replaced the CT and charged panel
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44744 | 0.50347 | 44744 | 0.52083 | 0.41667 | Short ckt fault | 0.31962 | 0.82187 | 314.6685 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | All Inverters | Grid failure | 47694.570000000007 | 44746 | 0.35 | 44746 | 0.37014 | 0.48333 | Grid down | 0.15013 | 0.85944 | 6154.1042 | Grid down from GSS end
Punganur | July | Inverter 08 | Short circuit fault | 1190.6400000000001 | 44750 | 0.43264 | 44750 | 0.44583 | 0.31667 | Short ckt fault | 0.15842 | 0.89289 | 168.4131 | Inverter 8 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 08 | Short circuit fault | 1190.6400000000001 | 44751 | 0.55486 | 44751 | 0.55903 | 0.1 | Short ckt fault | 0.083127 | 0.8361 | 82.7528 | Inverter 8 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 15 | DI1 fault | 1212.42 | 44751 | 0.52292 | 44751 | 0.54375 | 0.5 | DI1 fault | 0.36064 | 0.8361 | 365.5838 | Inverter 15 tripped on DI1 fault checked related connections,found ISU 3 Fan problem,replaced and restart the inverter.
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44755 | 0.68611 | 44755 | 0.69514 | 0.21667 | Short ckt fault | 0.051393 | 0.82292 | 50.6626 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 06 | Auto reset fault | 1219.68 | 44757 | 0.54583 | 44757 | 0.55 | 0.1 | Autoreset fault | 0.1012 | 0.81064 | 100.0601 | Inverter 6 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44759 | 0.50486 | 44759 | 0.51042 | 0.13333 | Short ckt fault | 0.077529 | 0.8483 | 78.7834 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Feeder 03 | Ground fault | 11681.670000000002 | 44760 | 0.33056 | 44760 | 0.37083 | 0.96667 | Earth Fault | 0.22671 | 0.84529 | 2238.6542 | Feeder 3 tripped on E/L,Due to relay not getting reset feeder late.
Punganur | July | All Inverters | Grid failure | 47694.570000000007 | 44761 | 0.54097 | 44761 | 0.54236 | 0.033333 | Grid fluctuation | 0.032658 | 0.80017 | 1246.363 | Grid fluctuation due to local feder issue.
Punganur | July | All Inverters | Grid failure | 47694.570000000007 | 44761 | 0.54653 | 44761 | 0.54792 | 0.033333 | Grid fluctuation | 0.032165 | 0.80017 | 1227.5483 | Grid fluctuation due to local feder issue.
Punganur | July | All Inverters | Grid failure | 47694.570000000007 | 44761 | 0.57222 | 44761 | 0.57292 | 0.016667 | Grid fluctuation | 0.013777 | 0.80017 | 525.7623 | Grid fluctuation due to local feder issue.
Punganur | July | Inverter 13 | Ground fault | 1212.42 | 44761 | 0.55 | 44761 | 0.56528 | 0.36667 | DI4 fault | 0.33509 | 0.80017 | 325.0802 | Inverter 13 tripped on DI4 fault checked related connections found 2 strings faulty rectified,and restart the inverter.
Punganur | July | Inverter 22 | CH2 COM Loss | 1190.6400000000001 | 44761 | 0.54306 | 44761 | 0.55208 | 0.21667 | CH2 COM Loss | 0.20912 | 0.80017 | 199.2356 | Inverter 22 tripped on CH2 com loss fault checked related connections,and restart the inverter.
Punganur | July | Inverter 30 | Ground fault | 1217.7 | 44761 | 0.60972 | 44761 | 0.61667 | 0.16667 | DI4 fault | 1.3155 | 0.80017 | 1281.7697 | Inverter 30 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | July | Inverter 18 | Short circuit fault | 900.24 | 44762 | 0.64653 | 44762 | 0.65278 | 0.15 | Short ckt fault | 0.053163 | 0.82309 | 39.3928 | Inverter 18 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 40 | Short circuit fault | 1202.8499999999999 | 44765 | 0.65903 | 44765 | 0.66458 | 0.13333 | Short ckt fault | 0.012431 | 0.82653 | 12.3584 | Inverter 40 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 02 | Ground fault | 1168.8599999999999 | 44768 | 0.64583 | 44768 | 0.77986 | 3.2167 | Earth fault & Current unbalance | 0.48231 | 0.83867 | 472.8001 | Inverter 2 tripped on Earth fault & Current unbalance fault checked related connections found the ISU 3 IGBT stag problem kept in group 2 mode,and restart the inverter
Punganur | July | Feeder 02 | Ground fault | 12042.360000000002 | 44769 | 0.50208 | 44769 | 0.50694 | 0.11667 | E/L & OL | 0.22671 | 0.80415 | 2195.4579 | Feeder 2 tripped on E/L & O/L ,fault. Trail charge taken ,feeder withstand.
Punganur | July | Inverter 02 | ISU stag issue | 1168.8599999999999 | 44769 | 0.40625 | 44769 | 0.65278 | 5.9167 | Run on 70 % load | 1.22 | 0.80415 | 1146.7287 | Inverter 2 runed on 70% load due to ISU 3 stag issue.
Punganur | July | Inverter 02 | ISU stag issue | 1168.8599999999999 | 44770 | 0.39583 | 44770 | 0.58333 | 4.5 | Run on 70 % load | 0.58 | 0.83403 | 565.4211 | Inverter 2 runed on 70% load due to ISU 3 stag issue.
Punganur | July | Inverter 02 | ISU stag issue | 1168.8599999999999 | 44771 | 0.39583 | 44771 | 0.58681 | 4.5833 | Run on 70 % load | 0.56 | 0.79041 | 517.3704 | Inverter 2 runed on 70% load due to ISU 3 stag issue.
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44771 | 0.43472 | 44771 | 0.43889 | 0.1 | Short ckt fault | 0.090866 | 0.79041 | 86.0346 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44771 | 0.55208 | 44771 | 0.5625 | 0.25 | Short ckt fault | 0.2443 | 0.79041 | 231.308 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 36 | Ground fault | 1232.55 | 44771 | 0.71528 | 44771 | 0.72361 | 0.2 | DI4 fault | 0.028772 | 0.79041 | 28.0302 | Inverter 36 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | July | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44773 | 0.50486 | 44773 | 0.51181 | 0.16667 | Short ckt fault | 0.12561 | 0.86831 | 130.6477 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | July | Inverter 11 | Ground fault | 1197.9000000000001 | 44773 | 0.54583 | 44773 | 0.5625 | 0.4 | Earth fault | 0.28275 | 0.86831 | 294.1051 | Inverter 11 tripped on earth fault checked related connections,found ISU 1 B-phase fuse blown replaced and restart the inverter
Punganur | August | Inverter 26 | Short circuit fault | 1197.9000000000001 | 44774 | 0.37431 | 44774 | 0.38333 | 0.21667 | Short ckt fault | 0.10594 | 0.81745 | 103.7382 | Inverter 26 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | August | Inverter 33 | Ground fault | 1173.1500000000001 | 44775 | 0.31389 | 44775 | 0.32847 | 0.35 | DI4 fault | 0.081711 | 0.85478 | 81.9388 | Inverter 33 tripped on DI4 fault checked related connections found 2 string afulty rectified,and restart the inverter.
Punganur | August | SCB.33.07 | String fault | 21.78 | 44775 | 0.32847 | 44775 | 0.44931 | 2.9 | String fault | 1.7018 | 0.85478 | 31.6834 | 3 nof of String fauilures rectification done
Punganur | August | Inverter 20 | Net loss fault | 1197.9000000000001 | 44776 | 0.53819 | 44776 | 0.56736 | 0.7 | Net loss | 0.015652 | 0.83755 | 15.7036 | Inverter 20 tripped on Net loss fault checked related connections,and restart the inverter
Punganur | August | Inverter 20 | Ground fault | 1197.9000000000001 | 44776 | 0.58542 | 44776 | 0.60278 | 0.41667 | DI4 fault | 0.010889 | 0.83755 | 10.9244 | Inverter 20 tripped on DI4 fault checked related connections found 3 string faulty rectified,and restart the inverter.
Punganur | August | Inverter 38 | Ground fault | 1217.7 | 44776 | 0.65208 | 44776 | 0.65833 | 0.15 | DI4 fault | 0.024041 | 0.83755 | 24.5187 | Inverter 38 tripped on DI4 fault checked related connections found 1 string faulty rectified,and restart the inverter.
Punganur | August | Inverter 38 | Ground fault | 1217.7 | 44776 | 0.7 | 44776 | 0.71458 | 0.35 | DI4 fault | 0.051906 | 0.83755 | 52.9375 | Inverter 38 tripped on DI4 fault checked related connections found 1 string faulty rectified,and restart the inverter.
Punganur | August | Inverter 20 | Ground fault | 1197.9000000000001 | 44777 | 0.28958 | 44777 | 0.3125 | 0.55 | DI4 fault | 0.060593 | 0.87227 | 63.3137 | Inverter 20 tripped on DI4 fault checked related connections found 2 string faulty rectified,and restart the inverter.
Punganur | August | SCB.20.04 | Ground fault | 14.52 | 44777 | 0.3125 | 44777 | 0.45486 | 3.4167 | DI4 fault | 1.0582 | 0.87227 | 13.4026 | 2 nof of String fauilures rectification done
Punganur | August | Inverter 02 | Auxilary supply failure | 1168.8599999999999 | 44778 | 0.26597 | 44778 | 0.29028 | 0.58333 | Auxilary supply fail | 0.027872 | 0.85116 | 27.7291 | Inverter 39 tripped due Aux supply cable issue,New cable layed and restart the inverter.
Punganur | August | Inverter 18 | Short circuit fault | 900.24 | 44778 | 0.35694 | 44778 | 0.36389 | 0.16667 | Short ckt fault | 0.07 | 0.85116 | 53.6372 | Inverter 18 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | August | Inverter 20 | Ground fault | 1197.9000000000001 | 44778 | 0.29028 | 44778 | 0.29583 | 0.13333 | DI4 fault | 0.010904 | 0.85116 | 11.1177 | Inverter 26 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | August | Inverter 20 | Ground fault | 1197.9000000000001 | 44780 | 0.5 | 44780 | 0.50833 | 0.2 | DI4 fault | 0.04585 | 0.86807 | 47.6776 | Inverter 20 tripped on DI4 fault checked related connections,found 2 strings fault rectified,and restart the inverter.
Punganur | August | SCB.20.08 | Ground fault | 14.52 | 44780 | 0.3125 | 44780 | 0.51389 | 4.8333 | DI4 fault | 1.3286 | 0.86807 | 16.7466 | 2 nof of String fauilures rectification done
Punganur | August | All Inverters | Grid failure | 47694.570000000007 | 44781 | 0.57708 | 44781 | 0.57847 | 0.033333 | Grid fluctuation | 0.020653 | 0.86009 | 847.2086 | Grid fluctuation due to local feder issue.
Punganur | August | All Inverters | Grid failure | 47694.570000000007 | 44781 | 0.74514 | 44781 | 0.74931 | 0.1 | Grid fluctuation | 0.001717 | 0.86009 | 70.4344 | Grid fluctuation due to local feder issue.
Punganur | August | SCB.09.08 | Ground fault | 43.56 | 44781 | 0.27083 | 44781 | 0.55556 | 6.8333 | DI4 fault | 2.2777 | 0.86009 | 85.335 | 6 nof of String fauilures rectification done
Punganur | August | Inverter 30 | Short circuit fault | 1217.7 | 44783 | 0.60069 | 44783 | 0.61944 | 0.45 | Short ckt fault | 0.14494 | 0.80393 | 141.8934 | Inverter 30 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | August | SCB.36.06 | Ground fault | 43.56 | 44785 | 0.27083 | 44785 | 0.52778 | 6.1667 | DI4 fault | 3.4683 | 0.80519 | 121.6474 | 4 nof of String fauilures rectification done
Punganur | August | SCB.40.01 | Ground fault | 14.52 | 44785 | 0.27083 | 44785 | 0.54514 | 6.5833 | DI4 fault | 3.7308 | 0.80519 | 43.6176 | 2 nof of String fauilures rectification done
Punganur | August | SCB.39.01 | Ground fault | 7.26 | 44785 | 0.27083 | 44785 | 0.54514 | 6.5833 | DI4 fault | 3.7308 | 0.80519 | 21.8088 | 1 nof of String fauilures rectification done
Punganur | August | Inverter 11 | Ground fault | 1197.9000000000001 | 44788 | 0.33611 | 44788 | 0.35069 | 0.35 | DI4 fault | 0.093118 | 0.82463 | 91.9836 | Inverter 11 tripped on DI4 fault checked related connections,and restart the inverter.
Punganur | August | Inverter 15 | Short circuit fault | 1212.42 | 44789 | 0.31528 | 44789 | 0.32847 | 0.31667 | Short ckt fault | 0.088781 | 0.79122 | 85.1661 | Inverter 15 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | August | Inverter 40 | Auxilary supply failure | 1202.8499999999999 | 44790 | 0.25694 | 44790 | 0.28125 | 0.58333 | Auxilary supply fail | 0.029861 | 0.79268 | 28.4717 | Inverter 40 tripped due Aux supply cable issue,New cable layed and restart the inverter.
Punganur | August | Inverter 16 | Ground fault | 1183.3800000000001 | 44790 | 0.45208 | 44790 | 0.45556 | 0.083333 | DI4 | 0.057309 | 0.79268 | 53.7587 | Inverter 16 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 36 | Temp. difference fault | 1232.55 | 44790 | 0.5375 | 44790 | 0.54861 | 0.26667 | Temperature difference | 0.26378 | 0.79268 | 257.718 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | August | IDT 18 | Buchloz trip | 2931 | 44791 | 0.51875 | 44791 | 0.52778 | 0.21667 | Buchloz trip | 0.19132 | 0.80402 | 450.8697 | Trafo 18 tripped due to trafo 19 fault auxilary supply fail.
Punganur | August | IDT 19 | Buchloz trip | 2421 | 44791 | 0.51875 | 44791 | 0.54583 | 0.65 | Buchloz trip | 0.54408 | 0.80402 | 1059.0763 | Trafo 19 tripped on Bucholz trip fault checked related connections,found water in buchloz terminal box.
Punganur | August | Inverter 39 | Auxilary supply failure | 1173.1500000000001 | 44791 | 0.30556 | 44791 | 0.31528 | 0.23333 | Auxilary supply fail | 0.048776 | 0.80402 | 46.0074 | Inverter 40 tripped due Aux supply cable issue,New cable layed and restart the inverter.
Punganur | August | Block 10 | Short circuit fault | 4811.3999999999996 | 44792 | 0.48889 | 44792 | 0.49653 | 0.18333 | Short ckt fault | 0.11488 | 0.8215 | 454.0654 | Block 10 inverters tripped due to 3-phase exhaust fan cables short circuited.
Punganur | August | SCB.22.01 | Ground fault | 14.52 | 44793 | 0.25208 | 44793 | 0.56111 | 7.4167 | DI4 | 4.03 | 0.80943 | 47.3644 | 2 nof of String failures rectification done
Punganur | August | Inverter 25 | Ground fault | 1205.1600000000001 | 44793 | 0.36319 | 44793 | 0.36458 | 0.033333 | DI4 | 0.02 | 0.80943 | 19.5099 | Inverter 25 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 10 | Ground fault | 1190.6400000000001 | 44794 | 0.38542 | 44794 | 0.39583 | 0.25 | DI4 | 0.16844 | 0.80772 | 161.9936 | Inverter 10 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 36 | Temp. difference fault | 1232.55 | 44796 | 0.43958 | 44796 | 0.44167 | 0.05 | Temperature difference | 0.046632 | 0.8032 | 46.1647 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | August | Inverter 11 | Ground fault | 1197.9000000000001 | 44797 | 0.27083 | 44797 | 0.28472 | 0.33333 | DI4 | 0.012613 | 0.81231 | 12.2736 | Inverter 11 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 11 | Ground fault | 1197.9000000000001 | 44798 | 0.57431 | 44798 | 0.58194 | 0.18333 | DI4 | 0.17611 | 0.81013 | 170.9065 | Inverter 11 tripped on DI4 fault checked related connections, found 1 string faulty rectified,and restart the inverter
Punganur | August | Inverter 36 | Temp. difference fault | 1232.55 | 44800 | 0.52014 | 44800 | 0.52222 | 0.05 | Temperature difference | 0.04127 | 0.8239 | 41.91 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | August | Inverter 34 | Ground fault | 1217.7 | 44800 | 0.675 | 44800 | 0.69236 | 0.41667 | DI4 | 0.066142 | 0.8239 | 66.3576 | Inverter 34 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | IDT 08 | Master trip | 2396 | 44801 | 0.34583 | 44801 | 0.36944 | 0.56667 | Master trip | 0.23016 | 0.82186 | 453.2317 | Due to T/L line fluctuations Trafo 8 tripped on Masterl trip fault checked related connections, charged transformer.
Punganur | August | Inverter 35 | Ground fault | 1188 | 44801 | 0.63194 | 44801 | 0.63819 | 0.15 | DI4 | 0.084682 | 0.82186 | 82.6814 | Inverter 35 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 11 | Ground fault | 1197.9000000000001 | 44802 | 0.43611 | 44802 | 0.44583 | 0.23333 | DI4 | 0.11441 | 0.81218 | 111.3084 | Inverter 11 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | Inverter 07 | Ground fault | 1190.6400000000001 | 44802 | 0.53194 | 44802 | 0.54167 | 0.23333 | DI4 | 0.1716 | 0.81218 | 165.9439 | Inverter 7 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | August | SCB.20.03 | Ground fault | 21.78 | 44802 | 0.27361 | 44802 | 0.44444 | 4.1 | DI4 | 1.262 | 0.81218 | 22.3234 | 3 nof of String failures rectification done
Punganur | August | Inverter 31 | Ground fault | 1217.7 | 44803 | 0.48264 | 44803 | 0.49653 | 0.33333 | Earth fault | 0.33391 | 0.78457 | 319.006 | Inverter 31 tripped on Earth fault fault checked related connections,found ISU 2 B-phase fuse blown replaced &and restart the inverter
Punganur | August | SCB.31.03 | Ground fault | 14.52 | 44803 | 0.29931 | 44803 | 0.46528 | 3.9833 | DI4 | 1.5735 | 0.78457 | 17.9248 | 2 nof of String failures rectification done
Punganur | August | Inverter 36 | Temp. difference fault | 1232.55 | 44803 | 0.55208 | 44803 | 0.55486 | 0.066667 | Temperature difference | 0.065935 | 0.78457 | 63.7612 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | September | Inverter 30 | Ground fault | 1217.7 | 44805 | 0.5125 | 44805 | 0.53125 | 0.45 | Earth fault | 0.26421 | 0.81951 | 263.6641 | Inverter 30 tripped on Earth fault fault checked related connections,found ISU 2 B-phase fuse blown replaced &and restart the inverter
Punganur | September | Inverter 17 | Ground fault | 1234.2 | 44805 | 0.67639 | 44805 | 0.68542 | 0.21667 | DI4 | 0.0086645 | 0.81951 | 8.7637 | Inverter 17 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 09 | Ground fault | 1205.1600000000001 | 44806 | 0.52222 | 44806 | 0.52431 | 0.05 | DI4 | 0.064208 | 0.77545 | 60.005 | Inverter 9 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 36 | Temp. difference fault | 1232.55 | 44806 | 0.5 | 44806 | 0.50556 | 0.13333 | Temperature difference | 0.14021 | 0.77545 | 134.0118 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | September | Inverter 34 | Net loss fault | 1217.7 | 44807 | 0.39028 | 44807 | 0.40278 | 0.3 | Net loss | 0.22445 | 0.81127 | 221.7354 | Inverter 34 tripped on Net loss fault checked related connections,and restart the inverter
Punganur | September | Inverter 38 | Ground fault | 1217.7 | 44808 | 0.32014 | 44808 | 0.33194 | 0.28333 | DI4 | 0.064509 | 0.81695 | 64.1742 | Inverter 38 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | SCB.29.02 | Ground fault | 14.52 | 44808 | 0.24722 | 44808 | 0.48958 | 5.8167 | DI4 | 2.0295 | 0.81695 | 24.0741 | 2 nof of String failures rectification done
Punganur | September | SCB.12.06 | String fault | 7.3479999999999999 | 44809 | 0.25139 | 44809 | 0.53264 | 6.75 | String fault | 4.25 | 0.77111 | 24.0809 | 1 nof of String failures rectification done
Punganur | September | SCB.01.03 | String fault | 14.52 | 44809 | 0.25139 | 44809 | 0.49444 | 5.8333 | String fault | 3.28 | 0.77111 | 36.7244 | 2 nof of String failures rectification done
Punganur | September | Feeder 02 | Ground fault | 12042.360000000002 | 44809 | 0.72222 | 44809 | 0.76319 | 0.98333 | E/L fault | 0.02 | 0.77111 | 185.7187 | Feeder-02 tripped on E/L fault
Punganur | September | Inverter 36 | Temp. difference fault | 1232.55 | 44810 | 0.51042 | 44810 | 0.5125 | 0.05 | Temperature difference | 0.05 | 0.81078 | 49.9665 | Inverter 36 tripped on temperature difference fault checked related connections,and restart the inverter
Punganur | September | Inverter 31 | Ground fault | 1217.7 | 44810 | 0.66111 | 44810 | 0.66528 | 0.1 | DI4 | 0.0147 | 0.81078 | 14.5132 | Inverter 31 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 31 | Ground fault | 1217.7 | 44811 | 0.31458 | 44811 | 0.325 | 0.25 | DI4 | 0.03273 | 0.82115 | 32.7272 | Inverter 31 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 34 | Ground fault | 1217.7 | 44811 | 0.30069 | 44811 | 0.31597 | 0.36667 | DI4 | 0.037099 | 0.82115 | 37.0961 | Inverter 34 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | SCB.34.04 | String fault | 21.78 | 44811 | 0.33681 | 44811 | 0.4375 | 2.4167 | String fault | 0.93281 | 0.82115 | 16.6829 | 3 nof of String failures rectification done
Punganur | September | Inverter 06 | Ground fault | 1219.68 | 44812 | 0.58056 | 44812 | 0.58472 | 0.1 | DI4 | 0.025204 | 0.88716 | 27.2721 | Inverter 6 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 06 | Ground fault | 1219.68 | 44812 | 0.63819 | 44812 | 0.65347 | 0.36667 | DI4 | 0.00836 | 0.88716 | 9.046 | Inverter 6 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 06 | Ground fault | 1219.68 | 44813 | 0.50417 | 44813 | 0.50833 | 0.1 | DI4 | 0.080823 | 0.82481 | 81.3081 | Inverter 6 tripped on DI4 fault checked related connections,and restart the inverter
Punganur | September | Inverter 35 | Short circuit fault | 1188 | 44813 | 0.50903 | 44813 | 0.5125 | 0.083333 | Short ckt fault | 0.057533 | 0.82481 | 56.3753 | Inverter 35 tripped on Short circuit fault checked related connections,and restart the inverter
Punganur | September | Feeder 01 | Ground fault | 12013.320000000002 | 44817 | 0.34028 | 44817 | 0.40278 | 1.5 | E/L fault | 0.90042 | 0.77845 | 8420.53 | Feeder 1 tripped on E/L,Due to relay not getting reset feeder charged late.
Punganur | September | IDT 08 | Ground fault | 2396 | 44817 | 0.44653 | 44817 | 0.50694 | 1.45 | E/L & OL Fault | 2.065 | 0.77845 | 3851.6165 | Block 4 OG feeder tripped on E/L & O/L fault, Checked trafos found trafo 8 HT busing flashover,rectification work done.
Punganur | September | All Inverters | Grid failure | 47694.570000000007 | 44818 | 0.65278 | 44818 | 0.65347 | 0.016667 | Grid fluctuation | 0.010431 | 0.78754 | 391.8196 | Grid fluctuation due to local feder issue.
Sepset 01 | April | Inverter 01 | Ground fault | 3478 | 44654 | 0.45903 | 44654 | 0.46389 | 0.11667 | Inverter Trip on ground fault | 0.1 | 0.73042 | 254.0417 | Inverter restored manually.
Sepset 01 | April | Inverter 02 | Contactor fault | 859 | 44664 | 0.34236 | 44664 | 0.35486 | 0.3 | Unit-1 Trip on contactor fault | 0.11 | 0.70338 | 66.4619 | Inverter restored manually.
Sepset 01 | April | Inverter 08 | Ground fault | 3497 | 44664 | 0.44861 | 44664 | 0.45486 | 0.15 | Inverter Trip on ground fault | 0.13 | 0.70338 | 319.7614 | Inverter restored manually.
Sepset 01 | April | Inverter 08 | Ground fault | 3497 | 44665 | 0.42431 | 44665 | 0.43264 | 0.2 | Inverter Trip on ground fault | 0.16 | 0.71738 | 401.3888 | Inverter restored manually.
Sepset 01 | April | Inverter 01 | AC under voltage | 3478 | 44666 | 0.68194 | 44666 | 0.68264 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69988 | 24.3418 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 01 | AC under voltage | 3478 | 44666 | 0.70139 | 44666 | 0.70208 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69988 | 24.3418 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 01 | PM high fault | 741 | 44667 | 0.50556 | 44667 | 0.50694 | 0.033333 | Unit 4 tripped on PM high fault. | 0.03 | 0.71113 | 15.8085 | Inverter auto restart automatically.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44670 | 0.59236 | 44670 | 0.60625 | 0.33333 | Inverter tripped on AC under voltage | 0.28 | 0.69695 | 5405.1534 | Inverter restored manually.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44671 | 0.59792 | 44671 | 0.61319 | 0.36667 | Inverter tripped on AC under voltage | 0.31 | 0.71517 | 6140.7429 | Inverter restored manually.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44671 | 0.67778 | 44671 | 0.68403 | 0.15 | Inverter tripped on AC under voltage | 0.07 | 0.71517 | 1386.6194 | Inverter restored manually.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44671 | 0.71458 | 44671 | 0.72639 | 0.28333 | Inverter tripped on AC under voltage | 0.05 | 0.71517 | 990.4424 | Inverter restored manually.
Sepset 01 | April | Inverter 01 | AC under voltage | 3478 | 44674 | 0.35486 | 44674 | 0.35556 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71045 | 24.7095 | Inverter auto restart automatically.
Sepset 01 | April | SCB.01.05 | String fault | 13 | 44674 | 0.62847 | 44674 | 0.62986 | 0.033333 | positive side Y-connector failure | 0.01 | 0.71045 | 0.092359 | positive side Y-connector replaced & string power restored.
Sepset 01 | April | SCB.01.06 | String fault | 13 | 44674 | 0.65278 | 44674 | 0.65417 | 0.033333 | positive side Y-connector failure | 0.01 | 0.71045 | 0.092359 | positive side Y-connector, positive mc4 replaced & string power restored.
Sepset 01 | April | All Inverters | PDP pro fault | 24300 | 44675 | 0.42986 | 44675 | 0.43194 | 0.05 | Inverter Trip on PDP pro fault | 0.01 | 0.7191 | 898 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 03 | PDP pro fault | 3458 | 44676 | 0.30486 | 44676 | 0.30694 | 0.05 | Inverter Trip on PDP pro fault | 0.009 | 0.71633 | 22.2935 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 05 | PDP pro fault | 3479 | 44676 | 0.30486 | 44676 | 0.30694 | 0.05 | Inverter Trip on PDP pro fault | 0.009 | 0.71633 | 22.4289 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 06 | PDP pro fault | 3510 | 44676 | 0.30486 | 44676 | 0.30694 | 0.05 | Inverter Trip on PDP pro fault | 0.009 | 0.71633 | 22.6287 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 07 | PDP pro fault | 3439 | 44676 | 0.30486 | 44676 | 0.30694 | 0.05 | Inverter Trip on PDP pro fault | 0.009 | 0.71633 | 22.171 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 08 | PDP pro fault | 3497 | 44676 | 0.30486 | 44676 | 0.30694 | 0.05 | Inverter Trip on PDP pro fault | 0.009 | 0.71633 | 22.5449 | Inverter auto restart automatically.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44676 | 0.67778 | 44676 | 0.77431 | 2.3167 | 33kv grid supply failure from 132/33 kv substation end | 0.39 | 0.71633 | 7737.9043 | Grid supply resumed at 18:42 hrs.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44677 | 0.60208 | 44677 | 0.6125 | 0.25 | 33kv grid supply failure from 132/33 kv substation end | 0.21 | 0.7212 | 4194.9175 | Grid supply restored at 14:42 hrs. & all inverters power limit set at 80 %
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44678 | 0.60347 | 44678 | 0.61319 | 0.23333 | Inverter tripped on AC under voltage | 0.2 | 0.70764 | 3920.0647 | Inverter restored manually.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44679 | 0.56806 | 44679 | 0.57361 | 0.13333 | Inverter tripped on AC under voltage | 0.13 | 0.69905 | 2517.1012 | Inverter restored manually.
Sepset 01 | April | Inverter 02 | PDP pro fault | 3439 | 44679 | 0.58958 | 44679 | 0.59167 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.69905 | 120.2018 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 03 | PDP pro fault | 3458 | 44679 | 0.58958 | 44679 | 0.59167 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.69905 | 120.8659 | Inverter auto restart automatically.
Sepset 01 | April | Inverter 01 | AC under voltage | 3478 | 44680 | 0.63125 | 44680 | 0.63194 | 0.016667 | Inverter tripped on AC under voltage | 0.02 | 0.71787 | 49.9351 | Inverter auto restart automatically.
Sepset 01 | April | All Inverters | Grid failure | 27698 | 44681 | 0.50069 | 44681 | 0.61806 | 2.8167 | 33 kv grid supply failed from substation end. | 2.34 | 0.43913 | 28461.6045 | Grid supply resumed at 14:50 hrs.
Sepset 01 | April | IDT 02 | HT panel surge arrester failure. | 6858 | 44681 | 0.50069 | 44681 | 0.77431 | 6.5667 | IDT 02 is under shutdown due to block-2 HT panel surge arrester failure. | 3.32 | 0.43913 | 9998.4039 | Checking & testing work done & work in progress.
Sepset 01 | May | Inverter 02 | PDP pro fault | 3439 | 44682 | 0.46667 | 44682 | 0.46875 | 0.05 | Inverter Trip on PDP pro fault | 0.04 | 0.73011 | 100.4338 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 03 | PDP pro fault | 3458 | 44682 | 0.46667 | 44682 | 0.46875 | 0.05 | Inverter Trip on PDP pro fault | 0.04 | 0.73011 | 100.9887 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 06 | PDP pro fault | 3510 | 44682 | 0.46667 | 44682 | 0.46875 | 0.05 | Inverter Trip on PDP pro fault | 0.04 | 0.73011 | 102.5073 | Inverter auto restart automatically.
Sepset 01 | May | All Inverters | Grid failure | 27698 | 44684 | 0.62083 | 44684 | 0.62639 | 0.13333 | Inverter tripped on AC under voltage | 0.05 | 0.74895 | 1037.2156 | Inverter restored manually.
Sepset 01 | May | Inverter 01 | AC under voltage | 3478 | 44684 | 0.67708 | 44684 | 0.67778 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.74895 | 0 | Inverter auto restart automatically.
Sepset 01 | May | All Inverters | Grid failure | 27698 | 44687 | 0.33611 | 44687 | 0.33681 | 0.016667 | Inverter tripped on AC under voltage | 0.013 | 0.707 | 254.5711 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 08 | PDP pro fault | 3497 | 44687 | 0.33611 | 44687 | 0.34722 | 0.26667 | Inverter Trip on PDP pro fault | 0.11 | 0.707 | 271.9603 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 01 | AC under voltage | 3478 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70846 | 76.3846 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 04 | AC under voltage | 3400 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70846 | 74.6715 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 08 | AC under voltage | 3497 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70846 | 76.8019 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 01 | AC under voltage | 3478 | 44691 | 0.62083 | 44691 | 0.62153 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7145 | 24.8505 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 01 | AC under voltage | 3478 | 44700 | 0.32569 | 44700 | 0.32708 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.77543 | 26.9695 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 02 | PDP pro fault | 3439 | 44701 | 0.53542 | 44701 | 0.5375 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.75947 | 130.5903 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 03 | PDP pro fault | 3458 | 44701 | 0.53542 | 44701 | 0.5375 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.75947 | 131.3118 | Inverter auto restart automatically.
Sepset 01 | May | SCB.04.02 | String fault | 52 | 44703 | 0.50347 | 44703 | 0.78889 | 6.85 | SCB 2A2 string no 1,8,9,14 Modules electricaly damage. | 3.4 | 0.75149 | 132.864 | Fault rectification work in progrss.
Sepset 01 | May | Inverter 07 | Ground fault | 3439 | 44704 | 0.28472 | 44704 | 0.29514 | 0.25 | Inverter Trip on Ground fault | 0.04 | 0.74519 | 102.5085 | Inverter restored manually.
Sepset 01 | May | SCB.04.02 | String fault | 52 | 44704 | 0.23403 | 44704 | 0.77708 | 13.0333 | SCB 2A2 string no 1,8,9,14 Modules electrically damaged. | 7.44 | 0.74519 | 288.2996 | Fault rectification work in progrss.
Sepset 01 | May | SCB.05.03 | String fault | 13 | 44704 | 0.65625 | 44704 | 0.65833 | 0.05 | positive side Y-connector failure | 0.03 | 0.74519 | 0.29062 | Fault rectification work done.
Sepset 01 | May | SCB.04.02 | String fault | 13 | 44705 | 0.30486 | 44705 | 0.33333 | 0.68333 | SCB 2A2 string no 9 Modules electrically damaged. | 0.19 | 0.73124 | 1.8062 | Module Fault rectification work done & string power resumed at 8:00 hrs. .
Sepset 01 | May | SCB.04.02 | String fault | 39 | 44705 | 0.30486 | 44705 | 0.77708 | 11.3333 | SCB 2A2 string no 1,8,14 Modules electrically damaged. | 5.76 | 0.73124 | 164.2656 | Module Fault rectification work in progrss.
Sepset 01 | May | All Inverters | Grid failure | 27698 | 44705 | 0.62153 | 44705 | 0.62292 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.73124 | 202.5387 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 07 | Ground fault | 3439 | 44705 | 0.62639 | 44705 | 0.6625 | 0.86667 | Inverter Trip on Ground fault | 0.42 | 0.73124 | 1056.1874 | Inverter restored manually.
Sepset 01 | May | Inverter 08 | Ground fault | 3497 | 44705 | 0.62917 | 44705 | 0.64931 | 0.48333 | Inverter Trip on Ground fault | 0.26 | 0.73124 | 664.8574 | Inverter restored manually.
Sepset 01 | May | Inverter 01 | AC under voltage | 3478 | 44705 | 0.64375 | 44705 | 0.64444 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.73124 | 25.4325 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 05 | Ground fault | 3479 | 44705 | 0.65694 | 44705 | 0.67778 | 0.5 | Inverter Trip on Ground fault | 0.22 | 0.73124 | 559.6759 | Inverter restored manually.
Sepset 01 | May | SCB.04.02 | String fault | 39 | 44706 | 0.24097 | 44706 | 0.77708 | 12.8667 | SCB 2A2 string no 1,8,14 Modules electrically damaged. | 7.17 | 0.74603 | 208.6123 | Module Fault rectification work in progrss.
Sepset 01 | May | SCB.04.02 | String fault | 26 | 44707 | 0.24167 | 44707 | 0.77708 | 12.85 | SCB 2A2 string no 1,14 Modules electrically damaged. | 6.13 | 0.74656 | 118.9875 | Module Fault rectification work in progress.
Sepset 01 | May | SCB.04.02 | String fault | 13 | 44707 | 0.24167 | 44707 | 0.64583 | 9.7 | SCB 2A2 string no.08 Modules electrically damaged. | 5.63 | 0.74656 | 54.6411 | Module Fault rectification work done & string power resumed at 15:30 hrs. .
Sepset 01 | May | Inverter 02 | PDP pro fault | 3439 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.72809 | 125.1954 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 05 | PDP pro fault | 3479 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.72809 | 126.6516 | Inverter auto restart automatically.
Sepset 01 | May | Inverter 06 | PDP pro fault | 3510 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter Trip on PDP pro fault | 0.05 | 0.72809 | 127.7801 | Inverter auto restart automatically.
Sepset 01 | May | SCB.04.02 | String fault | 26 | 44708 | 0.225 | 44708 | 0.79028 | 13.5667 | SCB 2A2 string no 1,14 Modules electrically damaged. | 7.6 | 0.72809 | 143.871 | Module Fault rectification work done.
Sepset 01 | May | SCB.04.02 | String fault | 13 | 44709 | 0.24306 | 44709 | 0.51944 | 6.6333 | SCB 2A2 string no 1 Modules electrically damaged. | 4.06 | 0.73377 | 38.7281 | Module Fault rectification work done.
Sepset 01 | May | SCB.04.02 | String fault | 13 | 44709 | 0.24306 | 44709 | 0.79236 | 13.1833 | SCB 2A2 string no 14 Modules electrically damaged. | 7.46 | 0.73377 | 71.1605 | Module Fault rectification work done.
Sepset 01 | May | Inverter 08 | Ground fault | 3497 | 44709 | 0.24306 | 44709 | 0.25347 | 0.25 | Inverter Trip on Ground fault | 0.01 | 0.73377 | 25.6598 | Inverter restored manually.
Sepset 01 | May | SCB.04.02 | String fault | 13 | 44710 | 0.24167 | 44710 | 0.51111 | 6.4667 | SCB 2A2 string no 14 Modules electrically damaged. | 3.82 | 0.73358 | 36.4293 | Module Fault rectification work done.
Sepset 01 | May | SCB.03.19 | String fault | 13 | 44711 | 0.63194 | 44711 | 0.63889 | 0.16667 | Ground fault | 0.12 | 0.72174 | 1.1259 | string no-14 ground Fault rectification work done.
Sepset 01 | May | All Inverters | Grid failure | 27698 | 44712 | 0.57083 | 44712 | 0.57153 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.7278 | 0 | Inverter auto restart automatically.
Sepset 01 | June | SCB.08.03 | String fault | 13 | 44715 | 0.5 | 44730 | 0.47222 | 194.77 | SCB 2A3 string no 4 Modules electrically damaged. | 2.38 | 0.7738 | 433 | Module Fault rectification work done.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44722 | 0.39722 | 44722 | 0.40486 | 0.18333 | 33KV Transmission line trip from substation end. | 0.08 | 0.74245 | 1645.1605 | Grid supply resumed at 09:43 hrs.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44723 | 0.69375 | 44723 | 0.69583 | 0.05 | 33KV Transmission line trip from substation end. | 0.001 | 0.7407 | 20.516 | Grid supply resumed at 16:42 hrs.
Sepset 01 | June | Inverter 01 | AC under voltage | 3478 | 44724 | 0.64931 | 44724 | 0.65 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7738 | 26.9128 | Inverter auto restart automatically.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44724 | 0.71042 | 44724 | 0.71111 | 0.016667 | 33KV Transmission line trip from substation end. | 0.001 | 0.7738 | 21.4327 | Grid supply resumed at 17:04 hrs.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44727 | 0.52778 | 44727 | 0.52986 | 0.05 | 33kv grid supply failure from 132/33 kv substation end | 0.02 | 0.76896 | 425.9756 | Grid supply resumed at 12:43 hrs.
Sepset 01 | June | Inverter 07 | Ground fault | 3439 | 44730 | 0.61667 | 44730 | 0.64583 | 0.7 | Inverter Trip on GND fault | 0.006 | 0.79752 | 16.4561 | Inverter restored manually.
Sepset 01 | June | Inverter 08 | Ground fault | 3497 | 44730 | 0.61667 | 44730 | 0.65625 | 0.95 | Inverter Trip on GND fault | 0.008 | 0.79752 | 22.3115 | Inverter restored manually.
Sepset 01 | June | Inverter 08 | Ground fault | 3497 | 44731 | 0.36042 | 44731 | 0.3625 | 0.05 | Inverter Trip on GND fault | 0.01 | 0.80358 | 28.1013 | Inverter restored manually.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44732 | 0.31944 | 44732 | 0.50833 | 4.5333 | 33kv line manually shutdown from substation end for Sepset -2 cable rectification work. | 2.16 | 0.72603 | 43436.9092 | Grid supply resumed at 12:12 hrs.
Sepset 01 | June | All Inverters | Grid failure | 27698 | 44732 | 0.64514 | 44732 | 0.73542 | 2.1667 | 33kv line manually shutdown from substation end for Sepset -2 cable rectification work. | 0.76 | 0.72603 | 15283.3569 | Grid supply resumed at 17:39 hrs.
Sepset 01 | June | SCB.02.13 | String fault | 13 | 44733 | 0.62153 | 44733 | 0.625 | 0.083333 | positive side Y-connector failure | 0.03 | 0.80186 | 0.31272 | y-connector male replaced & rectification work done.
Sepset 01 | June | SCB.04.02 | String fault | 13 | 44742 | 0.46181 | 44742 | 0.46528 | 0.083333 | positive side Y-connector failure | 0.03 | 0.83979 | 0.32752 | y-connector male replaced & rectification work done.
Sepset 01 | June | SCB.04.02 | String fault | 13 | 44742 | 0.47153 | 44742 | 0.475 | 0.083333 | positive side Y-connector failure | 0.09 | 0.83979 | 0.98255 | y-connector male replaced & rectification work done.
Sepset 01 | July | SCB.08.11 | String fault | 39 | 44747 | 0.34722 | 44747 | 0.39583 | 1.1667 | Ground fault | 0.09 | 0.89352 | 3.1363 | MC4-connector male/ female, 6sqmm cable positive & negative replaced & rectification work done.
Sepset 01 | July | SCB.08.10 | String fault | 13 | 44747 | 0.33681 | 44747 | 0.34722 | 0.25 | Ground fault | 0 | 0.89352 | 0 | MC4-connector male/ female, 6sqmm cable positive & negative replaced & rectification work done.
Sepset 01 | July | Inverter 01 | AC under voltage | 3478 | 44749 | 0.57639 | 44749 | 0.57708 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.94441 | 32.8467 | Inverter auto restart automatically.
Sepset 01 | July | Inverter 08 | Ground fault | 3439 | 44750 | 0.70069 | 44750 | 0.71875 | 0.43333 | Inverter Trip on Ground fault | 0.01 | 0.79999 | 27.5115 | Inverter restored manually.
Sepset 01 | July | SCB.02.05 | String fault | 13 | 44751 | 0.43403 | 44751 | 0.44444 | 0.25 | Ground fault | 0.13 | 0.87299 | 1.4753 | string fault rectification work done.
Sepset 01 | July | Inverter 03 | Ground fault | 3458 | 44753 | 0.34028 | 44753 | 0.34375 | 0.083333 | Inverter Trip on Ground fault | 0.02 | 0.87079 | 60.2239 | Inverter restored manually.
Sepset 01 | July | Inverter 06 | Ground fault | 3510 | 44753 | 0.42014 | 44753 | 0.43056 | 0.25 | Inverter Trip on Ground fault | 0.11 | 0.87079 | 336.2123 | Inverter restored manually.
Sepset 01 | July | SCB.06.16 | String fault | 182 | 44753 | 0.43056 | 44753 | 0.45833 | 0.66667 | Ground fault | 0.26 | 0.87079 | 41.2058 | string fault rectification work done.
Sepset 01 | July | SCB.06.17 | String fault | 182 | 44753 | 0.43056 | 44753 | 0.45833 | 0.66667 | Ground fault | 0.26 | 0.87079 | 41.2058 | string fault rectification work done.
Sepset 01 | July | SCB.06.18 | String fault | 182 | 44753 | 0.43056 | 44753 | 0.45833 | 0.66667 | Ground fault | 0.26 | 0.87079 | 41.2058 | string fault rectification work done.
Sepset 01 | July | Inverter 03 | Ground fault | 3458 | 44760 | 0.30069 | 44760 | 0.30694 | 0.15 | Inverter Trip on Ground fault | 0.01 | 0.8005 | 27.6813 | Inverter restored manually.
Sepset 01 | August | Inverter 01 | AC under voltage | 3478 | 44777 | 0.55278 | 44777 | 0.55417 | 0.033333 | Inverter tripped on AC under voltage | 0 | 0.7629 | 0 | Inverter auto restart automatically.
Sepset 01 | August | Inverter 04 | Ground fault | 3400 | 44777 | 0.59444 | 44777 | 0.60417 | 0.23333 | Ground fault | 0.08 | 0.7629 | 207.5088 | Inverter restored manually.
Sepset 01 | August | SCB.04.02 | String fault | 13 | 44777 | 0.60347 | 44777 | 0.61111 | 0.18333 | Ground fault | 0.03 | 0.7629 | 0.29753 | Ground fault rectification work done.
Sepset 01 | August | SCB.04.12 | String fault | 13 | 44777 | 0.61458 | 44777 | 0.67153 | 1.3667 | Ground fault | 0.03 | 0.7629 | 0.29753 | Ground fault rectification work done.
Sepset 01 | August | Inverter 04 | Ground fault | 3400 | 44779 | 0.26875 | 44779 | 0.27361 | 0.11667 | Ground fault | 0.004 | 0.80638 | 10.9668 | Inverter restored manually.
Sepset 01 | August | Inverter 04 | Ground fault | 3400 | 44779 | 0.28264 | 44779 | 0.2875 | 0.11667 | Ground fault | 0.01 | 0.80638 | 27.417 | Inverter restored manually.
Sepset 01 | August | Inverter 03 | Ground fault | 3478 | 44779 | 0.63333 | 44779 | 0.64097 | 0.18333 | Ground fault | 0.02 | 0.80638 | 56.092 | Inverter restored manually.
Sepset 01 | August | Inverter 03 | Ground fault | 3478 | 44779 | 0.65139 | 44779 | 0.65278 | 0.033333 | Ground fault | 0.01 | 0.80638 | 28.046 | Inverter restored manually.
Sepset 01 | August | Inverter 03 | Ground fault | 3478 | 44779 | 0.66875 | 44779 | 0.67222 | 0.083333 | Ground fault | 0.03 | 0.80638 | 84.138 | Inverter restored manually.
Sepset 01 | August | All Inverters | Grid failure | 27698 | 44788 | 0.45625 | 44788 | 0.45694 | 0.016667 | Inverters tripped on AC under voltage | 0.004 | 0.7629 | 84.5232 | Inverters auto restart automatically.
Sepset 01 | August | All Inverters | Grid failure | 27698 | 44791 | 0.32708 | 44791 | 0.32778 | 0.016667 | Inverters tripped on AC under voltage | 0.01 | 0.79796 | 221.0178 | Inverters auto restart automatically.
Sepset 01 | August | Inverter 01 | AC under voltage | 3478 | 44795 | 0.36875 | 44795 | 0.36944 | 0.016667 | Inverter tripped on AC under voltage | 0.008 | 0.7629 | 21.2269 | Inverter auto restart automatically.
Sepset 01 | August | Inverter 08 | Ground fault | 3439 | 44799 | 0.40347 | 44799 | 0.40625 | 0.066667 | Inverter Tripped on Ground fault | 0.05 | 0.80582 | 138.5599 | Inverter restored manually.
Sepset 01 | August | All Inverters | Grid failure | 27698 | 44803 | 0.35694 | 44803 | 0.35764 | 0.016667 | Inverters tripped on AC under voltage | 0.01 | 0.7629 | 211.308 | Inverters auto restart automatically.
Sepset 01 | September | Inverter 01 | Module over temp. fault | 708.5 | 44807 | 0.47222 | 44807 | 0.47361 | 0.033333 | Inverter-1, unit-4 tripped on module over temp. fault | 0.05 | 0.77958 | 27.6165 | Inverter auto restart automatically.
Sepset 01 | September | All Inverters | Grid failure | 27698 | 44808 | 0.39375 | 44808 | 0.69167 | 7.15 | 33kv grid supply failure for 33KV cable end termination kit failure of Sepset-1 Overhead Line. | 0.6 | 0.7913 | 13150.4564 | Grid supply resumed at 16:36 hrs.
Sepset 01 | September | Inverter 01 | AC under voltage | 3478 | 44810 | 0.64931 | 44810 | 0.65139 | 0.05 | Inverter tripped on AC under voltage | 0.001 | 0.7913 | 2.7521 | Inverter auto restart automatically.
Sepset 01 | September | All Inverters | Grid failure | 27698 | 44811 | 0.65278 | 44811 | 0.65486 | 0.05 | Inverters tripped on AC under voltage | 0.001 | 0.7913 | 21.9174 | Inverters auto restart automatically.
Sepset 02 | April | Inverter 14 | PDP pro fault | 3392 | 44652 | 0.38542 | 44652 | 0.3875 | 0.05 | Inverter Trip on PDP pro fault | 0.03 | 0.72085 | 73.3541 | Inverter automaticaly restart.
Sepset 02 | April | Inverter 14 | L over temp. fault | 716.56594629108 | 44652 | 0.25347 | 44653 | 0.76944 | 24.8 | Inverter no-14, unit-4 in shut down due to reactor bus fault. | 7.1 | 0.72085 | 7149 | Inverter manually start and Unit no-4 kept in off condition & other three units is in working condition as per sungrow engineer instructions.
Sepset 02 | April | Inverter 14 | Current leakage protection fault | 908.8 | 44655 | 0.47361 | 44655 | 0.4875 | 0.33333 | unit no-1 tripped on current leakage protection fault | 0.29 | 0.7351 | 193.738 | Inverter manually restored.
Sepset 02 | April | SCB.13.07 | String fault | 179.2 | 44656 | 0.50139 | 44656 | 0.61597 | 2.75 | Inverter side scb-1C2 dc breaker tripped | 2.48 | 0.73093 | 324.8358 | Inverter side and SCB-1C2 voltage checked. SCB manually restored.
Sepset 02 | April | SCB.15.01 | String fault | 12.8 | 44658 | 0.29167 | 44658 | 0.30556 | 0.33333 | Ground fault | 0.04 | 0.76041 | 0.38933 | Positive & Negative 6 sq.mm. DC cable and Positive & Negative MC4 connectors replaced and ground fault rectification work done.
Sepset 02 | April | SCB.13.09 | String fault | 12.8 | 44665 | 0.375 | 44665 | 0.3875 | 0.3 | Ground fault | 0.17 | 0.72252 | 1.5722 | Positive & Negative 6 sq.mm. DC cable and Positive & Negative MC4 connectors replaced and ground fault rectification work done.
Sepset 02 | April | Inverter 09 | AC under voltage | 3598 | 44666 | 0.68194 | 44666 | 0.68264 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 25.1279 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 10 | AC under voltage | 3412 | 44666 | 0.68194 | 44666 | 0.68264 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 23.8289 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 11 | AC under voltage | 3549 | 44666 | 0.68194 | 44666 | 0.68264 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 24.7857 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | AC under voltage | 3471 | 44666 | 0.68194 | 44666 | 0.68264 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 24.2409 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 09 | AC under voltage | 3598 | 44666 | 0.70139 | 44666 | 0.70208 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 25.1279 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 10 | AC under voltage | 3412 | 44666 | 0.70139 | 44666 | 0.70208 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 23.8289 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 11 | AC under voltage | 3549 | 44666 | 0.70139 | 44666 | 0.70208 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 24.7857 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | AC under voltage | 3471 | 44666 | 0.70139 | 44666 | 0.70208 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.69839 | 24.2409 | Inverter auto restart automatically.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44670 | 0.59236 | 44670 | 0.60625 | 0.33333 | Inverter tripped on AC under voltage | 0.28 | 0.68886 | 5349.7388 | Inverter manually restored.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44671 | 0.59792 | 44671 | 0.60833 | 0.25 | Inverter tripped on AC under voltage | 0.21 | 0.69745 | 4062.3416 | Inverter manually restored.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44671 | 0.67778 | 44671 | 0.68819 | 0.25 | Inverter tripped on AC under voltage | 0.1 | 0.69745 | 1934.4484 | Inverter manually restored.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44671 | 0.71458 | 44671 | 0.72569 | 0.26667 | Inverter tripped on AC under voltage | 0.05 | 0.69745 | 967.2242 | Inverter manually restored.
Sepset 02 | April | Inverter 09 | AC under voltage | 3598 | 44674 | 0.35486 | 44674 | 0.35556 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71205 | 25.6196 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 10 | AC under voltage | 3412 | 44674 | 0.35486 | 44674 | 0.35556 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71205 | 24.2952 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 11 | AC under voltage | 3549 | 44674 | 0.35486 | 44674 | 0.35556 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71205 | 25.2707 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | AC under voltage | 3471 | 44674 | 0.35486 | 44674 | 0.35556 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71205 | 24.7153 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | PDP pro fault | 3471 | 44675 | 0.42986 | 44675 | 0.43194 | 0.05 | Inverter Trip on PDP pro fault | 0.06 | 0.72206 | 150.3772 | Inverter automaticaly restart.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44676 | 0.30556 | 44676 | 0.68264 | 9.05 | 33kv grid supply failure from 132/33 kv substation end . | 7.16 | 0.66048 | 131164.6145 | Grid supply resumed at 16:23 hrs & all inverters power limit set at 80 %
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44677 | 0.60208 | 44677 | 0.6125 | 0.25 | 33kv grid supply failure from 132/33 kv substation end | 0.21 | 0.7212 | 4200.6727 | Grid supply restored at 14:42 hrs. & all inverters power limit set at 80 %
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44678 | 0.60347 | 44678 | 0.61319 | 0.23333 | Inverter tripped on AC under voltage | 0.2 | 0.69699 | 3866.368 | Inverter manually restored.
Sepset 02 | April | All Inverters | Grid failure | 27736 | 44679 | 0.56806 | 44679 | 0.57361 | 0.13333 | Inverter tripped on AC under voltage | 0.13 | 0.71063 | 2562.3175 | Inverter manually restored.
Sepset 02 | April | SCB.12.09 | String fault | 13 | 44679 | 0.46875 | 44679 | 0.48056 | 0.28333 | Y-connector failure | 0.29 | 0.71063 | 2.6791 | y-connector maale, MC4- connector mele replaced, rectification work done.
Sepset 02 | April | Inverter 09 | AC under voltage | 3598 | 44680 | 0.63125 | 44680 | 0.63194 | 0.016667 | Inverter tripped on AC under voltage | 0.02 | 0.71222 | 51.2516 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 10 | AC under voltage | 3412 | 44680 | 0.63125 | 44680 | 0.63194 | 0.016667 | Inverter tripped on AC under voltage | 0.02 | 0.71222 | 48.6021 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 11 | AC under voltage | 3549 | 44680 | 0.63125 | 44680 | 0.63194 | 0.016667 | Inverter tripped on AC under voltage | 0.02 | 0.71222 | 50.5536 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | AC under voltage | 3471 | 44680 | 0.63125 | 44680 | 0.63194 | 0.016667 | Inverter tripped on AC under voltage | 0.02 | 0.71222 | 49.4426 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | Soft start fault | 3471 | 44681 | 0.47292 | 44681 | 0.49028 | 0.41667 | Inverter tripped on soft start fault | 0.4 | 0.68711 | 953.9878 | Inverter manually restored.
Sepset 02 | April | Inverter 09 | PDP pro fault | 3598 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 123.6116 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 10 | PDP pro fault | 3412 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 117.2215 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 11 | PDP pro fault | 3549 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 121.9282 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 12 | PDP pro fault | 3471 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 119.2485 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 13 | PDP pro fault | 3555 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 122.1344 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 15 | PDP pro fault | 3379 | 44681 | 0.50069 | 44681 | 0.50278 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.68711 | 116.0878 | Inverter auto restart automatically.
Sepset 02 | April | Inverter 16 | Fan fault | 3379 | 44681 | 0.50278 | 44681 | 0.51111 | 0.2 | Inverter tripped on fan fault | 0.19 | 0.68711 | 441.1335 | Inverter manually restored.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44682 | 0.46667 | 44682 | 0.46875 | 0.05 | Inverter tripped on PDP pro fault | 0.04 | 0.72928 | 104.9573 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 15 | PDP pro fault | 3379 | 44682 | 0.46667 | 44682 | 0.46875 | 0.05 | Inverter tripped on PDP pro fault | 0.04 | 0.72928 | 98.5689 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44682 | 0.56181 | 44682 | 0.56389 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.72928 | 131.1967 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | PDP pro fault | 3549 | 44682 | 0.56181 | 44682 | 0.56389 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.72928 | 129.4099 | Inverter auto restart automatically.
Sepset 02 | May | All Inverters | Grid failure | 27736 | 44684 | 0.56806 | 44684 | 0.57361 | 0.13333 | Inverter tripped on AC under voltage | 0.05 | 0.75006 | 1040.1798 | Inverter manually restored.
Sepset 02 | May | Inverter 09 | AC under voltage | 3598 | 44684 | 0.67708 | 44684 | 0.67778 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.75006 | 0 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | AC under voltage | 3412 | 44684 | 0.67708 | 44684 | 0.67778 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.75006 | 0 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | AC under voltage | 3549 | 44684 | 0.67708 | 44684 | 0.67778 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.75006 | 0 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | AC under voltage | 3471 | 44684 | 0.67708 | 44684 | 0.67778 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.75006 | 0 | Inverter auto restart automatically.
Sepset 02 | May | SCB.13.17 | String fault | 13 | 44684 | 0.63194 | 44684 | 0.6375 | 0.13333 | Y-connector failure | 0.03 | 0.75006 | 0.29252 | y-connector maale, MC4- connector mele replaced, rectification work done.
Sepset 02 | May | SCB.16.17 | String fault | 12.8 | 44685 | 0.63194 | 44685 | 0.64028 | 0.2 | Y-connector failure | 0.13 | 0.72266 | 1.2025 | y-connector maale, MC4- connector male replaced, rectification work done.
Sepset 02 | May | Inverter 09 | L over temp. fault | 3598 | 44686 | 0.58472 | 44686 | 0.58889 | 0.1 | Inverter tripped on L-over Temp fault | 0.09 | 0.70671 | 228.8464 | Inverter manually restored.
Sepset 02 | May | All Inverters | Grid failure | 27736 | 44687 | 0.33611 | 44687 | 0.33681 | 0.016667 | Inverter tripped on AC under voltage | 0.013 | 0.70048 | 252.5707 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | AC under voltage | 3598 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70231 | 78.334 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | AC under voltage | 3412 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70231 | 74.2845 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | AC under voltage | 3549 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70231 | 77.2672 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | AC under voltage | 3471 | 44689 | 0.48194 | 44689 | 0.48264 | 0.016667 | Inverter tripped on AC under voltage | 0.031 | 0.70231 | 75.569 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44691 | 0.45694 | 44691 | 0.45972 | 0.066667 | Inverter tripped on PDP pro fault | 0.06 | 0.71134 | 153.564 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | PDP pro fault | 3412 | 44691 | 0.45694 | 44691 | 0.45972 | 0.066667 | Inverter tripped on PDP pro fault | 0.06 | 0.71134 | 145.6255 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | PDP pro fault | 3549 | 44691 | 0.45694 | 44691 | 0.45972 | 0.066667 | Inverter tripped on PDP pro fault | 0.06 | 0.71134 | 151.4727 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 13 | PDP pro fault | 3555 | 44691 | 0.45694 | 44691 | 0.45972 | 0.066667 | Inverter tripped on PDP pro fault | 0.06 | 0.71134 | 151.7288 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | AC under voltage | 3598 | 44691 | 0.62083 | 44691 | 0.62153 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71134 | 25.594 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | AC under voltage | 3412 | 44691 | 0.62083 | 44691 | 0.62153 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71134 | 24.2709 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | AC under voltage | 3549 | 44691 | 0.62083 | 44691 | 0.62153 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71134 | 25.2454 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | AC under voltage | 3471 | 44691 | 0.62083 | 44691 | 0.62153 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.71134 | 24.6906 | Inverter auto restart automatically.
Sepset 02 | May | SCB.09.08 | String fault | 12.8 | 44696 | 0.44306 | 44696 | 0.45139 | 0.2 | Ground fault | 0.16 | 0.726 | 1.4869 | negative 6 sq. mm cable , -ve & +ve MC4 connector replaced, rectification work done.
Sepset 02 | May | SCB.10.06 | String fault | 12.8 | 44696 | 0.63333 | 44696 | 0.63889 | 0.13333 | Y-connector failure | 0.07 | 0.726 | 0.6505 | y-connector male, replaced & rectification work done.
Sepset 02 | May | Inverter 09 | L over temp. fault | 3598 | 44698 | 0.52708 | 44698 | 0.53056 | 0.083333 | Inverter tripped on L-over Temp fault | 0.09 | 0.7323 | 237.1324 | Inverter manually restored.
Sepset 02 | May | SCB.13.09 | String fault | 12.8 | 44698 | 0.45139 | 44698 | 0.4625 | 0.26667 | Y-connector failure | 0.26 | 0.7323 | 2.4371 | Positive MC4 connector & Positive Y-Connector replaced, rectification work done.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44699 | 0.48611 | 44699 | 0.48819 | 0.05 | Inverter tripped on PDP pro fault | 0.04 | 0.73351 | 105.5668 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | PDP pro fault | 3549 | 44699 | 0.48611 | 44699 | 0.48819 | 0.05 | Inverter tripped on PDP pro fault | 0.04 | 0.73351 | 104.1292 | Inverter auto restart automatically.
Sepset 02 | May | SCB.14.16 | String fault | 12.8 | 44699 | 0.45 | 44699 | 0.46319 | 0.31667 | Y-connector failure | 0.27 | 0.73351 | 2.535 | y-connector male replaced & rectification work done.
Sepset 02 | May | Inverter 09 | AC under voltage | 3598 | 44700 | 0.32569 | 44700 | 0.32708 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.78052 | 28.0833 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | AC under voltage | 3412 | 44700 | 0.32569 | 44700 | 0.32708 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.78052 | 26.6315 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | AC under voltage | 3549 | 44700 | 0.32569 | 44700 | 0.32708 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.78052 | 27.7008 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | AC under voltage | 3471 | 44700 | 0.32569 | 44700 | 0.32708 | 0.033333 | Inverter tripped on AC under voltage | 0.01 | 0.78052 | 27.092 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44700 | 0.44167 | 44700 | 0.44375 | 0.05 | Inverter tripped on PDP pro fault | 0.04 | 0.78052 | 112.333 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44700 | 0.51111 | 44700 | 0.51319 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.78052 | 140.4163 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | PDP pro fault | 3549 | 44701 | 0.53542 | 44701 | 0.5375 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.7632 | 135.4291 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | PDP pro fault | 3471 | 44701 | 0.53542 | 44701 | 0.5375 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.7632 | 132.4527 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 09 | AC under voltage | 3598 | 44705 | 0.64375 | 44705 | 0.64444 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.74217 | 26.7032 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | AC under voltage | 3412 | 44705 | 0.64375 | 44705 | 0.64444 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.74217 | 25.3227 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | AC under voltage | 3549 | 44705 | 0.64375 | 44705 | 0.64444 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.74217 | 26.3395 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | AC under voltage | 3471 | 44705 | 0.64375 | 44705 | 0.64444 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.74217 | 25.7606 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 10 | Ground fault | 3412 | 44705 | 0.64583 | 44705 | 0.65278 | 0.16667 | Inverter tripped on ground fault | 0.09 | 0.74217 | 227.9047 | Inverter manually restored.
Sepset 02 | May | Inverter 09 | PDP pro fault | 3598 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.73202 | 131.691 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 11 | PDP pro fault | 3549 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.73202 | 129.8975 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 12 | PDP pro fault | 3471 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.73202 | 127.0426 | Inverter auto restart automatically.
Sepset 02 | May | Inverter 15 | PDP pro fault | 3379 | 44708 | 0.54028 | 44708 | 0.54236 | 0.05 | Inverter tripped on PDP pro fault | 0.05 | 0.73202 | 123.6753 | Inverter auto restart automatically.
Sepset 02 | May | SCB.12.05 | String fault | 44.8 | 44709 | 0.50347 | 44709 | 0.54306 | 0.95 | Ground fault | 0.93 | 0.73807 | 30.751 | Positive MC4 connector, Positive , Negative cable & 30 amp fuse replaced and rectification work done.
Sepset 02 | May | SCB.12.18 | String fault | 12.8 | 44709 | 0.46875 | 44709 | 0.47917 | 0.25 | Y-connector failure | 0.24 | 0.73807 | 2.2674 | Positive MC4 connector & Positive Y-Connector replaced, rectification work done.
Sepset 02 | May | Inverter 16 | Ground fault | 3379 | 44711 | 0.27639 | 44711 | 0.28611 | 0.23333 | Inverter tripped on ground fault | 0.03 | 0.72288 | 73.2778 | Inverter manually restored.
Sepset 02 | May | All Inverters | Grid failure | 27736 | 44712 | 0.57083 | 44712 | 0.57153 | 0.016667 | Inverter tripped on AC under voltage | 0 | 0.74904 | 0 | Inverter auto restart automatically.
Sepset 02 | May | SCB.11.03 | String fault | 76.8 | 44712 | 0.43611 | 44712 | 0.48125 | 1.0833 | Ground fault | 0.96 | 0.74904 | 55.2255 | Positive, negative MC4 connector, Positive cable replaced and rectification work done.
Sepset 02 | May | SCB.12.07 | String fault | 13 | 44712 | 0.63194 | 44712 | 0.63472 | 0.066667 | Y-connector failure | 0.03 | 0.74904 | 0.29213 | y-connector male replaced & rectification work done.
Sepset 02 | June | SCB.15.10 | String fault | 12.8 | 44715 | 0.47222 | 44715 | 0.48958 | 0.41667 | Ground fault | 0.39 | 0.73543 | 3.6712 | Positive, negative MC4 connector, Positive, negative cable replaced and rectification work done.
Sepset 02 | June | SCB.10.01 | String fault | 12.8 | 44716 | 0.59722 | 44716 | 0.60069 | 0.083333 | Y-connector failure | 0.02 | 0.7738 | 0.19809 | y-connector male replaced & rectification work done.
Sepset 02 | June | SCB.10.03 | String fault | 12.8 | 44716 | 0.60486 | 44716 | 0.60833 | 0.083333 | Y-connector failure | 0.02 | 0.7738 | 0.19809 | y-connector male replaced & rectification work done.
Sepset 02 | June | SCB.10.15 | String fault | 12.8 | 44716 | 0.63194 | 44716 | 0.63542 | 0.083333 | Y-connector failure | 0.03 | 0.7738 | 0.29714 | y-connector male replaced & rectification work done.
Sepset 02 | June | All Inverters | Grid failure | 27737 | 44722 | 0.39722 | 44722 | 0.40486 | 0.18333 | 33KV Transmition line trip from substation end. | 0.08 | 0.7738 | 1717.0312 | Grid supply resumed at 09:43 hrs.
Sepset 02 | June | All Inverters | Grid failure | 27737 | 44723 | 0.69375 | 44723 | 0.69583 | 0.05 | 33KV Transmition line trip from substation end. | 0.001 | 0.7738 | 21.4629 | Grid supply resumed at 16:42 hrs.
Sepset 02 | June | Inverter 16 | AC under voltage | 3379 | 44723 | 0.69583 | 44723 | 0.71944 | 0.56667 | Inverter tripped on AC under voltage | 0.04 | 0.7738 | 104.5868 | Inverter manually restored.
Sepset 02 | June | Inverter 09 | AC under voltage | 3598 | 44724 | 0.64931 | 44724 | 0.65 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7738 | 27.8413 | Inverter auto restart automatically.
Sepset 02 | June | Inverter 10 | AC under voltage | 3412 | 44724 | 0.64931 | 44724 | 0.65 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7738 | 26.4021 | Inverter auto restart automatically.
Sepset 02 | June | Inverter 11 | AC under voltage | 3549 | 44724 | 0.64931 | 44724 | 0.65 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7738 | 27.4622 | Inverter auto restart automatically.
Sepset 02 | June | Inverter 12 | AC under voltage | 3471 | 44724 | 0.64931 | 44724 | 0.65 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.7738 | 26.8586 | Inverter auto restart automatically.
Sepset 02 | June | All Inverters | Grid failure | 27737 | 44724 | 0.71042 | 44724 | 0.71111 | 0.016667 | 33KV Transmition line trip from substation end. | 0.001 | 0.7738 | 21.4629 | Grid supply resumed at 17:04 hrs.
Sepset 02 | June | Inverter 09 | Ground fault | 3598 | 44724 | 0.71667 | 44724 | 0.73333 | 0.4 | Inverter tripped on Ground fault | 0.01 | 0.7738 | 27.8413 | Inverter manually restored.
Sepset 02 | June | Inverter 13 | Ground fault | 3555 | 44724 | 0.71806 | 44724 | 0.73611 | 0.43333 | Inverter tripped on Ground fault | 0.01 | 0.7738 | 27.5086 | Inverter manually restored.
Sepset 02 | June | Inverter 14 | Ground fault | 3392 | 44724 | 0.72083 | 44724 | 0.73681 | 0.38333 | Inverter tripped on Ground fault | 0.008 | 0.7738 | 20.9978 | Inverter manually restored.
Sepset 02 | June | All Inverters | Grid failure | 27736 | 44727 | 0.52778 | 44727 | 0.52986 | 0.05 | 33kv grid supply failure from 132/33 kv substation end | 0.02 | 0.7655 | 424.6357 | Grid supply restored at 12:43 hrs.
Sepset 02 | June | SCB.16.08 | String fault | 12.8 | 44729 | 0.39167 | 44729 | 0.39931 | 0.18333 | Ground fault | 0.05 | 0.7712 | 0.49357 | Positive, negative MC4 connector, Positive, negative cable replaced and rectification work done.
Sepset 02 | June | SCB.16.08 | String fault | 12.8 | 44729 | 0.40903 | 44729 | 0.41597 | 0.16667 | Ground fault | 0.06 | 0.7712 | 0.59228 | Positive, negative MC4 connector, Positive, cable replaced and rectification work done.
Sepset 02 | June | Inverter 09 | Ground fault | 3598 | 44730 | 0.61181 | 44730 | 0.63125 | 0.46667 | Inverter tripped on GND fault | 0.003 | 0.76868 | 8.2972 | Inverter manually restored.
Sepset 02 | June | Inverter 13 | Ground fault | 3555 | 44730 | 0.62569 | 44730 | 0.62917 | 0.083333 | Inverter tripped on GND fault | 0.0008 | 0.76868 | 2.1861 | Inverter manually restored.
Sepset 02 | June | Inverter 16 | Ground fault | 3379 | 44730 | 0.64236 | 44730 | 0.64444 | 0.05 | Inverter tripped on GND fault | 0.0006 | 0.76868 | 1.5584 | Inverter manually restored.
Sepset 02 | June | All Inverters | Grid failure | 27737 | 44731 | 0.29167 | 44731 | 0.78819 | 11.9167 | 33KV Transmition line trip from substation end. | 1.19 | 0.7738 | 101305 | LA failure from substation end.
Sepset 02 | June | All Inverters | Grid failure | 27737 | 44732 | 0.23958 | 44732 | 0.73542 | 11.9 | 33KV Transmition line trip from substation end. | 5.56 | 0.7738 | 119333.6717 | Rectification work done.
Sepset 02 | June | SCB.09.11 | String fault | 12.8 | 44733 | 0.4375 | 44733 | 0.44444 | 0.16667 | Y-connector failure | 0.14 | 0.7738 | 1.3866 | y-connector male replaced & rectification work done.
Sepset 02 | June | IDT 06 | VCB breaker failure | 7020 | 44736 | 0.375 | 44736 | 0.78542 | 9.85 | Block-2 HT PANEL 33 KV VCB breaker failure | 4.57 | 0.7738 | 24824.5873 | Fault rectification work in progress.
Sepset 02 | June | IDT 05 | VCB breaker failure | 7010 | 44736 | 0.375 | 44736 | 0.43403 | 1.4167 | HT PANEL 33 KV VCB breaker tripped due to Block-2 HT PANEL 33 KV VCB breaker failure. | 0.98 | 0.7738 | 5315.8512 | HT panel manually restored.
Sepset 02 | June | IDT 07 | VCB breaker failure | 6947 | 44736 | 0.375 | 44736 | 0.43403 | 1.4167 | HT PANEL 33 KV VCB breaker tripped due to Block-2 HT PANEL 33 KV VCB breaker failure. | 0.98 | 0.7738 | 5268.0768 | HT panel manually restored.
Sepset 02 | June | IDT 08 | VCB breaker failure | 6758 | 44736 | 0.375 | 44736 | 0.43403 | 1.4167 | HT PANEL 33 KV VCB breaker tripped due to Block-2 HT PANEL 33 KV VCB breaker failure. | 0.98 | 0.7738 | 5124.7536 | HT panel manually restored.
Sepset 02 | June | IDT 06 | VCB breaker failure | 7020 | 44737 | 0.23264 | 44737 | 0.68333 | 10.8167 | Block-2 HT PANEL 33 KV VCB breaker failure | 6.24 | 0.7738 | 33896.1542 | Fault rectification work done.
Sepset 02 | June | Inverter 11 | Ground fault | 3549 | 44742 | 0.27778 | 44742 | 0.28333 | 0.13333 | Inverter tripped on ground fault | 0.01 | 0.7738 | 27.4622 | Inverter manually restored.
Sepset 02 | June | Inverter 12 | Ground fault | 3471 | 44742 | 0.27222 | 44742 | 0.28958 | 0.41667 | Inverter tripped on ground fault | 0.02 | 0.7738 | 53.7172 | Inverter manually restored.
Sepset 02 | June | Inverter 13 | Ground fault | 3555 | 44742 | 0.29306 | 44742 | 0.29653 | 0.083333 | Inverter tripped on ground fault | 0.01 | 0.7738 | 27.5086 | Inverter manually restored.
Sepset 02 | June | Inverter 16 | Ground fault | 3379 | 44742 | 0.26389 | 44742 | 0.26736 | 0.083333 | Inverter tripped on ground fault | 0.0004 | 0.7738 | 1.0459 | Inverter manually restored.
Sepset 02 | June | SCB.13.12 | String fault | 25.6 | 44742 | 0.42708 | 44742 | 0.44097 | 0.33333 | Ground fault | 0.25 | 0.7738 | 4.9523 | Positive y-connector male replaced, negative MC4 connector, and rectification work done.
Sepset 02 | June | SCB.16.08 | String fault | 25.6 | 44742 | 0.45833 | 44742 | 0.47222 | 0.33333 | Ground fault | 0.19 | 0.7738 | 3.7638 | y-connector male replaced & rectification work done.
Sepset 02 | July | SCB.16.12 | String fault | 25.6 | 44746 | 0.48472 | 44746 | 0.51528 | 0.73333 | Ground fault | 0.19 | 0.8005 | 3.8936 | String ground fault rectification work done.
Sepset 02 | July | SCB.16.14 | String fault | 51.2 | 44747 | 0.38889 | 44747 | 0.42708 | 0.91667 | Y-connector ground fault | 0.17 | 0.8005 | 6.9676 | Positive y-connector male replaced, negative MC4 connector, and rectification work done.
Sepset 02 | July | SCB.16.12 | String fault | 12.8 | 44747 | 0.47222 | 44747 | 0.47986 | 0.18333 | Ground fault | 0.03 | 0.8005 | 0.30739 | MC4-connector male/ female, 6sqmm cable positive & negative replaced & rectification work done.
Sepset 02 | July | Inverter 09 | AC under voltage | 3598 | 44749 | 0.57639 | 44749 | 0.57708 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.8005 | 28.802 | Inverter auto restart automatically.
Sepset 02 | July | Inverter 10 | AC under voltage | 3412 | 44749 | 0.57639 | 44749 | 0.57708 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.8005 | 27.3131 | Inverter auto restart automatically.
Sepset 02 | July | Inverter 11 | AC under voltage | 3549 | 44749 | 0.57639 | 44749 | 0.57708 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.8005 | 28.4097 | Inverter auto restart automatically.
Sepset 02 | July | Inverter 12 | AC under voltage | 3471 | 44749 | 0.57639 | 44749 | 0.57708 | 0.016667 | Inverter tripped on AC under voltage | 0.01 | 0.8005 | 27.7854 | Inverter auto restart automatically.
Sepset 02 | July | SCB.12.10 | String fault | 25.6 | 44751 | 0.50694 | 44751 | 0.51944 | 0.3 | Y-connector failure | 0.17 | 0.8005 | 3.4838 | String ground fault rectification work done.
Sepset 02 | July | Inverter 10 | Ground fault | 3412 | 44754 | 0.32083 | 44754 | 0.33125 | 0.25 | Inverter tripped on ground fault | 0.029 | 0.8005 | 79.2079 | Inverter manually restored.
Sepset 02 | July | All Inverters | Grid failure | 27736 | 44756 | 0.68194 | 44756 | 0.69167 | 0.23333 | Inverter tripped on AC under voltage | 0.01 | 0.8005 | 222.0267 | Inverter auto restart automatically.
Sepset 02 | July | Inverter 11 | DSP comm. fault | 3549 | 44761 | 0.50556 | 44761 | 0.50903 | 0.083333 | Inverter tripped on DSP com fault | 0.01 | 0.8005 | 28.4097 | Inverter manually restored.
Sepset 02 | July | Inverter 11 | DSP comm. fault | 3549 | 44761 | 0.6375 | 44761 | 0.64097 | 0.083333 | Inverter tripped on DSP com fault in unit-4 | 0.02 | 0.8005 | 56.8195 | Inverter manually restored.
Sepset 02 | July | Inverter 12 | Ground fault | 3471 | 44763 | 0.56181 | 44763 | 0.56528 | 0.083333 | Inverter tripped on ground fault | 0.03 | 0.8005 | 83.3561 | Inverter manually restored.
Sepset 02 | August | Inverter 10 | Contactor fault | 883.2 | 44774 | 0.31111 | 44774 | 0.31458 | 0.083333 | Inverter-unit no-3 tripped on Contactor fault | 0.02 | 0.7629 | 13.4759 | Inverter manually restored.
Sepset 02 | August | Inverter 10 | Contactor fault | 883.2 | 44774 | 0.31806 | 44774 | 0.325 | 0.16667 | Inverter-unit no-3 tripped on Contactor fault | 0.03 | 0.7629 | 20.2138 | Inverter manually restored.
Sepset 02 | August | Inverter 09 | AC under voltage | 3598 | 44777 | 0.55278 | 44777 | 0.55417 | 0.033333 | Inverter tripped on AC under voltage | 0 | 0.7629 | 0 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 10 | AC under voltage | 3412 | 44777 | 0.55278 | 44777 | 0.55417 | 0.033333 | Inverter tripped on AC under voltage | 0 | 0.7629 | 0 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 11 | AC under voltage | 3549 | 44777 | 0.55278 | 44777 | 0.55417 | 0.033333 | Inverter tripped on AC under voltage | 0 | 0.7629 | 0 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 12 | AC under voltage | 3471 | 44777 | 0.55278 | 44777 | 0.55417 | 0.033333 | Inverter tripped on AC under voltage | 0 | 0.7629 | 0 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 14 | Ground fault | 3392 | 44777 | 0.55278 | 44777 | 0.59097 | 0.91667 | Inverter tripped on Ground fault | 0.02 | 0.7629 | 51.7551 | Inverter manually restored.
Sepset 02 | August | Inverter 15 | Ground fault | 3379 | 44777 | 0.69236 | 44777 | 0.70208 | 0.23333 | Inverter tripped on Ground fault | 0.06 | 0.7629 | 154.6703 | Inverter manually restored.
Sepset 02 | August | All Inverters | Grid failure | 27736 | 44788 | 0.45625 | 44788 | 0.45694 | 0.016667 | Inverters tripped on AC under voltage | 0.004 | 0.7629 | 84.6392 | Inverters auto restart automatically.
Sepset 02 | August | All Inverters | Grid failure | 27736 | 44791 | 0.32708 | 44791 | 0.32778 | 0.016667 | Inverters tripped on AC under voltage | 0.01 | 0.78113 | 216.6537 | Inverters auto restart automatically.
Sepset 02 | August | Inverter 09 | AC under voltage | 3598 | 44795 | 0.36875 | 44795 | 0.36944 | 0.016667 | Inverter tripped on AC under voltage | 0.008 | 0.7629 | 21.9593 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 10 | AC under voltage | 3412 | 44795 | 0.36875 | 44795 | 0.36944 | 0.016667 | Inverter tripped on AC under voltage | 0.008 | 0.7629 | 20.8241 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 11 | AC under voltage | 3549 | 44795 | 0.36875 | 44795 | 0.36944 | 0.016667 | Inverter tripped on AC under voltage | 0.008 | 0.7629 | 21.6603 | Inverter auto restart automatically.
Sepset 02 | August | Inverter 12 | AC under voltage | 3471 | 44795 | 0.36875 | 44795 | 0.36944 | 0.016667 | Inverter tripped on AC under voltage | 0.008 | 0.7629 | 21.1842 | Inverter auto restart automatically.
Sepset 02 | August | All Inverters | Grid failure | 27736 | 44803 | 0.35694 | 44803 | 0.35764 | 0.016667 | Inverters tripped on AC under voltage | 0.01 | 0.88283 | 244.8616 | Inverters auto restart automatically.
Sepset 02 | September | Inverter 13 | Module over temp. fault | 980.6 | 44807 | 0.50278 | 44807 | 0.50417 | 0.033333 | Inverter-13, unit-1 tripped on module over temp. fault | 0.05 | 0.78075 | 38.2803 | Inverter manually restored.
Sepset 02 | September | Inverter 13 | Module over temp. fault | 980.6 | 44807 | 0.54236 | 44807 | 0.54514 | 0.066667 | Inverter-13, unit-1 tripped on module over temp. fault | 0.08 | 0.78075 | 61.2485 | Inverter manually restored.
Sepset 02 | September | All Inverters | Grid failure | 27736 | 44808 | 0.39375 | 44808 | 0.39583 | 0.05 | Inverters tripped on AC under voltage | 0 | 0.781 | 0 | Inverters auto restart automatically.
Sepset 02 | September | Inverter 14 | Ground fault | 3392 | 44810 | 0.26667 | 44810 | 0.29444 | 0.66667 | Ground fault | 0.05 | 0.76582 | 129.8829 | Inverter manually restored.
Sepset 02 | September | Inverter 09 | AC under voltage | 3598 | 44810 | 0.64931 | 44810 | 0.65139 | 0.05 | Inverter tripped on AC under voltage | 0.001 | 0.76582 | 2.7554 | Inverter auto restart automatically.
Sepset 02 | September | Inverter 10 | AC under voltage | 3412 | 44810 | 0.64931 | 44810 | 0.65139 | 0.05 | Inverter tripped on AC under voltage | 0.001 | 0.76582 | 2.613 | Inverter auto restart automatically.
Sepset 02 | September | Inverter 11 | AC under voltage | 3549 | 44810 | 0.64931 | 44810 | 0.65139 | 0.05 | Inverter tripped on AC under voltage | 0.001 | 0.76582 | 2.7179 | Inverter auto restart automatically.
Sepset 02 | September | Inverter 12 | AC under voltage | 3471 | 44810 | 0.64931 | 44810 | 0.65139 | 0.05 | Inverter tripped on AC under voltage | 0.001 | 0.76582 | 2.6582 | Inverter auto restart automatically.
Sepset 02 | September | All Inverters | Grid failure | 27736 | 44811 | 0.65278 | 44811 | 0.65486 | 0.05 | Inverters tripped on AC under voltage | 0.001 | 0.81039 | 22.4771 | Inverters auto restart automatically.
Sepset 02 | September | Inverter 15 | Ground fault | 3379 | 44812 | 0.73889 | 44812 | 0.76736 | 0.68333 | Ground fault | 0.01 | 0.766 | 25.8831 | Inverter manually restored.
Sepset 02 | September | Inverter 16 | Contactor fault | 3379 | 44813 | 0.34028 | 44813 | 0.35208 | 0.28333 | Sepset-2 Block-4 Inverter 2 Unit-3 contactor fault. | 0.12 | 0.766 | 310.5977 | Inverter manually restored.
Sepset | April | All Inverters | Grid failure | 2064 | 44658 | 0.65556 | 44658 | 0.65903 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0 | 0.6682 | 0 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44659 | 0.56667 | 44659 | 0.57014 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.08 | 0.6682 | 110.3332 | Grid Resumed
Sepset | April | SCB.01.19 | String fault | 5.16 | 44663 | 0.43889 | 44663 | 0.44444 | 0.13333 | 01 No String was under fault because of 10A fuse failure. | 0.12 | 0.6682 | 0.41375 | Work Completed & String Restored At- 10:40 hrs.
Sepset | April | SCB.02.04 | String fault | 5.16 | 44663 | 0.46111 | 44663 | 0.46736 | 0.15 | 01 No String Manual Shutdown For New Module Instalation | 0.14 | 0.6682 | 0.48271 | Work Completed & String Restored At- 11:13 hrs.
Sepset | April | All Inverters | Grid failure | 2064 | 44666 | 0.68264 | 44666 | 0.68611 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.02 | 0.6682 | 27.5833 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44666 | 0.70139 | 44666 | 0.70417 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.02 | 0.6682 | 27.5833 | Grid Resumed
Sepset | April | SCB.01.15 | String fault | 5.16 | 44671 | 0.55903 | 44671 | 0.5625 | 0.083333 | 01 No String Manual Shutdown For New Module Instalation | 0.08 | 0.6682 | 0.27583 | Work Completed & String Restored At- 13:30 hrs.
Sepset | April | All Inverters | Grid failure | 2064 | 44676 | 0.30486 | 44676 | 0.30903 | 0.1 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.6682 | 41.3749 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44676 | 0.48889 | 44676 | 0.49236 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.1 | 0.6682 | 137.9165 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44676 | 0.67639 | 44676 | 0.67917 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.6682 | 41.3749 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44677 | 0.60139 | 44677 | 0.60486 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.08 | 0.6682 | 110.3332 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44680 | 0.63056 | 44680 | 0.63403 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.07 | 0.6682 | 96.5415 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44681 | 0.50069 | 44681 | 0.50347 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.08 | 0.6682 | 110.3332 | Grid Resumed
Sepset | April | All Inverters | Grid failure | 2064 | 44681 | 0.69236 | 44681 | 0.69514 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.01 | 0.6682 | 13.7916 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44683 | 0.72986 | 44683 | 0.73681 | 0.16667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.02 | 0.6701 | 27.6617 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44684 | 0.66181 | 44684 | 0.66458 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0 | 0.6228 | 0 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44684 | 0.67639 | 44684 | 0.68056 | 0.1 | 11KV Grid Fluctuation From 132/11KV GSS. | 0 | 0.6228 | 0 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44684 | 0.71181 | 44684 | 0.71597 | 0.1 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.01 | 0.6228 | 12.8546 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44687 | 0.33681 | 44687 | 0.34028 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.04 | 0.62616 | 51.6959 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44687 | 0.55556 | 44687 | 0.56597 | 0.25 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.24 | 0.62616 | 310.1754 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44691 | 0.57639 | 44691 | 0.57917 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.6412 | 39.7033 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44691 | 0.62083 | 44691 | 0.62431 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.07 | 0.6412 | 92.6409 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44700 | 0.23958 | 44700 | 0.4375 | 4.75 | 11KV Transmission line fault from due guarding wire broken because of heavy wind . | 1.86 | 0.60884 | 2337.3451 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44705 | 0.61111 | 44705 | 0.61389 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.62678 | 38.81 | Grid Resumed
Sepset | May | All Inverters | Grid failure | 2064 | 44705 | 0.62361 | 44705 | 0.65903 | 0.85 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.37 | 0.62678 | 478.6564 | Grid Resumed
Sepset | May | SCB.01.12 | String fault | 7.52 | 44706 | 0.45972 | 44706 | 0.46389 | 0.1 | 01 No String was under fault because of 10A fuse failure. | 0.1 | 0.62021 | 0.4664 | Fuse Replaced & String Restored At - 11:08 hrs
Sepset | May | SCB.01.14 | String fault | 7.52 | 44706 | 0.46944 | 44706 | 0.47292 | 0.083333 | 01 No String was under fault because of 10A fuse failure. | 0.09 | 0.62021 | 0.41976 | Fuse Replaced & String Restored At - 11:21 hrs
Sepset | May | SCB.01.17 | String fault | 7.52 | 44706 | 0.48194 | 44706 | 0.48542 | 0.083333 | 01 No String was under fault because of 10A fuse failure. | 0.09 | 0.62021 | 0.41976 | Fuse Replaced & String Restored At - 11:39 hrs
Sepset | May | SCB.01.18 | String fault | 7.52 | 44706 | 0.50139 | 44706 | 0.50486 | 0.083333 | 01 No String was under fault because of 10A fuse failure. | 0.09 | 0.62021 | 0.41976 | Fuse Replaced & String Restored At - 12:07 hrs
Sepset | May | All Inverters | Grid failure | 2064 | 44706 | 0.74861 | 44706 | 0.75764 | 0.21667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.02 | 0.62021 | 25.6023 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44721 | 0.45486 | 44721 | 0.45764 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.07 | 0.6607 | 95.4579 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44721 | 0.67014 | 44721 | 0.67361 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.05 | 0.6607 | 68.1842 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44722 | 0.39722 | 44722 | 0.4 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.64913 | 40.1942 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44724 | 0.65069 | 44724 | 0.65347 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.06 | 0.63076 | 78.1132 | Grid Resumed
Sepset | June | SCB.01.15 | String fault | 7.52 | 44726 | 0.34375 | 44726 | 0.44792 | 2.5 | SMU No 15 Due to AJB Side 01 No Diode Failure | 1.71 | 0.63048 | 8.1075 | Diode Replaced & String Restored At - 10:45 hrs
Sepset | June | All Inverters | Grid failure | 2064 | 44726 | 0.72361 | 44726 | 0.72639 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0 | 0.63048 | 0 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44727 | 0.52708 | 44727 | 0.53056 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.02 | 0.66264 | 27.3536 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44731 | 0.49097 | 44731 | 0.49444 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.64034 | 39.6499 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44732 | 0.23958 | 44732 | 0.4875 | 5.95 | 11KV Grid Supply Failed From 132/11 KV GSS. | 1.96 | 0.63545 | 2570.6825 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44732 | 0.50833 | 44732 | 0.51111 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.07 | 0.63545 | 91.8101 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44733 | 0.64861 | 44733 | 0.66111 | 0.3 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.04 | 0.66961 | 55.283 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44736 | 0.37708 | 44736 | 0.38056 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.04 | 0.6354 | 52.459 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44736 | 0.53889 | 44736 | 0.54306 | 0.1 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.02 | 0.6354 | 26.2295 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44739 | 0.58125 | 44739 | 0.58472 | 0.083333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.03 | 0.65325 | 40.4494 | Grid Resumed
Sepset | June | All Inverters | Grid failure | 2064 | 44741 | 0.47639 | 44741 | 0.58542 | 2.6167 | 11KV Grid Supply Failed From 132/11 KV GSS. | 1.58 | 0.66907 | 2181.9048 | Grid Resumed
Sepset | July | All Inverters | Grid failure | 2064 | 44757 | 0.72569 | 44757 | 0.72778 | 0.05 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.01 | 0.77169 | 15.9276 | Grid Resumed
Sepset | July | All Inverters | Grid failure | 2064 | 44771 | 0.27431 | 44771 | 0.32569 | 1.2333 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.2 | 0.7241 | 298.9091 | 11KV Grid Supply Failed From 132/11 KV GSS.
Sepset | August | All Inverters | Grid failure | 2064 | 44781 | 0.38542 | 44781 | 0.38819 | 0.066667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.01 | 0.74208 | 15.3165 | Grid Resumed
Sepset | August | All Inverters | Grid failure | 2064 | 44785 | 0.64375 | 44785 | 0.64861 | 0.11667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.08 | 0.76658 | 126.5778 | Grid Resumed
Sepset | August | Inverter 02 | Ground fault | 1032 | 44786 | 0.27083 | 44786 | 0.3125 | 1 | Inverter no 2 tripped on earth fault. Fault rectification done and inverter started | 0.05 | 0.72053 | 37.1795 | Fault Rectify & Inverter Started At : 07:30 hrs.
Sepset | August | Inverter 02 | Ground fault | 1032 | 44786 | 0.36111 | 44786 | 0.37847 | 0.41667 | Inverter no 2 tripped on earth fault. Fault rectification done and inverter started | 0.11 | 0.72053 | 81.7949 | Fault Rectify & Inverter Started At :09:05 hrs.
Sepset | August | All Inverters | Grid failure | 2064 | 44789 | 0.45903 | 44789 | 0.49167 | 0.78333 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.49 | 0.75116 | 759.6899 | Grid Resumed
Sepset | August | All Inverters | Grid failure | 2064 | 44795 | 0.45694 | 44795 | 0.4625 | 0.13333 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.03 | 0.7219 | 44.7 | Grid Resumed
Sepset | August | All Inverters | Grid failure | 2064 | 44797 | 0.54097 | 44797 | 0.54306 | 0.05 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.07 | 0.72674 | 105 | Grid Resumed
Sepset | August | All Inverters | Grid failure | 2064 | 44799 | 0.55694 | 44799 | 0.56806 | 0.26667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.04 | 0.72167 | 59.581 | Grid Resumed
Sepset | August | All Inverters | Grid failure | 2064 | 44803 | 0.46528 | 44803 | 0.48056 | 0.36667 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.14 | 0.70704 | 204.3077 | Grid Resumed
Sepset | September | All Inverters | Grid failure | 2064 | 44811 | 0.65139 | 44811 | 0.65694 | 0.13333 | 11KV Grid Fluctuation From 132/11KV GSS. | 0.01 | 0.69858 | 14.4186 | Grid Resumed
Sepset | September | All Inverters | Grid failure | 2064 | 44814 | 0.29722 | 44814 | 0.32153 | 0.58333 | 11KV Grid Supply Failed From 132/11 KV GSS. | 0.1 | 0.70205 | 144.9036 | Grid Resumed
Sepset | September | All Inverters | Grid failure | 2064 | 44814 | 0.53264 | 44814 | 0.75139 | 5.25 | 11KV Grid Supply Failed From 132/11 KV GSS. | 2.33 | 0.70205 | 3376.2534 | Grid Resumed
Sepset | September | All Inverters | Grid failure | 2064 | 44815 | 0.73056 | 44815 | 0.73333 | 0.066667 | 11KV Grid Fluctuation From 132/11KV GSS. | 0 | 0.6567 | 0 | Grid Resumed
Tandur | April | SCB.11.16 | String fault | 1.8 | 44657 | 0.26528 | 44657 | 0.4625 | 4.7333 | String no. 16, table no. 03 , substring no. 01 found 01 nos MC4 is melted. | 2.1503 | 0.79956 | 3.0948 | Found 01 nos module MC4 connector melted .Replaced the MC4 connector & connected to load .
Tandur | April | Inverter 21 | PU comm. fault | 2916.8 | 44658 | 0.57222 | 44658 | 0.59583 | 0.56667 | PU communication fault | 0.44832 | 0.79252 | 1036.3383 | Inv tripped under PU communication fault, discussed with service engineer checked charging resistence of M1 & M2 section and FO cable at module unit.
Tandur | April | Inverter 21 | PU comm. fault | 2916.8 | 44658 | 0.61181 | 44658 | 0.61944 | 0.18333 | PU communication fault | 0.13698 | 0.79252 | 316.6368 | Inv tripped under PU communication fault, reset the same an inverter started. Need to check IGBT FO cable arrangement after generation hours.
Tandur | April | Inverter 21 | PU comm. fault | 2916.8 | 44658 | 0.72361 | 44658 | 0.75903 | 0.85 | Inverter tripped on PU Communication error and over current fault. | 0.057859 | 0.79252 | 133.7484 | Checked the inveter - found 1250 amp AC fuse (all 3phase) failed in M2 section. As discussed with ABB service engineer, we isolated the inverter. Checked for M1&M2 section IGBTs, found M2 IGBT failure. Now inverter will run on M1 section with 60% load.
Tandur | April | Inverter 21 | IGBT failure in M2 section | 1458.4 | 44659 | 0.26319 | 44660 | 0.63403 | 20.93 | M2 section off due to IGBT failure | 10.9 | 0.78095 | 12776 | Charged the inverter with 50 % load due to M2 Section IGBT failure
Tandur | April | SCB.20.15 | String fault | 123.2 | 44670 | 0.25694 | 44670 | 0.75556 | 11.9667 | IPC melted and it is suspected water ingress to IPC | 6.1904 | 0.80673 | 615.2569 | Replaced melted IPC after genetration hours
Tandur | April | Inverter 22 | Insulation failure | 2934 | 44672 | 0.71181 | 44672 | 0.71736 | 0.13333 | Inverter tripped on insulation failure ,floating checked found healthy | 0.020342 | 0.79413 | 47.3971 | Checked parameter & reset the inveter
Tandur | April | Inverter 02 | Insulation failure | 2833.6 | 44680 | 0.69236 | 44680 | 0.70833 | 0.38333 | Due to drizziling | 0.067296 | 0.78992 | 150.6301 | Checked parameter & reset the Fault
Tandur | April | Inverter 13 | Insulation failure | 2826 | 44680 | 0.69236 | 44680 | 0.70764 | 0.36667 | Due to drizziling | 0.063283 | 0.78992 | 141.2678 | Checked parameter & reset the Fault
Tandur | April | Inverter 14 | Insulation failure | 2657.6 | 44680 | 0.69028 | 44680 | 0.70208 | 0.28333 | Due to drizziling | 0.056144 | 0.78992 | 117.8629 | Checked parameter & reset the Fault
Tandur | April | Inverter 17 | Insulation failure | 2718 | 44680 | 0.69514 | 44680 | 0.70417 | 0.21667 | Due to drizziling | 0.03504 | 0.78992 | 75.2311 | Checked parameter & reset the Fault
Tandur | May | Inverter 21 | Clipping loss | 230 | 44684 | 0.46181 | 44684 | 0.54514 | 2 | Inverter Clipping loss due to inverter high temp | 1.9 | 0.79006 | 345.2581 | During peak hours inverter clipping due to high temp
Tandur | May | Inverter 21 | Clipping loss | 135 | 44687 | 0.51042 | 44687 | 0.58056 | 1.6833 | Inverter Clipping loss due to inverter high temperature | 1.59 | 0.80058 | 171.8437 | ABB analysing the data, to trace the cause of increase in Temp.
Tandur | May | Inverter 21 | 48V SMPS power supply failure | 2916.8 | 44694 | 0.60972 | 44694 | 0.63472 | 0.6 | M1 section 48V SMPS power supply | 0.35843 | 0.81338 | 850.3688 | Replaced SMPS M1 section and inverter charged with full load, inverter working normal condition kept under observation.
Tandur | May | Inverter 21 | Clipping loss | 510 | 44695 | 0.52778 | 44695 | 0.53819 | 0.25 | Inverter Clipping loss due to inverter high temperature | 0.23878 | 0.80363 | 97.8635 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | May | Inverter 21 | Clipping loss | 345 | 44696 | 0.51042 | 44696 | 0.52431 | 0.33333 | Inverter Clipping loss due to inverter high temperature | 0.32538 | 0.82632 | 92.7601 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 21 | Clipping loss | 106 | 44697 | 0.47292 | 44697 | 0.58056 | 2.5833 | Inverter Clipping loss due to inverter high temperature | 2.4537 | 0.81349 | 211.5867 | Data sent to ABB for analysis purpose.
Tandur | May | All Inverters | Grid failure | 61398.695 | 44698 | 0.63819 | 44698 | 0.675 | 0.88333 | GSS Tandur 220KV, 100MVA trafo trip due to incoming supply fail from shankarapally . | 0.00453 | 0.82688 | 229.9863 | Discussed with AE,they charged at GSS breaker after plant end all feeders charged
Tandur | May | Inverter 15 | Insulation failure | 2736 | 44699 | 0.63403 | 44699 | 0.64722 | 0.31667 | Insulation failure | 0.006978 | 0.83259 | 15.8956 | Checked parameter & reset the inveter
Tandur | May | Inverter 17 | Insulation failure | 2718 | 44699 | 0.62014 | 44699 | 0.65 | 0.71667 | Insulation failure | 0.012154 | 0.83259 | 27.5042 | Checked parameter & reset the inveter
Tandur | May | Inverter 20 | Insulation failure | 2710.4 | 44699 | 0.65347 | 44699 | 0.66042 | 0.16667 | Insulation failure | 0.001733 | 0.83259 | 3.9108 | Checked parameter & reset the inveter
Tandur | May | Inverter 21 | Insulation failure | 2916.8 | 44699 | 0.63194 | 44699 | 0.64722 | 0.36667 | Insulation failure | 0.006884 | 0.83259 | 16.7178 | Checked floting voltage & charged the inveter
Tandur | May | Inverter 06 | Insulation failure | 2921.6 | 44700 | 0.52569 | 44700 | 0.53611 | 0.25 | Inverter tripped on insulation failure | 0.030012 | 0.8528 | 74.7754 | Checked all the parameter & found.good. charged the inverter
Tandur | May | Inverter 09 | Insulation failure | 2682 | 44700 | 0.53056 | 44700 | 0.53958 | 0.21667 | Inverter tripped on insulation failure | 0.024299 | 0.8528 | 55.5763 | Checked all the parameter & found.good. charged the inverter
Tandur | May | Inverter 15 | Insulation failure | 2736 | 44700 | 0.52153 | 44700 | 0.53472 | 0.31667 | Inverter tripped on insulation failure | 0.037452 | 0.8528 | 87.3864 | Checked all the parameter & found.good. charged the inverter
Tandur | May | Inverter 17 | Insulation failure | 2718 | 44700 | 0.51042 | 44700 | 0.55 | 0.95 | Insulation resistance below limit | 0.083394 | 0.8528 | 193.2987 | Checked in DC field and not found any abnormalities then charged the inverter
Tandur | May | Inverter 03 | Insulation failure | 2858.695 | 44700 | 0.51736 | 44700 | 0.60556 | 2.1167 | Inverter tripped on insulation failure due to string no 8,9&10 floating voltage abnormal | 0.44433 | 0.8528 | 1083.2242 | Observed abnormal floating value of string no 08,09 & 10 disconnect the string charged the inverter
Tandur | May | SCB.03.08 | String fault | 369.6 | 44700 | 0.60625 | 44700 | 0.76389 | 3.7833 | Observed string cables damaged | 0.82078 | 0.8528 | 258.7048 | Isolated the particular faulty strings and started the inverter, checked the faulty string and rectified the same.
Tandur | May | Inverter 21 | Clipping loss | 112 | 44703 | 0.49931 | 44703 | 0.575 | 1.8167 | Inverter Clipping loss due to inverter AMB temperature | 1.7478 | 0.82328 | 161.1574 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 21 | Clipping loss | 61 | 44704 | 0.50764 | 44704 | 0.56528 | 1.3833 | Inverter Clipping loss due to inverter AMB temperature | 1.3323 | 0.8217 | 66.7794 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 21 | Clipping loss | 95 | 44705 | 0.46181 | 44705 | 0.55417 | 2.2167 | Inverter Clipping loss due to inverter high temperature | 2.1192 | 0.81586 | 164.2508 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 21 | Clipping loss | 113 | 44706 | 0.51389 | 44706 | 0.53542 | 0.51667 | Inverter Clipping loss due to inverter high temperature | 0.47786 | 0.81452 | 43.9826 | Data sent to ABB for analysis purpose.
Tandur | May | All Inverters | Grid failure | 61398.695 | 44706 | 0.73889 | 44706 | 0.78958 | 1.2167 | Line tripped GSS end. | 0.027143 | 0.81452 | 1357.4285 | discussed with ADE, Cross checked GSS End equipment and line then charged.
Tandur | May | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44708 | 0.24653 | 44708 | 0.27292 | 0.63333 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.028404 | 0.82142 | 63.2389 | Reset the inverter and inverter started normally.
Tandur | May | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44708 | 0.33542 | 44708 | 0.3625 | 0.65 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.21542 | 0.82142 | 479.612 | Reset the inverter and inverter started normally.
Tandur | May | Inverter 21 | Clipping loss | 48 | 44709 | 0.5125 | 44709 | 0.55972 | 1.1333 | Inverter Clipping loss due to inverter AMB temperature | 1.2187 | 0.81436 | 47.638 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44710 | 0.28819 | 44710 | 0.3 | 0.28333 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.049768 | 0.8049 | 108.5732 | Reset the inverter and inverter started normally.
Tandur | May | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44710 | 0.37847 | 44710 | 0.39931 | 0.5 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.33708 | 0.8049 | 735.3654 | Reset the inverter and inverter started normally.
Tandur | May | Inverter 21 | Clipping loss | 128 | 44710 | 0.47569 | 44710 | 0.54097 | 1.5667 | Inverter Clipping loss due to inverter AMB temperature | 1.5065 | 0.8049 | 155.2078 | Data sent to ABB for analysis purpose.
Tandur | May | Inverter 21 | Clipping loss | 125 | 44711 | 0.49306 | 44711 | 0.54028 | 1.1333 | Inverter Clipping loss due to inverter high temperature | 1.0345 | 0.80814 | 104.5041 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | May | Inverter 14 | Insulation failure | 2657.6 | 44712 | 0.28472 | 44712 | 0.29167 | 0.16667 | Insulation resistance below limit | 0.0024125 | 0.82318 | 5.2778 | Checked parameter & reset the inveter
Tandur | June | Inverter 12 | Insulation failure | 2898 | 44713 | 0.26736 | 44713 | 0.27569 | 0.2 | Insulation failure | 0.017654 | 0.82784 | 42.3526 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 12 | Insulation failure | 2898 | 44714 | 0.44236 | 44714 | 0.44722 | 0.11667 | Insulation failure | 0.10518 | 0.82145 | 250.3787 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 21 | Clipping loss | 309 | 44717 | 0.52292 | 44717 | 0.57917 | 1.35 | Inverter clipping loss due to M1 section fan failure | 1.1456 | 0.79365 | 280.9484 | Fan connection removed and re-connected
Tandur | June | Inverter 21 | Clipping loss | 136 | 44719 | 0.50556 | 44719 | 0.60625 | 2.4167 | Inverter Clipping loss due to inverter high temperature | 2.0614 | 0.79328 | 222.4019 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 21 | Clipping loss | 61 | 44723 | 0.45694 | 44723 | 0.60972 | 3.6667 | Inverter Clipping loss due to inverter high temperature | 3.0245 | 0.80341 | 148.2227 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 22 | Clipping loss | 69 | 44723 | 0.45694 | 44723 | 0.60972 | 3.6667 | Inverter Clipping loss due to inverter high temperature | 3.0245 | 0.80341 | 167.6618 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 21 | Clipping loss | 68 | 44724 | 0.44583 | 44724 | 0.58611 | 3.3667 | Inverter Clipping loss due to inverter high temperature | 2.9372 | 0.79761 | 159.3072 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 22 | Clipping loss | 73 | 44724 | 0.44583 | 44724 | 0.58611 | 3.3667 | Inverter Clipping loss due to inverter high temperature | 2.9372 | 0.79761 | 171.021 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 21 | Clipping loss | 60 | 44725 | 0.44167 | 44725 | 0.60764 | 3.9833 | Inverter Clipping loss due to inverter high temperature | 3.3059 | 0.8022 | 159.1181 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 22 | Clipping loss | 66 | 44725 | 0.44167 | 44725 | 0.60764 | 3.9833 | Inverter Clipping loss due to inverter high temperature | 3.3059 | 0.8022 | 175.03 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | PTR 02 | Under freq. fault | 30774.8 | 44725 | 0.7 | 44725 | 0.71667 | 0.4 | Under Frequency fault | 0.11854 | 0.8022 | 2926.3656 | Checked the relay and reset the same, after found everything normal charged the transformer succesfully.
Tandur | June | Inverter 21 | Clipping loss | 63 | 44726 | 0.43056 | 44726 | 0.57014 | 3.35 | Inverter Clipping loss due to inverter high temperature | 2.8337 | 0.81543 | 145.5748 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 22 | Clipping loss | 71 | 44726 | 0.43056 | 44726 | 0.57014 | 3.35 | Inverter Clipping loss due to inverter high temperature | 2.8345 | 0.81543 | 164.1019 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 14 | Insulation failure | 2657.6 | 44726 | 0.52986 | 44726 | 0.53472 | 0.11667 | Insulation failure | 0.13743 | 0.81543 | 297.8218 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 21 | Clipping loss | 65 | 44727 | 0.48125 | 44727 | 0.60764 | 3.0333 | Inverter Clipping loss due to inverter high temperature | 2.4487 | 0.82408 | 131.1649 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 22 | Clipping loss | 69 | 44727 | 0.48125 | 44727 | 0.60764 | 3.0333 | Inverter Clipping loss due to inverter high temperature | 2.461 | 0.82408 | 139.9355 | in discussion with ABB, to trace the cause of increase in Temp.
Tandur | June | Inverter 21 | Insulation failure | 2916.8 | 44727 | 0.72222 | 44727 | 0.72639 | 0.1 | Insulation failure | 0.019628 | 0.82408 | 47.1795 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 21 | Clipping loss | 166 | 44728 | 0.42847 | 44728 | 0.56389 | 3.25 | Inverter Clipping | 3.024 | 0.81795 | 410.5969 | ABB R&D team working on it to reslove the issue
Tandur | June | Inverter 22 | Clipping loss | 216 | 44728 | 0.42847 | 44728 | 0.56389 | 3.25 | Inverter Clipping | 3.026 | 0.81795 | 534.6205 | ABB R&D team working on it to reslove the issue
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44728 | 0.60833 | 44728 | 0.62014 | 0.28333 | Insulation failure | 0.0193 | 0.81795 | 42.9066 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 02 | Insulation failure | 2833.6 | 44728 | 0.67708 | 44728 | 0.68889 | 0.28333 | Insulation failure | 0.011892 | 0.81795 | 27.5617 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 22 | Clipping loss | 49 | 44729 | 0.42361 | 44729 | 0.60208 | 4.2833 | Inverter Clipping loss due to inverter high temperature | 3.8292 | 0.81524 | 152.9656 | ABB in discussion with their R&D Team.
Tandur | June | Inverter 21 | IGBT failure in M2 section | 2916.8 | 44729 | 0.53125 | 44729 | 0.77847 | 5.92 | M2 section IGBT failure | 2.59 | 0.81524 | 3507 | Checked the inveter - found 1250 amp AC fuse (Y&B phase) failed in M2 section. As discussed with ABB service engineer, we isolated the inverter. Checked for M1&M2 section IGBTs, found M2 IGBT failure. Now inverter will run on M1 section with 60% load.
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44729 | 0.65694 | 44729 | 0.66806 | 0.26667 | Insulation failure | 0.034375 | 0.81524 | 76.1689 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44731 | 0.48403 | 44731 | 0.50208 | 0.43333 | Insulation failure | 0.14514 | 0.84188 | 332.1233 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44732 | 0.65 | 44732 | 0.66667 | 0.4 | Insulation failure | 0.15464 | 0.8049 | 338.3098 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44733 | 0.575 | 44733 | 0.60972 | 0.83333 | Inverter tripped on insulation failure due to string no 21&23 floating voltage abnormal | 0.0881 | 0.81137 | 194.2884 | All strings floating checked found string 21&23 floating abnormal ,isolate the those two strings and charge the inverter
Tandur | June | SCB.17.21 | String fault | 252 | 44733 | 0.61042 | 44733 | 0.74375 | 3.2 | String no -21,23 found floating abnormal | 0.43074 | 0.81137 | 88.0716 | string 21&23 checked the floating ,and observed minor damage modules and replaced the same
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44738 | 0.43125 | 44738 | 0.44167 | 0.25 | Inverter tripped on insulation failure due to rain fall | 0.15977 | 0.8049 | 349.5419 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44739 | 0.51042 | 44739 | 0.52917 | 0.45 | Inverter tripped on insulation failure due to rain fall | 0.13256 | 0.8049 | 290.0127 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 17 | Insulation failure | 2718 | 44739 | 0.54792 | 44739 | 0.56181 | 0.33333 | Inverter tripped on insulation failure due to rain fall | 0.10399 | 0.8049 | 227.4945 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 03 | Insulation failure | 2858.695 | 44741 | 0.32639 | 44741 | 0.34792 | 0.51667 | Inverter tripped on insulation failure due to drizzling | 0.10057 | 0.83891 | 241.1796 | Checked all the parameter & found.good. charged the inverter
Tandur | June | Inverter 21 | LCL filter issue | 2916.8 | 44742 | 0.53958 | 44743 | 0.46806 | 10.87 | Inverter tripped under BU difference fault due to M2 section LCL filter issue. | 4.58 | 0.83814 | 7554 | Checked the AC fuse and contractor also checked the 24V buffer module all found ok and reset the fault
Tandur | July | Inverter 05 | Insulation failure | 2657.6 | 44747 | 0.5875 | 44747 | 0.59653 | 0.21667 | Inverter tripped on insulation failure | 0.022114 | 0.8146 | 47.8747 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 06 | Insulation failure | 2921.6 | 44747 | 0.57986 | 44747 | 0.58681 | 0.16667 | Inverter tripped on insulation failure | 0.019553 | 0.8146 | 46.5346 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 07 | Insulation failure | 2587.2 | 44747 | 0.65139 | 44747 | 0.65903 | 0.18333 | Inverter tripped on insulation failure | 0.038264 | 0.8146 | 80.6417 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 12 | Insulation failure | 2898 | 44747 | 0.58125 | 44747 | 0.59444 | 0.31667 | Inverter tripped on insulation failure | 0.033219 | 0.8146 | 78.4197 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 13 | Insulation failure | 2826 | 44747 | 0.59444 | 44747 | 0.60278 | 0.2 | Inverter tripped on insulation failure | 0.022736 | 0.8146 | 52.3386 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 14 | Insulation failure | 2657.6 | 44747 | 0.55208 | 44747 | 0.55903 | 0.16667 | Inverter tripped on insulation failure | 0.14848 | 0.8146 | 321.4415 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 20 | Insulation failure | 2710.4 | 44747 | 0.55278 | 44747 | 0.56111 | 0.2 | Inverter tripped on insulation failure | 0.14485 | 0.8146 | 319.8068 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 21 | LCL filter issue | 2916.8 | 44748 | 0.26181 | 44749 | 0.77639 | 24.62 | Inverter tripped under BU difference fault due to M2 section LCL filter issue. | 5.27 | 0.8146 | 7132 | Checked the inveter - found 1250 amp AC fuse failed in M2 Section (Y&R phase) . As discussed with ABB service engineer, isolated the M2 section and inverter M1 section charhed with 60% load .
Tandur | July | Inverter 02 | Insulation failure | 2833.6 | 44750 | 0.74306 | 44750 | 0.75347 | 0.25 | Inverter tripped on insulation failure | 0.01218 | 0.8146 | 28.1155 | Checked all the parameter & found.good then charged the inverter
Tandur | July | Inverter 16 | Insulation failure | 2868.8 | 44750 | 0.75278 | 44750 | 0.76528 | 0.3 | Inverter tripped on insulation failure | 0.0080249 | 0.8146 | 18.7536 | Checked all the parameter & found good then charged the inverter
Tandur | July | Inverter 02 | Insulation failure | 2833.6 | 44751 | 0.65347 | 44751 | 0.66319 | 0.23333 | Inverter tripped on insulation failure | 0.035208 | 0.8146 | 81.2699 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 02 | Insulation failure | 2833.6 | 44751 | 0.70069 | 44751 | 0.70833 | 0.18333 | Inverter tripped on insulation failure | 0.017287 | 0.8146 | 39.902 | Checked all the parameter & found.good. charged the inverter
Tandur | July | Inverter 11 | Insulation failure | 3024 | 44751 | 0.46181 | 44751 | 0.46944 | 0.18333 | Inverter tripped on insulation failure | 0.014844 | 0.8146 | 36.5671 | Checked all the parameter & found.good. charged the inverter
Tandur | July | PTR 01 | Differential current fault | 30623.895 | 44752 | 0.31667 | 44752 | 0.4 | 2 | PTR-1 33KV side Y-Ph Epoxy insulator fail. | 0.13614 | 0.8146 | 3396.1416 | Replaced with spare supporting insuator and charged the PTR, after verifing IR,Ratio,Magnetic balance.
Tandur | July | Inverter 21 | LCL over temp. fault | 2916.8 | 44757 | 0.50556 | 44757 | 0.54514 | 0.95 | Inverter tripped on secondary over temp in M2 section LCL filter | 0.58988 | 0.85892 | 1477.8204 | Discussed with ABB service engineer, re started the inverter
Tandur | July | Inverter 21 | LCL over temp. fault | 2916.8 | 44757 | 0.58056 | 44757 | 0.77708 | 4.72 | Inverter tripped on secondary over temp in M2 section LCL filter | 1.53 | 0.85892 | 2489 | Discussed with ABB service engineer, interer changed the temperature sensor of M1 and M2 and charged the inverter.
Tandur | July | Inverter 09 | Insulation failure | 2682 | 44761 | 0.62708 | 44761 | 0.64236 | 0.36667 | insulation failure | 0.15968 | 0.85107 | 364.4715 | Checked all the parameter & restarted the inverter
Tandur | July | IDT 16 | IDT 16 tripped | 2869 | 44771 | 0.57639 | 44771 | 0.62153 | 1.0833 | Higher winding temperature | 0.59666 | 0.7995 | 1368.6052 | Checked the relay and reset, checked the LV bus-bar duct for higher temperature found all ok. After inspection transformer ideally charged for 10min. Now transformer healthy and Inverter charged.
Tandur | August | Inverter 05 | Insulation failure | 2657.6 | 44774 | 0.29444 | 44774 | 0.30278 | 0.2 | Inverter tripped on insulation failure | 0.032695 | 0.8146 | 70.7815 | Checked all the parameter & found.good. charged the inverter
Tandur | August | Inverter 05 | Insulation failure | 2657.6 | 44775 | 0.49306 | 44775 | 0.50278 | 0.23333 | Inverter tripped on insulation failure | 0.13274 | 0.8146 | 287.3694 | Checked all the parameter & found.good. charged the inverter
Tandur | August | Inverter 11 | Insulation failure | 3024 | 44777 | 0.54792 | 44777 | 0.55625 | 0.2 | Inverter tripped on insulation failure | 0.0084203 | 0.81318 | 20.706 | Checked all the parameter & found.good. charged the inverter
Tandur | August | Inverter 07 | Insulation failure | 2587.2 | 44777 | 0.59444 | 44777 | 0.60347 | 0.21667 | Inverter tripped on insulation failure | 0.049483 | 0.81318 | 104.1049 | Checked all the parameter & found.good. charged the inverter
Tandur | August | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44778 | 0.4625 | 44778 | 0.48333 | 0.5 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.33582 | 0.86545 | 787.7482 | IGBT Feedback cable checked and restarted.
Tandur | August | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44779 | 0.57361 | 44779 | 0.58264 | 0.21667 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.21868 | 0.8698 | 515.5275 | Reset the inverter and inverter started normally.
Tandur | August | Inverter 04 | Insulation failure | 2646 | 44781 | 0.31944 | 44781 | 0.33264 | 0.31667 | Inverter tripped on insulation failure . | 0.024183 | 0.8208 | 52.5212 | Checked all the parameter & restarted the inverter
Tandur | August | Inverter 11 | Insulation failure | 3024 | 44782 | 0.3625 | 44782 | 0.37222 | 0.23333 | Inverter tripped on insulation failure . | 0.043533 | 0.91952 | 121.0497 | Checked all the parameter & restarted the inverter
Tandur | August | Inverter 12 | Insulation failure | 2898 | 44782 | 0.29792 | 44782 | 0.30556 | 0.18333 | Inverter tripped on insulation failure . | 0.010672 | 0.91952 | 28.4383 | Checked all the parameter & restarted the inverter
Tandur | August | Inverter 21 | BU current difference fault | 2916.8 | 44783 | 0.51319 | 44783 | 0.52986 | 0.4 | Inverter tripped under BU difference fault | 0.28201 | 0.9054 | 744.7562 | as per service engineer instructions checked AC section fuses and SMPS voltage of both M1 & M2 sections. Found helthy, then charged the inverter.
Tandur | August | Inverter 21 | LCL filter issue | 2916.8 | 44784 | 0.46042 | 44787 | 0.76528 | 34.87 | Inverter tripped under BU difference fault | 6 | 0.85991 | 8306 | Checked the inveter - found LCL failed in M2 Section . As discussed with ABB service engineer, isolated the M2 section and inverter M1 section charhed with 60% load .
Tandur | August | Inverter 20 | Faulty temp. f/b from IGBT | 2710.4 | 44784 | 0.31111 | 44784 | 0.32708 | 0.38333 | Inverter-20 tripped on faulty temp feedback from IGBT | 0.048226 | 0.85991 | 112.3993 | Reset the inverter and inverter started normally.
Tandur | August | Inverter 06 | Insulation failure | 2921.6 | 44787 | 0.70486 | 44787 | 0.72083 | 0.38333 | Inverter tripped on insulation failure . | 0.026856 | 0.94818 | 74.3961 | Checked all the parameter & found.good. Charged the inverter
Tandur | August | CS 04 | HT panel tripped | 16991.2 | 44789 | 0.42083 | 44789 | 0.49861 | 1.8667 | CS -04 HT Panel (at TS) tripped under over-current fault. | 1.5782 | 0.76122 | 20412.5645 | Checked CS-4 all Incomers, found Block-10 Master Trip activated. Isolated the Block-10 and charged remaining blocks.
Tandur | August | Inverter 10 | HT panel tripped | 2657.6 | 44789 | 0.49931 | 44789 | 0.58819 | 2.1333 | CS -04 HT Panel (at TS) tripped under over-current fault. | 1.6755 | 0.76122 | 3389.473 | Block-10 HT panel inspection carried out ,observed flashover in B-phase epoxy bushing and arclyic sheet. Cleaned it properly and then charge the Block-10.
Tandur | August | Inverter 21 | LCL over temp. fault | 2916.8 | 44789 | 0.51319 | 44789 | 0.52222 | 0.21667 | Inverter tripped on over temp in LCL | 0.21641 | 0.76122 | 480.4902 | Discussed with ABB service engineer, checked all parameter reset the fault and charged the inverter.
Tandur | August | Inverter 14 | BU current difference fault | 2657.6 | 44798 | 0.63472 | 44798 | 0.65903 | 0.58333 | Inverter tripped under BU current difference fault | 0.41277 | 0.8111 | 889.7612 | Rph AC fuse failed in M2 Section . As discussed with ABB service engineer, isolated the M2 section and inverter M1 section charhed with 60% load .
Tandur | August | Inverter 14 | BU current difference fault | 1328.8 | 44798 | 0.65972 | 44798 | 0.69028 | 0.73333 | Inverter tripped under BU current difference fault | 0.20051 | 0.8111 | 216.1054 | M1 section in load.
Tandur | August | Inverter 21 | Clipping loss | 461 | 44798 | 0.40556 | 44798 | 0.44167 | 0.86667 | Inverter Clipping loss due to M1 Section Fan Failure | 0.71994 | 0.8111 | 269.1993 | Fan Replaced with spare.
Tandur | September | Inverter 12 | Insulation failure | 2898 | 44806 | 0.29444 | 44806 | 0.30069 | 0.15 | Inverter tripped on insulation failure . | 0.032169 | 0.81475 | 75.9556 | Checked all the parameter & found.good. Charged the inverter
Tandur | September | Inverter 08 | Insulation failure | 2808 | 44808 | 0.27986 | 44808 | 0.28819 | 0.2 | Inverter tripped on insulation failure . | 0.014705 | 0.87556 | 36.1531 | Checked all the parameter & found good. Charged the inverter
Tandur | September | Inverter 11 | IDT 11 tripped | 3024 | 44812 | 0.44583 | 44812 | 0.75903 | 7.5167 | IDT tripped on over current due to Inverter AC breaker end B phase bus bar melted | 2.6528 | 0.81815 | 6563.1983 | Checked IDT Lv side and inv AC section fonud inverter B phase busing and bus duct bus bar melted restoration WIP.
Tandur | September | Inverter 18 | Insulation failure | 2833.6 | 44812 | 0.57153 | 44812 | 0.63889 | 1.6167 | Inverter tripped on insulation failure . | 0.58047 | 0.81815 | 1345.7128 | Checked all the parameter & found good. Charged the inverter
Tandur | September | SCB.18.10 | String fault | 123.2 | 44812 | 0.63889 | 44813 | 0.47083 | 7.95 | Inverter -18 string-10 floating voltage abnormal | 2.4 | 0.81815 | 253 | Field inspection completed found string cable cable damged
Tandur | September | Inverter 18 | Insulation failure | 2833.6 | 44813 | 0.47083 | 44813 | 0.47153 | 0.016667 | Manual shutdown taken for fuse connected to load. | 0.010926 | 0.86349 | 26.733 | String rectification completed and charged the inverter.
Tandur | September | Inverter 11 | B phase bus bar melted | 3024 | 44813 | 0.25972 | 44813 | 0.29306 | 0.8 | Inverter under shutdown due to bus melted (IDT to Inverter) | 0.041604 | 0.86349 | 108.6346 | Checked IDT Lv side and inv AC section fonud inverter B phase busing and bus duct bus bar melted. Replaced with modified bus-bar available at site and charged the inverter. Now under observation.
Tandur | September | Inverter 10 | Insulation failure | 2657.6 | 44814 | 0.33403 | 44814 | 0.35417 | 0.48333 | Inverter tripped on insulation failure . | 0.10693 | 0.91119 | 258.9325 | Checked all the parameter & found good. Charged the inverter
VGSPL | April | Inverter 12 | External fault (DC Ground Short) | 942.4 | 44655 | 0.5875 | 44655 | 0.59722 | 0.23333 | INV-12 tripped due to External Fault | 0.2017 | 0.73926 | 140.5209 | 5Amp fuse replaced & Restarted inverter
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44657 | 0.41528 | 44657 | 0.42292 | 0.18333 | Grid down due to Earth Fault from Jhunir GSS | 0.1237 | 0.76329 | 2139 | Auto Restored Plant after Resuming grid
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44657 | 0.69028 | 44657 | 0.69444 | 0.1 | Grid down due to Earth Fault from Jhunir GSS | 0.0434 | 0.76329 | 774 | Auto Restored Plant after Resuming grid
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44659 | 0.61944 | 44659 | 0.62986 | 0.25 | Grid down due to Earth Fault from Jhunir GSS | 0.1889 | 0.74625 | 3072 | Auto Restored Plant after Resuming grid
VGSPL | April | Inverter 16 | Over current fault | 942.4 | 44659 | 0.58681 | 44659 | 0.60069 | 0.33333 | Inv-16 Tripped due to OverCurrent | 0.2826 | 0.74625 | 198.7417 | Restarted inverter
VGSPL | April | Inverter 16 | Ground fault | 942.4 | 44660 | 0.54097 | 44660 | 0.54931 | 0.2 | Inv-16 Tripped due to Ground Fault | 0.1765 | 0.72196 | 120.0858 | SMU Panel connector replaced & Restarted inverter
VGSPL | April | Inverter 16 | Control Circuit Error Fault | 942.4 | 44660 | 0.57639 | 44660 | 0.58472 | 0.2 | Inv-16 Tripped due to Control Circuit Error Fault | 0.1709 | 0.72196 | 116.2757 | Restarted inverter
VGSPL | April | Inverter 19 | Control Circuit Error Fault | 830.8 | 44660 | 0.57639 | 44660 | 0.59375 | 0.41667 | Inv-19 Tripped due to Control Circuit Error Fault | 0.3876 | 0.72196 | 232.4834 | Restarted inverter
VGSPL | April | Inverter 19 | Control Circuit Error Fault | 830.8 | 44662 | 0.63194 | 44662 | 0.64583 | 0.33333 | Inv-19 Tripped due to Control Circuit Error Fault | 0.2718 | 0.75523 | 170.5404 | Restarted inverter
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44664 | 0.34722 | 44664 | 0.34931 | 0.05 | Grid Down Due to Phase Jump | 0.0152 | 0.76343 | 290 | Auto Restored Plant after Resuming grid
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44665 | 0.69097 | 44665 | 0.70278 | 0.28333 | Grid down due to Earth Fault from Jhunir GSS | 0.0302 | 0.77976 | 508 | Auto Restored Plant after Resuming grid
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44665 | 0.70833 | 44665 | 0.7375 | 0.7 | Grid down due to Earth Fault from Jhunir GSS | 0.084 | 0.77976 | 1429 | Auto Restored Plant after Resuming grid
VGSPL | April | All Inverters | Grid failure | 16014.6 | 44666 | 0.49097 | 44666 | 0.49792 | 0.16667 | Grid down due to Earth Fault from Jhunir GSS | 0.1337 | 0.75726 | 2174 | Auto Restored Plant after Resuming grid
VGSPL | April | Block 02 | VCB tripped | 3769.6 | 44669 | 0.46528 | 44669 | 0.46806 | 0.066667 | B-2 VCB Tripped | 0.0548 | 0.74673 | 154.2544 | Restarted inverter
VGSPL | April | All Inverters | Phase Jump | 16014.6 | 44679 | 0.42083 | 44679 | 0.42222 | 0.033333 | Phase Jump | 0.0223 | 0.76923 | 381 | Auto Restored Plant after Resuming grid
VGSPL | April | Inverter 16 | Ground fault | 942.4 | 44679 | 0.59375 | 44679 | 0.60417 | 0.25 | INV-16 tripped due to Ground Fault | 0.1822 | 0.76923 | 132.0807 | string rectification done & Restarted inverter
VGSPL | April | Inverter 19 | External fault (DC Ground Short) | 830.8 | 44680 | 0.59375 | 44680 | 0.60278 | 0.21667 | Inv-19 Tripped due to External Fault | 0.1917 | 0.7781 | 123.9243 | Restarted inverter
VGSPL | May | Inverter 17 | Cooling fan failure | 942.4 | 44685 | 0.46875 | 44685 | 0.53125 | 1.5 | Inv-17 Tripped due to cooling Fan Failure | 1.2715 | 0.75926 | 909.7599 | Restarted inverter
VGSPL | May | All Inverters | Grid failure | 16014.6 | 44685 | 0.6875 | 44685 | 0.70417 | 0.4 | Grid down due to Earth Fault from Jhunir GSS | 0.082618 | 0.75926 | 1329 | Auto Restored Plant after Resuming grid
VGSPL | May | All Inverters | Grid failure | 16014.6 | 44687 | 0.40833 | 44687 | 0.41875 | 0.25 | Grid down due to Earth Fault from 220kv Jhunir GSS | 0.0529 | 0.75006 | 808 | Auto Restored Plant after Resuming grid
VGSPL | May | Inverter 01 | Major Fault | 942.4 | 44690 | 0.3125 | 44690 | 0.33333 | 0.5 | Inv-1 Tripped due to Major Fault | 0.1052 | 0.76266 | 75.61 | Restarted inverter
VGSPL | May | Inverter 16 | Over temp. fault | 942.4 | 44693 | 0.5625 | 44693 | 0.58194 | 0.46667 | Inv-16 Tripped due to over temperature Fault | 0.3617 | 0.7419 | 252.8884 | Restarted inverter
VGSPL | May | SCB.02.03 | String fault | 12.4 | 44699 | 0.22569 | 44699 | 0.45833 | 5.5833 | Inv-7 String-4 | 1.9002 | 0.74152 | 17.4721 | 30 Amp fuse, 1 pair MC4 connector used.
VGSPL | May | All Inverters | Grid failure | 16014.6 | 44702 | 0.65278 | 44702 | 0.66875 | 0.38333 | Grid down due to Earth Fault from 220kv Jhunir GSS | 0.0571 | 0.74913 | 886 | Auto Restored Plant after Resuming grid
VGSPL | May | SCB.20.03 | String fault | 148.8 | 44705 | 0.22708 | 44705 | 0.80833 | 13.95 | Tr.-1 GOC Software issue | 4.9966 | 0.76835 | 571.2591 | Restarted Tracker
VGSPL | May | SCB.22.01 | String fault | 148.8 | 44705 | 0.22708 | 44705 | 0.47917 | 6.05 | Tr-31 smps Fault | 4.8653 | 0.76835 | 556.2523 | Restarted Tracker
VGSPL | May | SCB.23.05 | String fault | 148.8 | 44705 | 0.22708 | 44705 | 0.80833 | 13.95 | Tr-24 VFD Fault | 4.8653 | 0.76835 | 556.2523 | Restarted Tracker(SMPS Replaced)
VGSPL | May | SCB.22.03 | String fault | 148.8 | 44706 | 0.225 | 44706 | 0.80486 | 13.9167 | Tr-29 GOC SOFTWARE ISSUE Fault | 3.9364 | 0.75121 | 440.0063 | Restarted Tracker
VGSPL | May | SCB.19.02 | String fault | 148.8 | 44706 | 0.225 | 44706 | 0.80486 | 13.9167 | Tr-8 GOC Fault | 4.5358 | 0.75121 | 507.0072 | Restarted Tracker
VGSPL | May | SCB.23.02 | String fault | 148.8 | 44706 | 0.225 | 44706 | 0.80486 | 13.9167 | Tr-30 GOC Fault | 3.1401 | 0.75121 | 351.005 | Restarted Tracker
VGSPL | May | SCB.22.01 | String fault | 148.8 | 44706 | 0.225 | 44706 | 0.80486 | 13.9167 | Tr-35 GOC Fault | 3.9364 | 0.75121 | 440.0063 | Restarted Tracker
VGSPL | May | All Inverters | Grid failure | 16014.6 | 44707 | 0.70903 | 44707 | 0.71389 | 0.11667 | Grid down due to line changeover from jhunir line to budhlada line (Shutdown taken by Boha GSS PSPCL team for maintenance work) | 0.0378 | 0.76496 | 696 | Auto Restored Plant after Resuming grid
VGSPL | June | SCB.23.04 | String fault | 148.8 | 44714 | 0.54167 | 44714 | 0.80278 | 6.2667 | Tr.-26 stopped due to GOC issue | 0.91559 | 0.7335 | 99.9324 | Restarted Tracker after rectification done.
VGSPL | June | SCB.05.01 | String fault | 24.8 | 44717 | 0.45833 | 44717 | 0.80486 | 8.3167 | Inv-05 SCB-02 ,String No-03&08 Faulty Due to connector Burnt. | 4.6063 | 0.73983 | 84.5148 | 2 Pair MC4 Connector Used.
VGSPL | June | SCB.05.01 | String fault | 24.8 | 44718 | 0.22222 | 44718 | 0.41667 | 4.6667 | Inv-05 SCB-02 ,String No-03&08 Faulty Due to connector Burnt. | 1.3314 | 0.75453 | 24.9136 | 2 Pair MC4 Connector Used.
VGSPL | June | Block 01 | Fire Incident in SISS Room. | 3763.4 | 44721 | 0.63889 | 44742 | 0.80903 | 301 | B-01 RMU Tripped Due to Fire Incident in SISS Room. | 1.1541 | 0.74637 | 357760 | Inverter Under Breakdown due to Fire Incident.
VGSPL | June | SCB.01.02 | String fault | 12.4 | 44722 | 0.5 | 44722 | 0.54167 | 1 | Inv-18 String-4 y connector Burnt | 0.8899 | 0.78044 | 8.612 | 1 Pair y Connector Used.
VGSPL | June | All Inverters | Grid failure | 16014.6 | 44733 | 0.74861 | 44733 | 0.76111 | 0.3 | Grid down due to Earth Fault from Jhunir GSS | 0.0184 | 0.64885 | 251 | Auto Restored Plant after Resuming grid
VGSPL | July | Block 01 | Fire Incident in SISS Room. | 3503 | 44743 | 0.22917 | 44773 | 0.81597 | 427 | Inverter Stopped Due to Fire Incident in SISS Room. | 4.5623 | 0.78474 | 405202 | Inverter Under Breakdown due to Fire Incident.
VGSPL | July | Inverter 19 | Ground fault | 830.8 | 44744 | 0.48958 | 44744 | 0.51389 | 0.58333 | Inv tripped due to ground fault | 0.4712 | 0.78214 | 306.1865 | Rectification done 1 nos 5 amp(Inv) and 1 pair MC4 connector used.
VGSPL | July | Inverter 16 | External fault (DC Ground Short) | 942.4 | 44752 | 0.54861 | 44752 | 0.61458 | 1.5833 | External fault (DC Ground Short) | 0.6418 | 0.8191 | 495.4182 | After Replace 5 Amps Fuse holder Restart Inverter normally.
VGSPL | July | Inverter 06 | External fault (DC Ground Short) | 942.4 | 44753 | 0.38542 | 44753 | 0.425 | 0.95 | External fault (DC Ground Short) | 0.5819 | 0.7425 | 407.1741 | After Replace 5 Amps Fuse holder Restart Inverter normally.
VGSPL | July | Inverter 12 | External fault (DC Ground Short) | 942.4 | 44754 | 0.375 | 44754 | 0.4375 | 1.5 | External fault (DC Ground Short) | 0.9969 | 0.7946 | 746.5097 | Replaced 5 Amps Fuse & checked voltage of all string then Restarted Inverter.
VGSPL | July | Inverter 13 | External fault (DC Ground Short) | 942.4 | 44754 | 0.24097 | 44754 | 0.38403 | 3.4333 | External fault (DC Ground Short) | 0.5512 | 0.7946 | 412.7557 | Replaced 5 Amps Fuse & checked voltage of all string then Restarted Inverter.
VGSPL | July | Inverter 14 | External fault (DC Ground Short) | 942.4 | 44754 | 0.36806 | 44754 | 0.42361 | 1.3333 | External fault (DC Ground Short) | 0.8277 | 0.7946 | 619.8075 | Replaced 5 Amps Fuse & checked voltage of all string then Restarted Inverter.
VGSPL | July | Inverter 16 | External fault (DC Ground Short) | 942.4 | 44754 | 0.36806 | 44754 | 0.43056 | 1.5 | External fault (DC Ground Short) | 0.9455 | 0.7946 | 708.0197 | Replaced 5 Amps Fuse & checked voltage of all string then Restarted Inverter.
VGSPL | July | Inverter 17 | External fault (DC Ground Short) | 942.4 | 44754 | 0.38542 | 44754 | 0.44514 | 1.4333 | External fault (DC Ground Short) | 0.9894 | 0.7946 | 740.8934 | Replaced 5 Amps Fuse & checked voltage of all string then Restarted Inverter.
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44757 | 0.26458 | 44757 | 0.27222 | 0.18333 | Grid down due to line changeover from jhunir line to budhlada line . | 0.0101 | 0.7998 | 201 | Auto Restored Plant after Resuming grid
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44757 | 0.34792 | 44757 | 0.35417 | 0.15 | Grid down due to line changeover from budhlada line to jhunir line. | 0.0503 | 0.7998 | 904 | Auto Restored Plant after Resuming grid
VGSPL | July | SCB.04.02 | String fault | 24.8 | 44757 | 0.22778 | 44757 | 0.41667 | 4.5333 | Inv-14 SCB-4 String-9&4. | 1.2199 | 0.7998 | 24.1968 | 30 Amp fuse, 2 pair MC4 &2 pair y connector used.
VGSPL | July | Inverter 10 | DC overcurrent fault | 942.4 | 44758 | 0.53333 | 44758 | 0.54722 | 0.33333 | DC overcurrent | 0.333 | 0.73478 | 230.589 | Restarted inverter
VGSPL | July | Inverter 10 | External fault (DC Ground Short) | 942.4 | 44758 | 0.57639 | 44758 | 0.59514 | 0.45 | External fault (DC Ground Short) | 0.435 | 0.73478 | 301.2199 | 5amp,30 Amp fuse replaced, 2 pair MC4 &2 pair y connector used.
VGSPL | July | Inverter 14 | External fault (DC Ground Short) | 942.4 | 44758 | 0.35417 | 44758 | 0.45833 | 2.5 | External fault (DC Ground Short) | 1.5978 | 0.73478 | 1106.379 | 30 Amp fuse, 2 pair MC4 &2 pair y connector used.
VGSPL | July | SCB.15.02 | String fault | 396.8 | 44758 | 0.29167 | 44758 | 0.41667 | 3 | External fault (DC Ground Short) | 1.198 | 0.73478 | 349.2912 | 5amp,30 Amp fuse replaced, 2 pair MC4 &2 pair y connector used.
VGSPL | July | Inverter 15 | External fault (DC Ground Short) | 942.4 | 44758 | 0.28125 | 44758 | 0.29167 | 0.25 | External fault (DC Ground Short) | 0.0245 | 0.73478 | 16.9653 | 5amp,30 Amp fuse replaced, 1 pair MC4.
VGSPL | July | Inverter 14 | External fault (DC Ground Short) | 942.4 | 44759 | 0.45833 | 44759 | 0.47153 | 0.31667 | External fault (DC Ground Short) | 0.6785 | 0.7902 | 505.2684 | 5amp,30 Amp fuse replaced, 1 pair MC4.
VGSPL | July | Inverter 15 | External fault (DC Ground Short) | 942.4 | 44759 | 0.45139 | 44759 | 0.46181 | 0.25 | External fault (DC Ground Short) | 0.22 | 0.7902 | 163.8306 | 5amp,30 Amp fuse replaced, 1 pair MC4.
VGSPL | July | SCB.03.01 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.39583 | 4 | Inv-09 SCB -1 String-8. | 0.9195 | 0.7734 | 8.8182 | 30 Amp fuse, 1 pair MC4 used.
VGSPL | July | SCB.03.03 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.41667 | 4.5 | Inv-09 SCB -3 String-4. | 1.2443 | 0.7734 | 11.933 | 30 Amp fuse, 1 pair y connector used.
VGSPL | July | SCB.04.01 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.43056 | 4.8333 | Inv-14 SCB -1 String-15. | 1.4819 | 0.7734 | 14.2117 | 30 Amp fuse, 1 pair MC4 used.
VGSPL | July | SCB.04.02 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.45833 | 5.5 | Inv-09 SCB -3 String-4. | 2.0122 | 0.7734 | 19.2973 | 15mtr cable & 1 pair mc4 used
VGSPL | July | SCB.04.03 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.48958 | 6.25 | Inv-15 SCB -3 String-16. | 2.6634 | 0.7734 | 25.5424 | 30 Amp fuse, 1 pair MC4 used.
VGSPL | July | SCB.04.04 | String fault | 12.4 | 44760 | 0.22917 | 44760 | 0.51389 | 6.8333 | Inv-15 SCB -4 String-10. | 3.1277 | 0.7734 | 29.9951 | 30 Amp fuse, 1 pair MC4 used.
VGSPL | July | SCB.02.04 | String fault | 12.4 | 44761 | 0.23056 | 44761 | 0.38889 | 3.8 | Inv-02 SCB -4 String-2. | 0.7778 | 0.7765 | 7.4891 | 30 Amp fuse, 1 pair MC4 used.
VGSPL | July | SCB.17.02 | String fault | 24.8 | 44761 | 0.23056 | 44761 | 0.44583 | 5.1667 | Inv-17 SCB -2 String-09&12. | 1.5632 | 0.7765 | 30.1029 | 30 Amp fuse, 2 pair MC4 used.
VGSPL | July | SCB.20.04 | String fault | 12.4 | 44761 | 0.22708 | 44761 | 0.46736 | 5.7667 | Inv-20 SCB -4 String-06. | 2.5593 | 0.7765 | 24.6425 | 15mtr cable & 1 pair mc4 used
VGSPL | July | SCB.20.05 | String fault | 12.4 | 44761 | 0.22708 | 44761 | 0.4875 | 6.25 | Inv-20 SCB -5 String-03. | 2.8217 | 0.7765 | 27.169 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | SCB.13.02 | String fault | 12.4 | 44762 | 0.23194 | 44762 | 0.39931 | 4.0167 | Inv-13 SCB -2 String-02. | 0.7376 | 0.8288 | 7.5804 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | Inverter 12 | External fault (DC Ground Short) | 942.4 | 44763 | 0.23889 | 44763 | 0.31597 | 1.85 | External fault (DC Ground Short) | 0.0043 | 0.6716 | 2.7215 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | SCB.12.03 | String fault | 595.2 | 44763 | 0.35417 | 44763 | 0.6875 | 8 | Inv-12 SCB -1,3&4 Breakdown. | 2.1571 | 0.6716 | 862.2712 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | Inverter 16 | External fault (DC Ground Short) | 942.4 | 44763 | 0.5 | 44763 | 0.52083 | 0.5 | External fault (DC Ground Short) | 0.0551 | 0.6716 | 34.8737 | 15mtr cable & 1 pair mc4 used
VGSPL | July | SCB.16.04 | String fault | 396.8 | 44763 | 0.55556 | 44763 | 0.71875 | 3.9167 | Inv-16 SCB -2&4 Breakdown. | 2.03 | 0.6716 | 540.9765 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | Inverter 19 | External fault (DC Ground Short) | 830.8 | 44763 | 0.58333 | 44763 | 0.61111 | 0.66667 | External fault (DC Ground Short) | 0.5486 | 0.6716 | 306.0998 | 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | Inverter 10 | External fault (DC Ground Short) | 942.4 | 44766 | 0.22917 | 44766 | 0.39583 | 4 | External fault (DC Ground Short) | 0.9816 | 0.7408 | 685.2867 | 5amp, 30 Amp fuse, 2 pair MC4 used.
VGSPL | July | Inverter 16 | External fault (DC Ground Short) | 942.4 | 44766 | 0.22917 | 44766 | 0.38542 | 3.75 | External fault (DC Ground Short) | 0.8277 | 0.7408 | 577.8441 | 5Amp, 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | July | SCB.16.01 | String fault | 198.4 | 44766 | 0.39583 | 44766 | 0.48958 | 2.25 | Inv-16 SCB -1 . | 1.6053 | 0.7408 | 235.9393 | String-10&11 .1 Nos 30 Amp fuse, 2 pair MC4 &1 pair Y connector used.
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44769 | 0.71667 | 44769 | 0.72083 | 0.1 | Grid down due to line changeover from Jhunir line to Budhlada line . | 0.0303 | 0.7765 | 548 | Grid down due to line changeover from Jhunir line to Budhlada line .
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44769 | 0.74514 | 44769 | 0.74931 | 0.1 | Grid down due to line changeover from budhlada line to Jhunir line. | 0.0191 | 0.7765 | 375 | Auto Restored Plant after Resuming grid
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44771 | 0.41528 | 44771 | 0.41736 | 0.05 | Grid down due to Earth Fault in Transmission Line. | 0.004 | 0.6352 | 53 | Auto Restored Plant after Resuming grid
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44771 | 0.53194 | 44771 | 0.54306 | 0.26667 | Grid down due to Earth Fault in Transmission Line. | 0.1859 | 0.6352 | 2490 | Auto Restored Plant after Resuming grid
VGSPL | July | All Inverters | Grid failure | 16014.6 | 44771 | 0.55069 | 44771 | 0.81111 | 6.25 | Grid down due to Earth Fault Insulator Puncher VGSUPL Site. | 2.5544 | 0.6352 | 34221 | Insulator Replaced &Charged Plant from GSS side.
VGSPL | August | Block 01 | Fire Incident in SISS Room. | 3503 | 44774 | 0.23958 | 44804 | 0.81111 | 415 | Inverter Stopped Due to Fire Incident in SISS Room. | 6.3704 | 0.7595 | 488686 | Inverter Under Breakdown due to Fire Incident.
VGSPL | August | Inverter 14 | External fault (DC Ground Short) | 942.4 | 44774 | 0.38889 | 44774 | 0.42361 | 0.83333 | External fault (DC Ground Short) | 0.4845 | 0.7595 | 346.7822 | 5Amp, 30 Amp fuse, 1 pair MC4 & 2 pair Y connectior used.
VGSPL | August | Inverter 19 | External fault (DC Ground Short) | 830.8 | 44774 | 0.36806 | 44774 | 0.39583 | 0.66667 | External fault (DC Ground Short) | 0.3033 | 0.7595 | 191.3801 | 5amp, 30 Amp fuse, 1 pair MC4 used.
VGSPL | August | SCB.01.02 | String fault | 24.8 | 44776 | 0.23819 | 44776 | 0.54167 | 7.2833 | Inv-19 SCB -1 String-03,6 | 3.648 | 0.7691 | 69.5808 | 70mtr cable & 1 pair mc4 used
VGSPL | August | SCB.06.02 | String fault | 24.8 | 44776 | 0.23819 | 44776 | 0.50694 | 6.45 | Inv-20 SCB -1 String-03,5 | 4.2482 | 0.7691 | 81.0288 | 30 Amp fuse, 1 pair MC4 & 1 Y connectior used.
VGSPL | August | SCB.02.01 | String fault | 24.8 | 44778 | 0.24097 | 44778 | 0.45833 | 5.2167 | Inv-5 SCB -1 String-10,11 | 1.286 | 0.8282 | 26.4136 | 30 Amp fuse, 1 pair MC4 & 1 Y connectior used.
VGSPL | August | SCB.02.05 | String fault | 12.4 | 44778 | 0.24097 | 44778 | 0.5 | 6.2167 | Inv-7 SCB -1 String-6 | 1.7352 | 0.8282 | 17.8199 | 1 pair MC4 & 1 Y connectior used.
VGSPL | August | SCB.02.03 | String fault | 12.4 | 44778 | 0.24097 | 44778 | 0.5 | 6.2167 | Inv-8 SCB -3 String-14 | 1.7352 | 0.8282 | 17.8199 | 30 Amp fuse, 2 pair MC4 & 1 Y connectior used.
VGSPL | August | Inverter 07 | Cooling fan failure | 942.4 | 44779 | 0.53472 | 44779 | 0.58333 | 1.1667 | Inv no -07 tripped due to Cooling fan failure | 0.7979 | 0.7684 | 577.7914 | After Replaced Cooling Fan with new one Reastart inverter
VGSPL | August | SCB.03.03 | String fault | 24.8 | 44779 | 0.24167 | 44779 | 0.47917 | 5.7 | Inv-9 SCB -3 String-3,14. | 1.8036 | 0.7684 | 34.37 | 30 Amp fuse, 1 pair MC4 connectior used.
VGSPL | August | SCB.03.02 | String fault | 12.4 | 44779 | 0.24167 | 44779 | 0.5 | 6.2 | Inv-10 SCB -2 String-7. | 2.2199 | 0.7684 | 21.1516 | 1 nos DC joint used
VGSPL | August | SCB.03.03 | String fault | 12.4 | 44779 | 0.24167 | 44779 | 0.5 | 6.2 | Inv-12 SCB -3 String-11. | 2.2199 | 0.7684 | 21.1516 | 2 pair MC4 & 1 Y connectior used.
VGSPL | August | Inverter 20 | External fault (DC Ground Short) | 830.8 | 44780 | 0.44444 | 44780 | 0.45139 | 0.16667 | External fault (DC Ground Short) | 0.112 | 0.806 | 74.998 | 5Amp, 30 Amp fuse, 1 pair MC4 & 1 pair Y connectior used.
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44781 | 0.29861 | 44781 | 0.30139 | 0.066667 | Grid down due to Earth Fault from Jhunir GSS | 0.0141 | 0.78104 | 253 | Auto Restored Plant after Resuming grid
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44781 | 0.71597 | 44781 | 0.71875 | 0.066667 | Grid down due to Earth Fault from Jhunir GSS | 0.0196 | 0.78104 | 379 | Auto Restored Plant after Resuming grid
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44784 | 0.34167 | 44784 | 0.34444 | 0.066667 | Grid down due to Earth Fault from Jhunir GSS | 0.0162 | 0.7804 | 282 | Auto Restored Plant after Resuming grid
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44784 | 0.71042 | 44784 | 0.71458 | 0.1 | Grid down due to Earth Fault from Jhunir GSS | 0.0113 | 0.7804 | 178 | Auto Restored Plant after Resuming grid
VGSPL | August | Inverter 17 | Over current fault | 942.4 | 44790 | 0.45972 | 44790 | 0.46736 | 0.18333 | Inverter Tripped Due to DC overcurrent | 0.1507 | 0.82628 | 117.3478 | Restarted inverter
VGSPL | August | Inverter 17 | Over current fault | 942.4 | 44790 | 0.54306 | 44790 | 0.54792 | 0.11667 | Inverter Tripped Due to DC overcurrent | 0.0786 | 0.82628 | 61.2046 | Restarted inverter
VGSPL | August | SCB.20.04 | String fault | 12.4 | 44791 | 0.23264 | 44791 | 0.625 | 9.4167 | string cable found faulty | 6.756 | 0.73188 | 61.3131 | 2 pair MC4 & 1 Y connectior used.
VGSPL | August | SCB.20.04 | String fault | 24.8 | 44791 | 0.45833 | 44791 | 0.75 | 7 | string cable found faulty | 5.9938 | 0.73188 | 108.7917 | 3 pair MC4 & 1 Y connectior used.
VGSPL | August | SCB.19.05 | String fault | 12.4 | 44791 | 0.23264 | 44791 | 0.625 | 9.4167 | string cable found faulty | 6.756 | 0.73188 | 61.3131 | 30 Amp fuse& 25mtr cable , 1 pair MC4 connectior used.
VGSPL | August | Inverter 17 | Ground fault | 942.4 | 44792 | 0.53889 | 44792 | 0.55 | 0.26667 | Inverter Tripped Due to DC Ground fault | 0.2038 | 0.75457 | 144.9233 | 30 Amp fuse,1 pair y connector used.
VGSPL | August | Inverter 17 | Ground fault | 942.4 | 44792 | 0.57986 | 44792 | 0.59444 | 0.35 | Inverter Tripped Due to DC Ground fault | 0.3496 | 0.75457 | 248.6025 | 30mtr cable , 2 pair MC4 connectior
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44797 | 0.34236 | 44797 | 0.34444 | 0.05 | Grid down due to Earth Fault from Jhunir GSS | 0.0183 | 0.75069 | 359 | Auto Restored Plant after Resuming grid
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44797 | 0.71389 | 44797 | 0.71736 | 0.083333 | Grid down due to Earth Fault from Jhunir GSS | 0.0192 | 0.75069 | 336 | Auto Restored Plant after Resuming grid
VGSPL | August | Block 02 | VCB tripped | 3769.6 | 44797 | 0.39861 | 44797 | 0.40417 | 0.13333 | B-2 VCB Tripped | 0.0375 | 0.75069 | 106.1182 | Charged VCB breaker
VGSPL | August | Block 03 | VCB tripped | 3769.6 | 44797 | 0.39861 | 44797 | 0.40417 | 0.13333 | B-3 VCB Tripped | 0.0375 | 0.75069 | 106.1182 | Charged VCB breaker
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44799 | 0.44375 | 44799 | 0.45417 | 0.25 | Grid down due to Earth Fault from Jhunir GSS | 0.0621 | 0.71047 | 950 | Auto Restored Plant after Resuming grid
VGSPL | August | All Inverters | Grid failure | 16014.6 | 44801 | 0.29444 | 44801 | 0.32014 | 0.61667 | Grid down due to 66Kv Line Disc changed by Boha GSS | 0.09 | 0.7423 | 1879 | Auto Restored Plant after Resuming grid
VGSPL | August | SCB.10.03 | String fault | 12.4 | 44803 | 0.24306 | 44803 | 0.54167 | 7.1667 | string cable found faulty | 3.9126 | 0.7789 | 37.7893 | 30 Amp fuse& 30mtr cable , 1 pair MC4 connectior used.
VGSPL | August | SCB.14.04 | String fault | 12.4 | 44803 | 0.24306 | 44803 | 0.54167 | 7.1667 | string cable found faulty | 3.9126 | 0.7789 | 37.7893 | 30 Amp fuse& 20mtr cable , 1 pair MC4 connectior used.
VGSPL | September | Block 01 | Fire Incident in SISS Room. | 3503 | 44805 | 0.24653 | 44816 | 0.78472 | 152.68 | Inverter Stopped Due to Fire Incident in SISS Room. | 6.4724 | 0.7894 | 208617 | Inverter Under Breakdown due to Fire Incident.
VGSPL | September | SCB.17.01 | String fault | 12.4 | 44806 | 0.24653 | 44806 | 0.66667 | 10.0833 | string cable found faulty | 6.3934 | 0.76 | 60.2514 | 30mtr cable&1 pair MC4 ,1 Nos Y connectior used.
VGSPL | September | SCB.20.03 | String fault | 49.6 | 44807 | 0.25069 | 44807 | 0.7875 | 12.8833 | Tracker in breakdown due to shaft pin handle damaged | 1.5127 | 0.7597 | 57 | Tracker in breakdown due to shaft pin handle damaged
VGSPL | September | SCB.20.03 | String fault | 49.6 | 44808 | 0.25486 | 44808 | 0.78958 | 12.8333 | Tracker in breakdown due to shaft pin handle damaged | 2.8107 | 0.746 | 104 | Tracker in breakdown due to shaft pin handle damaged
VGSPL | September | SCB.20.03 | String fault | 49.6 | 44809 | 0.25139 | 44809 | 0.78264 | 12.75 | Tracker in breakdown due to shaft pin handle damaged | 2.716 | 0.7349 | 99 | Tracker in breakdown due to shaft pin handle damaged
VGSPL | September | SCB.20.03 | String fault | 49.6 | 44810 | 0.24861 | 44810 | 0.78542 | 12.8833 | Tracker in breakdown due to shaft pin handle damaged | 2.7406 | 0.7798 | 106 | Tracker in breakdown due to shaft pin handle damaged
VGSPL | September | All Inverters | Grid failure | 16014.6 | 44811 | 0.37361 | 44811 | 0.46806 | 2.2667 | Grid down due to permit taken by Boha GSS | 1.5747 | 0.72173 | 25131 | Auto Restored Plant after Resuming grid
VGSPL | September | All Inverters | Grid failure | 16014.6 | 44813 | 0.58125 | 44813 | 0.59306 | 0.28333 | Grid Down due to Protection relay test checked by PSPCL team at 220 kv jhunir GSS FROM 13:57Hrs to 14:14Hrs | 0.2401 | 0.7276 | 3708 | Auto Restored Plant after Resuming grid
VGSPL | September | All Inverters | Grid failure | 16014.6 | 44816 | 0.60625 | 44816 | 0.64097 | 0.83333 | Grid down due to line changeover from Jhunir line to Budhlada line . | 0.4438 | 0.79 | 7618 | Auto Restored Plant after Resuming grid
VGSPL | September | All Inverters | Grid failure | 16014.6 | 44816 | 0.68056 | 44816 | 0.6875 | 0.16667 | Grid down due to line changeover from budhlada line to Jhunir line. | 0.0441 | 0.79 | 814 | Auto Restored Plant after Resuming grid
VGSUPL | April | Inverter 12 | Ground Fault | 780.8 | 44654 | 0.60417 | 44654 | 0.60972 | 0.13333 | Inverter tripped in ground fault | 0.0988 | 0.75896 | 58.5486 | After reset inverter started
VGSUPL | April | Inverter 11 | Ac Switch Response fault | 780.8 | 44655 | 0.58611 | 44655 | 0.60764 | 0.51667 | Inverter tripped in Ac Switch Response fault | 0.3899 | 0.74882 | 227.9676 | After reset inverter started
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44655 | 0.39514 | 44655 | 0.58611 | 4.5833 | Grid down due to annual maintenance at Boha GSS | 3.1168 | 0.74882 | 49151 | system auto restored after resuming grid
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44657 | 0.41528 | 44657 | 0.42292 | 0.18333 | Grid down due to earth fault at Jhunir GSS | 0.1404 | 0.77166 | 2277 | system auto restored after resuming grid
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44657 | 0.69028 | 44657 | 0.69444 | 0.1 | Grid down due to earth fault at Jhunir GSS | 0.0291 | 0.77166 | 481 | system auto restored after resuming grid
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44657 | 0.47083 | 44657 | 0.475 | 0.1 | Inverter tripped in pv power interrupted fault | 0.0888 | 0.77166 | 53.5033 | After reset inverter started
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44657 | 0.55208 | 44657 | 0.55694 | 0.11667 | Inverter tripped in pv power interrupted fault | 0.0995 | 0.77166 | 59.9502 | After reset inverter started
VGSUPL | April | Inverter 21 | Ac Switch Response fault | 792 | 44657 | 0.42292 | 44657 | 0.43056 | 0.18333 | Inverter tripped in Ac Switch Response fault | 0.146 | 0.77166 | 89.2289 | After reset inverter started
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44658 | 0.43056 | 44658 | 0.44792 | 0.41667 | Inverter tripped in pv power interrupted fault | 0.3507 | 0.71983 | 197.1083 | After reset inverter started
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44658 | 0.49306 | 44658 | 0.51736 | 0.58333 | Inverter tripped in pv power interrupted fault | 0.5719 | 0.71983 | 321.4321 | After reset inverter started
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44659 | 0.61944 | 44659 | 0.62986 | 0.25 | Grid down due to earth fault at Jhunir GSS | 0.1048 | 0.73545 | 1571 | system auto restored after resuming grid
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44660 | 0.52917 | 44660 | 0.53403 | 0.11667 | Inverter tripped in pv power interrupted fault | 0.1055 | 0.74341 | 61.2383 | After reset inverter started
VGSUPL | April | SCB.02.06 | String fault | 6.1 | 44663 | 0.25347 | 44663 | 0.45833 | 4.9167 | string found faulty | 1.7583 | 0.7865 | 8.4357 | Rectification done
VGSUPL | April | SCB.13.01 | String fault | 12.2 | 44663 | 0.25347 | 44663 | 0.44792 | 4.6667 | 2nos string found faulty | 1.5913 | 0.7865 | 15.269 | Rectification done
VGSUPL | April | SCB.04.01 | String fault | 12.2 | 44664 | 0.25 | 44664 | 0.43194 | 4.3667 | 2nos string found faulty | 1.4848 | 0.7704 | 13.9555 | Rectification done
VGSUPL | April | SCB.03.04 | String fault | 6.1 | 44664 | 0.25 | 44664 | 0.44167 | 4.6 | string found faulty | 1.6313 | 0.7704 | 7.6662 | Rectification done
VGSUPL | April | SCB.04.04 | String fault | 6.1 | 44664 | 0.25 | 44664 | 0.44792 | 4.75 | string found faulty | 1.7518 | 0.7704 | 8.2325 | Rectification done
VGSUPL | April | SCB.07.02 | String fault | 12.2 | 44665 | 0.25 | 44665 | 0.45833 | 5 | string found faulty | 2.0726 | 0.76641 | 19.3793 | Rectification done
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44665 | 0.69097 | 44665 | 0.70278 | 0.28333 | Grid down due to earth fault at Jhunir GSS | 0.0642 | 0.76641 | 954 | system auto restored after resuming grid
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44665 | 0.70833 | 44665 | 0.7375 | 0.7 | Grid down due to earth fault at Jhunir GSS | 0.1206 | 0.76641 | 1860 | system auto restored after resuming grid
VGSUPL | April | All Inverters | Grid failure | 17999.015 | 44666 | 0.49097 | 44666 | 0.49792 | 0.16667 | Grid down due to earth fault at Jhunir GSS | 0.1365 | 0.78697 | 2263 | system auto restored after resuming grid
VGSUPL | April | Inverter 22 | Ac Switch Response fault | 792 | 44666 | 0.49792 | 44666 | 0.50347 | 0.13333 | Inverter tripped in Ac Switch Response fault | 0.1094 | 0.78697 | 68.1866 | After reset inverter started
VGSUPL | April | Inverter 13 | Ac Switch Response fault | 780.8 | 44666 | 0.49792 | 44666 | 0.50486 | 0.16667 | Inverter tripped in Ac Switch Response fault | 0.1365 | 0.78697 | 83.8743 | After reset inverter started
VGSUPL | April | Inverter 10 | PV power interrupted | 780.8 | 44667 | 0.5625 | 44667 | 0.57153 | 0.21667 | Inverter tripped in pv power interrupted fault | 0.168 | 0.78041 | 102.3694 | After reset inverter started
VGSUPL | April | IDT 02 | RMU Tripped | 1561.6 | 44668 | 0.30903 | 44668 | 0.33681 | 0.66667 | RMU Trip in Relay Malfunction Fault | 0.2269 | 0.74944 | 265.5481 | After reset Relay Malfunction Trafo Charged Succsfully started
VGSUPL | April | SCB.04.02 | String fault | 12.2 | 44672 | 0.25139 | 44672 | 0.45833 | 4.9667 | string found faulty | 0.5765 | 0.82674 | 5.8147 | Rectification done
VGSUPL | April | SCB.03.01 | String fault | 12.2 | 44674 | 0.24306 | 44674 | 0.41667 | 4.1667 | string found faulty | 1.3492 | 0.77121 | 12.6943 | Rectification done
VGSUPL | April | SCB.02.02 | String fault | 6.1 | 44674 | 0.24306 | 44674 | 0.42361 | 4.3333 | string found faulty | 1.4694 | 0.77121 | 6.9126 | Rectification done
VGSUPL | April | SCB.09.03 | String fault | 12.2 | 44674 | 0.24306 | 44674 | 0.4375 | 4.6667 | string found faulty | 1.721 | 0.77121 | 16.1925 | Rectification done
VGSUPL | April | Inverter 25 | Fan Rotation Fault | 725 | 44678 | 0.29861 | 44678 | 0.40625 | 2.5833 | Inverter Started On 10% Due to Fan Rotation Fault. | 1.2672 | 0.76192 | 699.9897 | Dc Section Fan Capacitor Change
VGSUPL | April | Inverter 25 | Fan Rotation Fault | 725 | 44678 | 0.42569 | 44678 | 0.44444 | 0.45 | Inverter Started On 10% Due to Fan Rotation Fault. | 0.372 | 0.76192 | 205.4894 | Ac Section Fan Capacitor Change
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44685 | 0.6875 | 44685 | 0.70417 | 0.4 | Grid down due to earth fault at Jhunir GSS | 0.0679 | 0.78081 | 1106 | system auto restored after resuming grid
VGSUPL | May | SCB.02.01 | String fault | 6.1 | 44685 | 0.27083 | 44685 | 0.45833 | 4.5 | string found faulty | 1.8771 | 0.78081 | 8.9405 | Rectification done
VGSUPL | May | SCB.10.06 | String fault | 6.1 | 44685 | 0.27083 | 44685 | 0.46528 | 4.6667 | string found faulty | 2.0112 | 0.78081 | 9.5792 | Rectification done
VGSUPL | May | SCB.22.05 | String fault | 6 | 44685 | 0.27083 | 44685 | 0.46528 | 4.6667 | string found faulty | 2.0112 | 0.78081 | 9.4222 | Rectification done
VGSUPL | May | SCB.22.01 | String fault | 6 | 44685 | 0.27083 | 44685 | 0.47222 | 4.8333 | string found faulty | 2.145 | 0.78081 | 10.049 | Rectification done
VGSUPL | May | SCB.21.01 | String fault | 6 | 44685 | 0.27083 | 44685 | 0.47222 | 4.8333 | string found faulty | 2.145 | 0.78081 | 10.049 | Rectification done
VGSUPL | May | Inverter 21 | Ground Fault | 792 | 44685 | 0.3375 | 44685 | 0.36458 | 0.65 | Inverter tripped in ground fault | 0.1988 | 0.78081 | 122.938 | After reset inverter started
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44687 | 0.40625 | 44687 | 0.41875 | 0.3 | Grid down due to earth fault at Jhunir GSS | 0.0662 | 0.7776 | 1071 | system auto restored after resuming grid
VGSUPL | May | Inverter 26 | Ground Fault | 750 | 44690 | 0.33611 | 44690 | 0.36458 | 0.68333 | Inverter tripped in ground fault | 0.2507 | 0.76864 | 144.524 | After reset inverter started
VGSUPL | May | SCB.02.01 | String fault | 6.1 | 44691 | 0.23611 | 44691 | 0.47222 | 5.6667 | string found faulty | 2.1719 | 0.76345 | 10.1146 | Rectification done
VGSUPL | May | SCB.04.05 | String fault | 6.1 | 44691 | 0.23611 | 44691 | 0.47917 | 5.8333 | string found faulty | 2.301 | 0.76345 | 10.7158 | Rectification done
VGSUPL | May | SCB.09.03 | String fault | 6.1 | 44691 | 0.23611 | 44691 | 0.47222 | 5.6667 | string found faulty | 2.171 | 0.76345 | 10.1104 | Rectification done
VGSUPL | May | SCB.09.03 | String fault | 6.1 | 44691 | 0.23611 | 44691 | 0.47917 | 5.8333 | string found faulty | 2.301 | 0.76345 | 10.7158 | Rectification done
VGSUPL | May | SCB.14.02 | String fault | 6.1 | 44691 | 0.23611 | 44691 | 0.47917 | 5.8333 | string found faulty | 2.3016 | 0.76345 | 10.7186 | Rectification done
VGSUPL | May | SCB.05.04 | String fault | 6.1 | 44692 | 0.23611 | 44692 | 0.46181 | 5.4167 | string found faulty | 1.954 | 0.75504 | 8.9997 | Rectification done
VGSUPL | May | SCB.04.01 | String fault | 6.1 | 44693 | 0.23611 | 44693 | 0.47222 | 5.6667 | string found faulty | 2.3392 | 0.74109 | 10.5747 | Rectification done
VGSUPL | May | SCB.04.01 | String fault | 6.1 | 44693 | 0.23611 | 44693 | 0.47222 | 5.6667 | string found faulty | 2.3392 | 0.74109 | 10.5747 | Rectification done
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44694 | 0.29167 | 44694 | 0.29931 | 0.18333 | Grid Down due to line change over Jhunir gss to Budhlada Gss. | 0.0295 | 0.75509 | 470 | system auto restored after resuming grid
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44694 | 0.50417 | 44694 | 0.50972 | 0.13333 | Grid Down due to line change over Budhlada gss to jhunir Gss. | 0.1138 | 0.75509 | 1801 | system auto restored after resuming grid
VGSUPL | May | SCB.19.01 | String fault | 6 | 44696 | 0.23264 | 44696 | 0.44444 | 5.0833 | string found faulty | 2.03 | 0.7435 | 9.0558 | Rectification done
VGSUPL | May | SCB.14.04 | String fault | 6.1 | 44696 | 0.23264 | 44696 | 0.45139 | 5.25 | string found faulty | 2.55 | 0.7435 | 11.5651 | Rectification done
VGSUPL | May | SCB.06.05 | String fault | 18.3 | 44696 | 0.23264 | 44696 | 0.46528 | 5.5833 | string found faulty | 2.1511 | 0.7435 | 29.2678 | Rectification done
VGSUPL | May | SCB.05.04 | String fault | 6.1 | 44696 | 0.23264 | 44696 | 0.47222 | 5.75 | string found faulty | 2.5947 | 0.7435 | 11.7678 | Rectification done
VGSUPL | May | SCB.12.05 | String fault | 6.1 | 44697 | 0.23264 | 44697 | 0.47917 | 5.9167 | string found faulty | 1.5614 | 0.78967 | 7.5212 | Rectification done
VGSUPL | May | SCB.06.05 | String fault | 6.1 | 44697 | 0.23264 | 44697 | 0.47222 | 5.75 | string found faulty | 1.4626 | 0.78967 | 7.0453 | Rectification done
VGSUPL | May | Inverter 11 | Ac Mov Ac Cap fault | 780.8 | 44698 | 0.27778 | 44698 | 0.30903 | 0.75 | Inverter tripped in Ac Mov Ac Cap fault | 0.0644 | 0.80356 | 40.4056 | After reset inverter started
VGSUPL | May | Inverter 12 | Internal SW fault | 780.8 | 44698 | 0.51667 | 44698 | 0.52222 | 0.13333 | Inverter tripped internal SW fault | 0.0846 | 0.80356 | 53.0795 | After reset inverter started
VGSUPL | May | SCB.20.06 | String fault | 6 | 44698 | 0.23264 | 44698 | 0.4375 | 4.9167 | string found faulty | 1.2012 | 0.80356 | 5.7914 | Rectification done
VGSUPL | May | SCB.18.06 | String fault | 6.1 | 44698 | 0.23264 | 44698 | 0.44444 | 5.0833 | string found faulty | 1.2628 | 0.80356 | 6.1899 | Rectification done
VGSUPL | May | Inverter 22 | Fan Rotation Fault | 712.8 | 44699 | 0.55 | 44699 | 0.64375 | 2.25 | Inverter Started On 10% Due to Fan Rotation Fault. | 1.491 | 0.77661 | 825.3698 | IGBT Section Fan Change.
VGSUPL | May | Inverter 12 | Internal SW fault | 780.8 | 44699 | 0.52222 | 44699 | 0.52847 | 0.15 | Inverter tripped in SW fault | 0.1227 | 0.77661 | 74.4025 | After reset inverter started
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44702 | 0.65417 | 44702 | 0.66875 | 0.35 | Grid down due to earth fault at Jhunir GSS | 0.0407 | 0.76691 | 651 | system auto restored after resuming grid
VGSUPL | May | Inverter 12 | Ac Mov Ac Cap fault | 780.8 | 44702 | 0.66875 | 44702 | 0.69167 | 0.55 | Inverter tripped in Ac Mov Ac Cap fault | 0.0274 | 0.76691 | 16.4072 | After reset inverter started
VGSUPL | May | Inverter 22 | Ground Fault | 792 | 44703 | 0.45139 | 44703 | 0.45625 | 0.11667 | Inverter tripped in ground fault | 0.0993 | 0.7266 | 57.1436 | After reset inverter started
VGSUPL | May | Inverter 21 | Ground Fault | 792 | 44703 | 0.51736 | 44703 | 0.52569 | 0.2 | Inverter tripped in ground fault | 0.1877 | 0.7266 | 108.0147 | After reset inverter started
VGSUPL | May | SCB.21.03 | String fault | 18 | 44704 | 0.24306 | 44704 | 0.44444 | 4.8333 | string found faulty | 1.2857 | 0.8514 | 19.7035 | Rectification done
VGSUPL | May | SCB.01.05 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.45139 | 5 | string found faulty | 1.3781 | 0.8514 | 7.1572 | Rectification done
VGSUPL | May | SCB.02.06 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.45486 | 5.0833 | string found faulty | 1.4437 | 0.8514 | 7.4979 | Rectification done
VGSUPL | May | SCB.01.03 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.46181 | 5.25 | string found faulty | 1.5803 | 0.8514 | 8.2073 | Rectification done
VGSUPL | May | SCB.02.05 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.46875 | 5.4167 | string found faulty | 1.7198 | 0.8514 | 8.9318 | Rectification done
VGSUPL | May | SCB.04.04 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.47569 | 5.5833 | string found faulty | 1.8552 | 0.8514 | 9.635 | Rectification done
VGSUPL | May | SCB.03.04 | String fault | 6.1 | 44704 | 0.24306 | 44704 | 0.48264 | 5.75 | string found faulty | 1.9896 | 0.8514 | 10.333 | Rectification done
VGSUPL | May | SCB.01.06 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.41667 | 4.4167 | string found faulty | 1.6185 | 0.80138 | 7.9119 | Rectification done
VGSUPL | May | SCB.08.06 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.42361 | 4.5833 | string found faulty | 1.7411 | 0.80138 | 8.5112 | Rectification done
VGSUPL | May | SCB.22.04 | String fault | 6 | 44705 | 0.23264 | 44705 | 0.4375 | 4.9167 | string found faulty | 1.9623 | 0.80138 | 9.4352 | Rectification done
VGSUPL | May | SCB.12.03 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.45139 | 5.25 | string found faulty | 2.2242 | 0.80138 | 10.8728 | Rectification done
VGSUPL | May | SCB.12.01 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.47222 | 5.75 | string found faulty | 2.6059 | 0.80138 | 12.7387 | Rectification done
VGSUPL | May | SCB.12.04 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.47917 | 5.9167 | string found faulty | 2.7563 | 0.80138 | 13.4739 | Rectification done
VGSUPL | May | SCB.08.05 | String fault | 6.1 | 44705 | 0.23264 | 44705 | 0.49306 | 6.25 | string found faulty | 3.0104 | 0.80138 | 14.716 | Rectification done
VGSUPL | May | Inverter 01 | Ground Fault | 780.8 | 44705 | 0.66667 | 44705 | 0.67222 | 0.13333 | Inverter tripped in ground fault | 0.0732 | 0.80138 | 45.8023 | After reset inverter started
VGSUPL | May | SCB.01.06 | String fault | 6.1 | 44706 | 0.22917 | 44706 | 0.43056 | 4.8333 | string found faulty | 1.8724 | 0.785 | 8.966 | Rectification done
VGSUPL | May | SCB.01.04 | String fault | 18.3 | 44706 | 0.22917 | 44706 | 0.45486 | 5.4167 | string found faulty | 2.3871 | 0.785 | 34.2918 | Rectification done
VGSUPL | May | SCB.21.04 | String fault | 6 | 44706 | 0.22917 | 44706 | 0.46528 | 5.6667 | string found faulty | 2.6141 | 0.785 | 12.3124 | Rectification done
VGSUPL | May | SCB.21.05 | String fault | 6 | 44706 | 0.22917 | 44706 | 0.47917 | 6 | string found faulty | 2.9264 | 0.785 | 13.7833 | Rectification done
VGSUPL | May | SCB.13.01 | String fault | 12.2 | 44707 | 0.22569 | 44707 | 0.4875 | 6.2833 | string found faulty | 2.8549 | 0.7764 | 27.0418 | Rectification done
VGSUPL | May | SCB.17.02 | String fault | 6.1 | 44707 | 0.22569 | 44707 | 0.49653 | 6.5 | string found faulty | 3.0676 | 0.7764 | 14.5283 | Rectification done
VGSUPL | May | SCB.11.04 | String fault | 6.1 | 44707 | 0.22569 | 44707 | 0.52361 | 7.15 | string found faulty | 3.6635 | 0.7764 | 17.3505 | Rectification done
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44707 | 0.70903 | 44707 | 0.71667 | 0.18333 | Grid down due to line changeover from Jhunir to Budhlada(shutdown taken by Boha GSS PSPCL team for maintenance work) | 0.051 | 0.7764 | 818 | system auto restored after resuming grid
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44707 | 0.78611 | 44707 | 0.79722 | 0.26667 | Grid down due to line changeover from Budhlada to Jhunir GSS | 0.0036 | 0.7764 | 57 | system auto restored after resuming grid
VGSUPL | May | SCB.01.04 | String fault | 6.1 | 44708 | 0.22917 | 44708 | 0.48056 | 6.0333 | string found faulty | 2.622 | 0.76675 | 12.2635 | Rectification done
VGSUPL | May | All Inverters | Grid failure | 17999.015 | 44708 | 0.39236 | 44708 | 0.40764 | 0.36667 | Grid down due to line changeover maintenance at 220kv Jhunir GSS | 0.2404 | 0.76675 | 3875 | system auto restored after resuming grid
VGSUPL | May | Inverter 16 | Ac Switch Response fault | 780.8 | 44708 | 0.40764 | 44708 | 0.425 | 0.41667 | Inverter tripped in AC switch response fault | 0.3011 | 0.76675 | 180.2615 | Inverter started after fault clear
VGSUPL | May | Inverter 04 | Fan Rotation Fault | 702.72 | 44709 | 0.53194 | 44709 | 0.56597 | 0.81667 | Inverter run at 10% load due to fan rotation fault | 0.6519 | 0.76873 | 352.1583 | Inverter running at full load after IGBT fan replaced
VGSUPL | May | Inverter 04 | Fan Rotation Fault | 702.72 | 44709 | 0.575 | 44709 | 0.62083 | 1.1 | Inverter run at 10% load due to fan rotation fault | 0.6074 | 0.76873 | 328.1193 | Inverter running at full load after inverter DC side fan capacitor changed
VGSUPL | May | Inverter 21 | Fan Rotation Fault | 792 | 44710 | 0.31944 | 44710 | 0.33889 | 0.46667 | Inverter run at 10% load due to fan rotation fault | 0.1552 | 0.75409 | 92.6915 | Inverter running at full load after reset
VGSUPL | May | Inverter 04 | PV power interrupted | 780.8 | 44710 | 0.38889 | 44710 | 0.39583 | 0.16667 | Inverter tripped in PV power interrupted fault | 0.107 | 0.75409 | 63.0009 | After reset inverter started
VGSUPL | June | Inverter 12 | Internal SW fault | 780.8 | 44713 | 0.35486 | 44713 | 0.36111 | 0.15 | Inverter tripped in Internal SW fault | 0.0701 | 0.73631 | 40.3013 | After reset inverter started
VGSUPL | June | Inverter 16 | Ac Switch Response fault | 780.8 | 44714 | 0.25694 | 44714 | 0.29375 | 0.88333 | Inverter tripped in AC switch response fault | 0.0862 | 0.7491 | 50.4184 | After reset inverter started
VGSUPL | June | Inverter 12 | Internal SW fault | 780.8 | 44714 | 0.52778 | 44714 | 0.53472 | 0.16667 | Inverter tripped in Internal SW fault | 0.1483 | 0.7491 | 86.7406 | After reset inverter started
VGSUPL | June | Inverter 21 | Fan Rotation Fault | 712.8 | 44715 | 0.34583 | 44715 | 0.36806 | 0.53333 | Inverter run at 10% load due to fan rotation fault | 0.2576 | 0.74589 | 136.9574 | Inverter run at full load after reset
VGSUPL | June | Inverter 16 | Ac Switch Response fault | 780.8 | 44717 | 0.25347 | 44717 | 0.45694 | 4.8833 | Inverter tripped in AC switch response fault | 2.1774 | 0.73745 | 1253.7505 | Inverter started after Pf contector replaced
VGSUPL | June | Inverter 12 | Internal SW fault | 780.8 | 44718 | 0.31458 | 44718 | 0.34097 | 0.63333 | Inverter tripped in Internal SW fault | 0.2013 | 0.7509 | 118.0221 | After reset inverter started
VGSUPL | June | Inverter 12 | Internal SW fault | 780.8 | 44718 | 0.5625 | 44718 | 0.57986 | 0.41667 | Inverter tripped in Internal SW fault | 0.3286 | 0.7509 | 192.6581 | After reset inverter started
VGSUPL | June | All Inverters | Grid failure | 17999.015 | 44721 | 0.40278 | 44721 | 0.40556 | 0.066667 | Grid down due to Relay Testing Work at Jhunir GSS | 0.0193 | 0.72638 | 295 | system auto restored after resuming grid
VGSUPL | June | Inverter 16 | Ac Switch Response fault | 780.8 | 44722 | 0.22569 | 44722 | 0.34722 | 2.9167 | Inverter tripped in AC switch response fault | 0.4302 | 0.72377 | 243.116 | Inverter started after Pf contector replaced
VGSUPL | June | IDT 08 | RMU Tripped | 1561.6 | 44722 | 0.34722 | 44722 | 0.42222 | 1.8 | RMU Mannually stopped for breaker Change of Inv-16 | 1.0106 | 0.72377 | 1142.227 | RMU Started after AC Breaker changed of Inv-16
VGSUPL | June | Inverter 26 | Ground Fault | 750 | 44724 | 0.51458 | 44724 | 0.51944 | 0.11667 | Inverter tripped in Ground Fault . | 0.0976 | 0.71992 | 52.6983 | After reset inverter started
VGSUPL | June | SCB.01.04 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.42361 | 4.75 | string found faulty | 1.3378 | 0.71727 | 5.8533 | Rectification done
VGSUPL | June | SCB.01.05 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.43056 | 4.9167 | string found faulty | 1.4497 | 0.71727 | 6.3429 | Rectification done
VGSUPL | June | SCB.01.03 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.4375 | 5.0833 | string found faulty | 1.5822 | 0.71727 | 6.9227 | Rectification done
VGSUPL | June | SCB.17.02 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.45139 | 5.4167 | string found faulty | 1.788 | 0.71727 | 7.8231 | Rectification done
VGSUPL | June | SCB.18.01 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.46181 | 5.6667 | string found faulty | 1.9503 | 0.71727 | 8.5332 | Rectification done
VGSUPL | June | SCB.13.06 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.47222 | 5.9167 | string found faulty | 2.1197 | 0.71727 | 9.2744 | Rectification done
VGSUPL | June | SCB.15.06 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.47917 | 6.0833 | string found faulty | 2.2609 | 0.71727 | 9.8922 | Rectification done
VGSUPL | June | SCB.15.03 | String fault | 6.1 | 44726 | 0.22569 | 44726 | 0.48611 | 6.25 | string found faulty | 2.3629 | 0.71727 | 10.3385 | Rectification done
VGSUPL | June | Inverter 16 | AC Power Interupted fault | 780.8 | 44726 | 0.44931 | 44726 | 0.45417 | 0.11667 | Inverter tripped in AC Power Interupted Fault . | 0.0756 | 0.71727 | 42.3393 | After reset inverter started
VGSUPL | June | Inverter 01 | Phase Imbalance Fault | 780.8 | 44727 | 0.46944 | 44727 | 0.47708 | 0.18333 | Inverter tripped in Phase Imbalance Fault . | 0.1659 | 0.71803 | 93.01 | Y Phase 1250 amp Fuse Change After Inverter Started.
VGSUPL | June | Inverter 04 | Fan Rotation Fault | 702.72 | 44728 | 0.5125 | 44728 | 0.55417 | 1 | Inverter run at 10% load due to fan rotation fault | 0.8815 | 0.74093 | 458.9675 | Inverter run at full load after reset
VGSUPL | June | SCB.03.05 | String fault | 24.4 | 44731 | 0.22569 | 44731 | 0.41667 | 4.5833 | string found faulty | 0.6568 | 0.89674 | 14.3711 | Rectification done
VGSUPL | June | SCB.03.04 | String fault | 18.3 | 44731 | 0.22569 | 44731 | 0.43056 | 4.9167 | string found faulty | 0.7327 | 0.89674 | 12.0239 | Rectification done
VGSUPL | June | SCB.03.03 | String fault | 18.3 | 44731 | 0.22569 | 44731 | 0.44444 | 5.25 | string found faulty | 0.7892 | 0.89674 | 12.9511 | Rectification done
VGSUPL | June | SCB.03.02 | String fault | 6.1 | 44731 | 0.22569 | 44731 | 0.45139 | 5.4167 | string found faulty | 0.8171 | 0.89674 | 4.4696 | Rectification done
VGSUPL | June | SCB.20.06 | String fault | 18 | 44731 | 0.22569 | 44731 | 0.46528 | 5.75 | string found faulty | 0.8846 | 0.89674 | 14.2787 | Rectification done
VGSUPL | June | SCB.20.03 | String fault | 12 | 44731 | 0.22569 | 44731 | 0.47569 | 6 | string found faulty | 0.9422 | 0.89674 | 10.1389 | Rectification done
VGSUPL | June | SCB.20.02 | String fault | 6 | 44731 | 0.22569 | 44731 | 0.48264 | 6.1667 | string found faulty | 0.9864 | 0.89674 | 5.3073 | Rectification done
VGSUPL | June | SCB.18.01 | String fault | 12.2 | 44732 | 0.22569 | 44732 | 0.40278 | 4.25 | string found faulty | 1.0247 | 0.82293 | 10.2877 | Rectification done
VGSUPL | June | SCB.18.04 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.40972 | 4.4167 | string found faulty | 1.1195 | 0.82293 | 5.6197 | Rectification done
VGSUPL | June | SCB.17.01 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.42014 | 4.6667 | string found faulty | 1.291 | 0.82293 | 6.4807 | Rectification done
VGSUPL | June | SCB.22.02 | String fault | 6 | 44732 | 0.22569 | 44732 | 0.46875 | 5.8333 | string found faulty | 1.1213 | 0.82293 | 5.5365 | Rectification done
VGSUPL | June | SCB.22.05 | String fault | 6 | 44732 | 0.22569 | 44732 | 0.47569 | 6 | string found faulty | 2.2384 | 0.82293 | 11.0523 | Rectification done
VGSUPL | June | SCB.09.03 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.48264 | 6.1667 | string found faulty | 2.351 | 0.82293 | 11.8017 | Rectification done
VGSUPL | June | SCB.10.02 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.48611 | 6.25 | string found faulty | 2.3851 | 0.82293 | 11.9729 | Rectification done
VGSUPL | June | SCB.11.04 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.49306 | 6.4167 | string found faulty | 2.4695 | 0.82293 | 12.3966 | Rectification done
VGSUPL | June | SCB.11.03 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.50347 | 6.6667 | string found faulty | 2.5988 | 0.82293 | 13.0456 | Rectification done
VGSUPL | June | SCB.23.04 | String fault | 6.1 | 44732 | 0.22569 | 44732 | 0.51042 | 6.8333 | string found faulty | 2.667 | 0.82293 | 13.388 | Rectification done
VGSUPL | June | SCB.16.01 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.40972 | 4.1667 | string found faulty | 0.3537 | 0.81991 | 1.769 | Rectification done
VGSUPL | June | SCB.14.02 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.42014 | 4.4167 | string found faulty | 0.3899 | 0.81991 | 1.9501 | Rectification done
VGSUPL | June | SCB.16.02 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.42361 | 4.5 | string found faulty | 0.404 | 0.81991 | 2.0206 | Rectification done
VGSUPL | June | SCB.14.04 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.43056 | 4.6667 | string found faulty | 0.4353 | 0.81991 | 2.1771 | Rectification done
VGSUPL | June | SCB.14.06 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.4375 | 4.8333 | string found faulty | 0.4873 | 0.81991 | 2.4372 | Rectification done
VGSUPL | June | SCB.15.01 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.44792 | 5.0833 | string found faulty | 0.6126 | 0.81991 | 3.0639 | Rectification done
VGSUPL | June | SCB.10.02 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.45486 | 5.25 | string found faulty | 0.6956 | 0.81991 | 3.479 | Rectification done
VGSUPL | June | SCB.08.04 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.46528 | 5.5 | string found faulty | 0.8587 | 0.81991 | 4.2948 | Rectification done
VGSUPL | June | SCB.07.04 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.47222 | 5.6667 | string found faulty | 1.0315 | 0.81991 | 5.159 | Rectification done
VGSUPL | June | SCB.08.06 | String fault | 6.1 | 44733 | 0.23611 | 44733 | 0.47917 | 5.8333 | string found faulty | 1.177 | 0.81991 | 5.8867 | Rectification done
VGSUPL | June | SCB.06.03 | String fault | 6.1 | 44734 | 0.24306 | 44734 | 0.41667 | 4.1667 | string found faulty | 0.9746 | 0.80328 | 4.7756 | Rectification done
VGSUPL | June | SCB.06.05 | String fault | 6.1 | 44734 | 0.24306 | 44734 | 0.43056 | 4.5 | string found faulty | 1.2207 | 0.80328 | 5.9814 | Rectification done
VGSUPL | June | SCB.05.01 | String fault | 6.1 | 44734 | 0.24306 | 44734 | 0.44097 | 4.75 | string found faulty | 1.3939 | 0.80328 | 6.8301 | Rectification done
VGSUPL | June | SCB.06.01 | String fault | 6.1 | 44736 | 0.22917 | 44736 | 0.44097 | 5.0833 | string found faulty | 2.0372 | 0.77002 | 9.5689 | Rectification done
VGSUPL | June | SCB.06.02 | String fault | 6.1 | 44736 | 0.22917 | 44736 | 0.45833 | 5.5 | string found faulty | 2.4056 | 0.77002 | 11.2993 | Rectification done
VGSUPL | June | SCB.07.03 | String fault | 6.1 | 44736 | 0.22917 | 44736 | 0.46181 | 5.5833 | string found faulty | 2.481 | 0.77002 | 11.6535 | Rectification done
VGSUPL | June | SCB.01.02 | String fault | 6.1 | 44736 | 0.22917 | 44736 | 0.47222 | 5.8333 | string found faulty | 2.711 | 0.77002 | 12.7338 | Rectification done
VGSUPL | June | SCB.04.06 | String fault | 6.1 | 44738 | 0.22917 | 44738 | 0.4375 | 5 | string found faulty | 1.7714 | 0.77141 | 8.3355 | Rectification done
VGSUPL | June | SCB.04.05 | String fault | 6.1 | 44738 | 0.22917 | 44738 | 0.44444 | 5.1667 | string found faulty | 1.9053 | 0.77141 | 8.9656 | Rectification done
VGSUPL | June | Inverter 27 | Ac Switch Response fault | 725 | 44739 | 0.28819 | 44739 | 0.29931 | 0.26667 | Inverter tripped in AC switch response fault | 0.0372 | 0.76521 | 20.6378 | After reset inverter started
VGSUPL | June | Inverter 21 | Fan Rotation Fault | 702.72 | 44742 | 0.31736 | 44742 | 0.32917 | 0.28333 | Inverter run at 10% load due to fan rotation fault | 0.0659 | 0.81994 | 37.9708 | Inverter run at full load after reset
VGSUPL | June | SCB.24.04 | String fault | 6.1 | 44742 | 0.22917 | 44742 | 0.44444 | 5.1667 | string found faulty | 1.2778 | 0.81994 | 6.3911 | Rectification done
VGSUPL | July | SCB.01.04 | String fault | 12.2 | 44743 | 0.26389 | 44743 | 0.43889 | 4.2 | string found faulty | 0.7278 | 0.81674 | 7.252 | Rectification done
VGSUPL | July | SCB.22.06 | String fault | 6 | 44743 | 0.26389 | 44743 | 0.45 | 4.4667 | string found faulty | 0.8652 | 0.81674 | 4.2399 | Rectification done
VGSUPL | July | SCB.22.05 | String fault | 12 | 44743 | 0.26389 | 44743 | 0.46944 | 4.9333 | string found faulty | 1.134 | 0.81674 | 11.1142 | Rectification done
VGSUPL | July | SCB.21.04 | String fault | 6 | 44743 | 0.26389 | 44743 | 0.47361 | 5.0333 | string found faulty | 1.2153 | 0.81674 | 5.9555 | Rectification done
VGSUPL | July | Inverter 12 | Ac Switch Response fault | 780.8 | 44743 | 0.31944 | 44743 | 0.34583 | 0.63333 | Inverter tripped in AC switch response fault | 0.0882 | 0.81674 | 56.2462 | After reset inverter started
VGSUPL | July | Inverter 01 | Ground Fault | 780.8 | 44743 | 0.47222 | 44743 | 0.48611 | 0.33333 | Inverter tripped in ground fault | 0.3288 | 0.81674 | 209.6796 | After reset inverter started
VGSUPL | July | SCB.09.02 | String fault | 6.1 | 44744 | 0.23264 | 44744 | 0.44236 | 5.0333 | string found faulty | 1.5717 | 0.78678 | 7.5431 | Rectification done
VGSUPL | July | SCB.10.03 | String fault | 6.1 | 44744 | 0.23264 | 44744 | 0.45278 | 5.2833 | string found faulty | 1.7989 | 0.78678 | 8.6336 | Rectification done
VGSUPL | July | SCB.10.05 | String fault | 12.2 | 44744 | 0.23264 | 44744 | 0.46736 | 5.6333 | string found faulty | 2.11 | 0.78678 | 20.2533 | Rectification done
VGSUPL | July | SCB.08.04 | String fault | 6.1 | 44744 | 0.23264 | 44744 | 0.475 | 5.8167 | string found faulty | 2.2419 | 0.78678 | 10.7597 | Rectification done
VGSUPL | July | SCB.07.05 | String fault | 6.1 | 44744 | 0.23264 | 44744 | 0.48403 | 6.0333 | string found faulty | 2.3998 | 0.78678 | 11.5175 | Rectification done
VGSUPL | July | SCB.02.05 | String fault | 6.1 | 44745 | 0.23958 | 44745 | 0.42917 | 4.55 | string found faulty | 0.7519 | 0.82544 | 3.786 | Rectification done
VGSUPL | July | SCB.02.03 | String fault | 6.1 | 44745 | 0.23958 | 44745 | 0.43681 | 4.7333 | string found faulty | 0.8106 | 0.82544 | 4.0815 | Rectification done
VGSUPL | July | SCB.13.05 | String fault | 6.1 | 44749 | 0.23264 | 44749 | 0.42222 | 4.55 | string found faulty | 2.5504 | 0.79731 | 12.4041 | Rectification done
VGSUPL | July | SCB.06.05 | String fault | 12.2 | 44751 | 0.23264 | 44751 | 0.375 | 3.4167 | string found faulty | 0.7096 | 0.74803 | 6.4758 | Rectification done
VGSUPL | July | Inverter 08 | Ground Fault | 780.8 | 44752 | 0.62847 | 44752 | 0.63542 | 0.16667 | Inverter tripped in ground fault | 0.0449 | 0.86542 | 30.3398 | After reset inverter started
VGSUPL | July | SCB.12.06 | String fault | 6.1 | 44754 | 0.24653 | 44754 | 0.4375 | 4.5833 | string found faulty | 1.5708 | 0.90614 | 8.6826 | Rectification done
VGSUPL | July | SCB.11.02 | String fault | 6.1 | 44754 | 0.24653 | 44754 | 0.44444 | 4.75 | string found faulty | 1.8277 | 0.90614 | 10.1026 | Rectification done
VGSUPL | July | SCB.12.03 | String fault | 6.1 | 44756 | 0.23264 | 44756 | 0.64583 | 9.9167 | string found faulty | 1.0622 | 0.87482 | 5.6683 | Rectification done
VGSUPL | July | SCB.12.05 | String fault | 6.1 | 44756 | 0.23264 | 44756 | 0.63889 | 9.75 | string found faulty | 1.0129 | 0.87482 | 5.4052 | Rectification done
VGSUPL | July | SCB.01.03 | String fault | 12.2 | 44756 | 0.23264 | 44756 | 0.62847 | 9.5 | string found faulty | 0.9327 | 0.87482 | 9.9545 | Rectification done
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44757 | 0.26458 | 44757 | 0.27222 | 0.18333 | Grid down due to line changeover from Jhunir to Budhlada(shutdown taken by PSPCL team) | 0.0111 | 0.82685 | 193 | system auto restored after resuming grid
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44757 | 0.34792 | 44757 | 0.35417 | 0.15 | Grid down due to line changeover from Budhlada to Jhunir GSS | 0.0608 | 0.82685 | 1053 | system auto restored after resuming grid
VGSUPL | July | SCB.11.03 | String fault | 6.1 | 44757 | 0.22222 | 44757 | 0.43958 | 5.2167 | string found faulty | 1.7639 | 0.82685 | 8.8967 | Rectification done
VGSUPL | July | SCB.19.02 | String fault | 18.3 | 44758 | 0.22222 | 44758 | 0.44444 | 5.3333 | string found faulty | 2.0551 | 0.75865 | 28.5315 | Rectification done
VGSUPL | July | SCB.18.01 | String fault | 6.1 | 44758 | 0.22222 | 44758 | 0.45486 | 5.5833 | string found faulty | 2.2737 | 0.75865 | 10.5221 | Rectification done
VGSUPL | July | SCB.18.02 | String fault | 12.2 | 44764 | 0.22708 | 44764 | 0.45139 | 5.3833 | string found faulty | 1.2456 | 0.81387 | 12.3678 | Rectification done
VGSUPL | July | SCB.13.06 | String fault | 30.5 | 44765 | 0.23403 | 44765 | 0.41806 | 4.4167 | string found faulty | 1.1836 | 0.8048 | 29.0533 | Rectification done
VGSUPL | July | SCB.08.05 | String fault | 6.1 | 44765 | 0.23403 | 44765 | 0.44236 | 5 | string found faulty | 1.4953 | 0.8048 | 7.3409 | Rectification done
VGSUPL | July | SCB.15.05 | String fault | 6.1 | 44765 | 0.23403 | 44765 | 0.45278 | 5.25 | string found faulty | 1.6857 | 0.8048 | 8.2756 | Rectification done
VGSUPL | July | SCB.15.06 | String fault | 6.1 | 44765 | 0.23403 | 44765 | 0.46667 | 5.5833 | string found faulty | 1.8967 | 0.8048 | 9.3115 | Rectification done
VGSUPL | July | SCB.05.03 | String fault | 6.1 | 44765 | 0.23403 | 44765 | 0.49097 | 6.1667 | string found faulty | 2.2515 | 0.8048 | 11.0533 | Rectification done
VGSUPL | July | Inverter 12 | Ground Fault | 780.8 | 44766 | 0.40278 | 44766 | 0.45486 | 1.25 | Inverter tripped in ground fault | 0.8299 | 0.78663 | 509.7268 | After reset inverter started
VGSUPL | July | Inverter 21 | Fan Rotation Fault | 712.8 | 44768 | 0.53194 | 44768 | 0.56597 | 0.81667 | Inverter run at 10% load due to fan rotation fault | 0.6697 | 0.80601 | 384.7584 | Inverter running at full load after IGBT fan replaced
VGSUPL | July | Inverter 14 | Fan Rotation Fault | 702.72 | 44769 | 0.45139 | 44769 | 0.49861 | 1.1333 | Inverter run at 10% load due to fan rotation fault | 0.9269 | 0.77419 | 504.268 | Inverter running at full load after IGBT fan replaced
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44769 | 0.71667 | 44769 | 0.72083 | 0.1 | Grid down due to line changeover from Jhunir to Budhlada(shutdown taken by PSPCL team) | 0.0283 | 0.77419 | 460 | system auto restored after resuming grid
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44769 | 0.74514 | 44769 | 0.74792 | 0.066667 | Grid down due to line changeover from Budhlada to Jhunir GSS | 0.0108 | 0.77419 | 176 | system auto restored after resuming grid
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44771 | 0.41528 | 44771 | 0.41736 | 0.05 | Grid Down due to Earth fault at Boha GSS | 0.0042 | 0.69377 | 61 | system auto restored after resuming grid
VGSUPL | July | All Inverters | Grid failure | 17999.015 | 44771 | 0.53194 | 44771 | 0.80625 | 6.5833 | system auto restored after Tower no-07, R Phase Disc insulator Faulty | 2.5045 | 0.69377 | 36528 | system auto restored after Tower no-07, R Phase Disc insulator Replaced
VGSUPL | July | Inverter 21 | Ac Switch Response fault | 792 | 44773 | 0.38403 | 44773 | 0.40278 | 0.45 | Inverter tripped in AC switch response fault | 0.121 | 0.86521 | 82.9149 | After reset inverter started
VGSUPL | August | All Inverters | Grid failure | 17999 | 44781 | 0.29861 | 44781 | 0.30069 | 0.05 | Grid Down due to Earth fault at Boha GSS | 0.0081 | 0.77279 | 131 | system auto restored after resuming grid
VGSUPL | August | Inverter 06 | Fan Rotation Fault | 702.7 | 44781 | 0.51319 | 44781 | 0.52778 | 0.35 | Inverter run at 10% load due to fan rotation fault | 0.3092 | 0.77279 | 167.9086 | Inverter running at full load after IGBT fan replaced
VGSUPL | August | Inverter 21 | Fan Rotation Fault | 712.8 | 44781 | 0.54167 | 44781 | 0.5625 | 0.5 | Inverter run at 10% load due to fan rotation fault | 0.4658 | 0.77279 | 256.5847 | Inverter running at full load after IGBT fan replaced
VGSUPL | August | All Inverters | Grid failure | 17999 | 44781 | 0.71597 | 44781 | 0.71875 | 0.066667 | Grid Down due to Earth fault at Boha GSS | 0.016954 | 0.77279 | 275 | system auto restored after resuming grid
VGSUPL | August | All Inverters | Grid failure | 17999.015 | 44784 | 0.34167 | 44784 | 0.34444 | 0.066667 | Grid Down due to Earth fault at Boha GSS | 0.0159 | 0.82109 | 272 | system auto restored after resuming grid
VGSUPL | August | All Inverters | Grid failure | 17999.015 | 44784 | 0.71042 | 44784 | 0.71458 | 0.1 | Grid Down due to Earth fault at Boha GSS | 0.0119 | 0.82109 | 202 | system auto restored after resuming grid
VGSUPL | August | Inverter 04 | Ac Switch Response fault | 780.8 | 44786 | 0.26111 | 44786 | 0.70833 | 10.7333 | Inv. Tripped in AC switch Response Fault | 6.625 | 0.74343 | 3845.6334 | AC breaker Replace After Started.
VGSUPL | August | All Inverters | Grid failure | 17999.015 | 44797 | 0.34236 | 44797 | 0.34444 | 0.05 | Grid down due to line changeover from Jhunir to Budhlada(shutdown taken by PSPCL team) | 0.0209 | 0.79237 | 341 | system auto restored after resuming grid
VGSUPL | August | All Inverters | Grid failure | 17999.015 | 44797 | 0.71389 | 44797 | 0.71667 | 0.066667 | Grid down due to line changeover from Budhlada to Jhunir GSS | 0.016 | 0.79237 | 269 | system auto restored after resuming grid
VGSUPL | August | Inverter 14 | PV power interrupted | 780.8 | 44799 | 0.44306 | 44799 | 0.45139 | 0.2 | Inverter tripped in PV power interrupted fault | 0.1049 | 0.76077 | 62.3118 | After reset inverter started
VGSUPL | August | Inverter 23 | Fan Rotation Fault | 780.75 | 44799 | 0.44792 | 44799 | 0.48611 | 0.91667 | inverter tripped in fan rotation fault | 0.6923 | 0.76077 | 411.2078 | After reset inverter started
VGSUPL | August | All Inverters | Grid failure | 17999.015 | 44801 | 0.29444 | 44801 | 0.32014 | 0.61667 | 66kv Line Disc change at Boha GSS | 0.117 | 0.77229 | 1896 | system auto restored after resuming grid
VGSUPL | August | Inverter 12 | PV power interrupted | 780.8 | 44804 | 0.52569 | 44804 | 0.53542 | 0.23333 | Inverter tripped in PV power interrupted fault | 0.2162 | 0.783 | 132.1766 | After reset inverter started
VGSUPL | September | SCB.08.05 | String fault | 6.1 | 44809 | 0.25139 | 44809 | 0.43472 | 4.4 | string found faulty | 1.75 | 0.75707 | 8.0818 | Rectification done
VGSUPL | September | SCB.03.05 | String fault | 6.1 | 44811 | 0.25208 | 44811 | 0.37361 | 2.9167 | string found faulty | 0.6338 | 0.7475 | 2.89 | Rectification done
VGSUPL | September | SCB.03.01 | String fault | 18.3 | 44811 | 0.25208 | 44811 | 0.37361 | 2.9167 | string found faulty | 0.6338 | 0.7475 | 8.6699 | Rectification done
VGSUPL | September | SCB.01.05 | String fault | 6.1 | 44811 | 0.25208 | 44811 | 0.37361 | 2.9167 | string found faulty | 0.6338 | 0.7475 | 2.89 | Rectification done
VGSUPL | September | SCB.01.04 | String fault | 6.1 | 44811 | 0.25208 | 44811 | 0.37361 | 2.9167 | string found faulty | 0.6338 | 0.7475 | 2.89 | Rectification done
VGSUPL | September | All Inverters | Grid failure | 17999.015 | 44811 | 0.37361 | 44811 | 0.46667 | 2.2333 | Grid down due to Permit taken by PSPCL Team. | 1.5966 | 0.7475 | 25138 | system auto restored after resuming grid
VGSUPL | September | SCB.03.05 | String fault | 6.1 | 44811 | 0.46667 | 44811 | 0.50694 | 0.96667 | string found faulty | 0.8596 | 0.7475 | 3.9195 | Rectification done
VGSUPL | September | SCB.03.01 | String fault | 18.3 | 44811 | 0.46667 | 44811 | 0.52083 | 1.3 | string found faulty | 1.1628 | 0.7475 | 15.9061 | Rectification done
VGSUPL | September | SCB.01.05 | String fault | 6.1 | 44811 | 0.46667 | 44811 | 0.52778 | 1.4667 | string found faulty | 1.3142 | 0.7475 | 5.9924 | Rectification done
VGSUPL | September | SCB.01.04 | String fault | 6.1 | 44811 | 0.46667 | 44811 | 0.53472 | 1.6333 | string found faulty | 1.4625 | 0.7475 | 6.6686 | Rectification done
VGSUPL | September | All Inverters | Grid failure | 17999.015 | 44813 | 0.58125 | 44813 | 0.59306 | 0.28333 | Grid down due to protection Relay Test checked by PSPCL team at 220kv Jhunir GSS. | 0.2205 | 0.76967 | 3591 | system auto restored after resuming grid
VGSUPL | September | Inverter 12 | Internal SW fault | 780.8 | 44813 | 0.59306 | 44813 | 0.6 | 0.16667 | Inverter tripped in SW Internal fault | 0.1258 | 0.76967 | 75.601 | After reset inverter started
VGSUPL | September | All Inverters | Grid failure | 17999.015 | 44816 | 0.60625 | 44816 | 0.64097 | 0.83333 | Grid down due to line changeover from Jhunir to Budhlada | 0.41 | 0.76745 | 6647 | system auto restored after resuming grid
VGSUPL | September | All Inverters | Grid failure | 17999.015 | 44816 | 0.68056 | 44816 | 0.6875 | 0.16667 | Grid down due to line changeover from Jhunir to Budhlada | 0.0474 | 0.76745 | 776 | system auto restored after resuming grid